## Cover
Investment Case Workbook - Factory A Vietnam DPPA Grid CfD Minimum BESS
Grid-connected DPPA with CfD (ND57/2025) · prepared 2026-09-13 · REopt dispatch + proforma_vietnam financial engine
REopt run UUID: 335a9b84-9e49-45bb-8ec9-5e392780cd12
Model validation status |  | Live tie-out of every Excel-derived metric against the engine
Colour legend
Hardcoded input / engine output | Case file terms, REopt dispatch results, 8760-h settlement totals, tie-out references
Live Excel formula (white) | Everything derivable is a formula - trace with Excel's formula auditing tools
PASS / REVIEW check cell | Excel-vs-engine tie-out at stated tolerances
Contents
Executive Summary | Headline KPIs for both counterparties
Assumptions | Every case input & contract term with unit, source and named cell
Model Basis | Methodology, settlement math, simplifications register
Pro Forma (Audit) | Full cash flow rebuilt with live formulas + engine tie-out
FX Sensitivity | USD returns under VND depreciation (editable)
Buyer Analysis | Offtaker savings vs business-as-usual
Developer Returns | Sources & uses, coverage, equity cash flow
Technical Results | System sizing, year-1 energy balance, bill comparison
Battery SOH | State of health replayed from the solved dispatch; drives the battery derate
Dispatch Profile | 8760-h dispatch incl. original PV generation; chart shows the peak-load week
Load Duration | Load and net-load duration curves
Year 1 BAU vs DPPA | Side-by-side year-1 buyer/seller position
Monthly / Hourly Settlement | ND57 fee chain, VND-native (full configuration on Assumptions)
Prepared for investment and lending review. Figures are model outputs, not offers; REopt sizing is optimizer output and may shift with solver versions.
Regenerate offline anytime: python -m proforma_vietnam.rebuild_report --case-dir <case>.

## Executive Summary
Investment & PPA Negotiation Summary - Factory A Vietnam DPPA Grid CfD Minimum BESS
Grid-connected DPPA with CfD (ND57/2025) · prepared 2026-09-13 · REopt dispatch + proforma_vietnam financial model
Project & System
PV Size (kW) | 5914
Battery Power (kW) | 592
Battery Energy (kWh) | 1184
Total Investment (USD) | 3028160
Contract Terms
CfD Strike Price (VND/kWh) | 2000
CfD Strike Escalation (per year) | 4%
Annual Contract Volume (kWh) | 7896846.067
Transmission Loss Factor k | 1.026
Distribution Loss Factor K_pp | 1.0273
DPPA Service Fee (VND/kWh) | 360
Settlement Adder C_CL (VND/kWh) | 163.3
Analysis Period (Years) | 20
Developer (Seller) Returns
Equity IRR | 25.97%
Project IRR | 17.42%
NPV (USD) | 1982821.8524 | At owner discount rate
Minimum DSCR (debt years) | 1.4777 | Lender covenant view
Average DSCR | 1.7075
Simple Payback (Years) | 4.8687
Equity Investment (USD) | 908448
Debt Principal (USD) | 2119712
Buyer (Offtaker) Outcome
Year 1 BAU Cost (USD) | 731030.93
Year 1 Cost With Project (USD) | 836704.4068
Year 1 Buyer Savings (USD) | -105673.4768
Year 1 Savings (% of BAU) | -14.46%
First 10 Years Buyer Savings (USD) | -1269302.3453 | Cumulative, years 1-10
First 10 Years Savings (% of BAU) | -14.46%
Lifetime Buyer Savings (USD) | -3149863.7182 | Sum over analysis period
Lifetime Savings (% of BAU) | -14.47%
Model Basis & Conventions
• Buyer settlement quantity Q_Khc = min(hourly load, loss-adjusted generation Q_adj); excess generation is sold by the generator at FMP and never billed to the buyer.
• PV degradation, O&M escalation and battery replacement (REopt schedule) are applied across the analysis period.
• PV straight-line depreciation over 20 years (Circular 45/2013/TT-BTC permits 7-20 years for generating equipment).
• Vietnam CIT: 4-year exemption + 9-year 50% reduction from first profitable year; 5-year tax-loss carryforward.
• All USD figures at the fixed contract exchange rate (see Assumptions); FX drift between VND revenue and USD reporting is quantified on the FX Sensitivity sheet.

## Assumptions
Assumptions & Model Inputs
Shaded cells are hardcoded inputs (case file or engine output); named cells drive every formula on the Pro Forma (Audit) sheet.
Project & Run
Case name | Factory A Vietnam DPPA Grid CfD Minimum BESS |  | case.json
Financing structure | Grid DPPA with CfD (ND57/2025) |  | proforma_vietnam.structures
REopt run UUID | 335a9b84-9e49-45bb-8ec9-5e392780cd12 |  | REopt API
Report prepared | 2026-09-13
Analysis period | 20 | years | proforma_vietnam.defaults replacement policy (PROJECT_YEARS) unless case.json financial.analysis_years overrides
Tariff year | 2025 |  | case.json tariff.year
Voltage level | 22-110kV |  | case.json tariff.voltage_level
TOU schedule | decision_963 |  | case.json tariff.tou_schedule
Site & Load Profile (case.json)
Latitude | 10.8231 | deg | case.json site.latitude
Longitude | 106.6297 | deg | case.json site.longitude
Load profile file | Sample Load Profile/Emivest_clean.csv |  | case.json load_profile.path (8760 hourly kW)
Load year | 2025 |  | case.json load_profile.year
PV Technology (case.json)
PV minimum size | 5914 | kW | case.json technologies.pv.min_kw
PV maximum size | 5914 | kW | case.json technologies.pv.max_kw
PV installed cost | 480 | USD/kW | case.json technologies.pv.installed_cost_per_kw
PV O&M cost | 6 | USD/kW/yr | case.json technologies.pv.om_cost_per_kw
PV degradation (case input) | 0.5% | per year | case.json technologies.pv.degradation_fraction
PVWatts tilt | 10 |  | case.json technologies.pv.pvwatts (production factor inputs)
PVWatts azimuth | 180 |  | case.json technologies.pv.pvwatts (production factor inputs)
PVWatts array_type | 1 |  | case.json technologies.pv.pvwatts (production factor inputs)
PVWatts module_type | 0 |  | case.json technologies.pv.pvwatts (production factor inputs)
PVWatts losses | 14 |  | case.json technologies.pv.pvwatts (production factor inputs)
PVWatts dc_ac_ratio | 1.2 |  | case.json technologies.pv.pvwatts (production factor inputs)
Storage Technology (case.json)
Storage minimum power | 592 | kW | case.json technologies.storage.min_kw
Storage maximum power | 592 | kW | case.json technologies.storage.max_kw
Storage minimum energy | 1184 | kWh | case.json technologies.storage.min_kwh
Storage maximum energy | 1184 | kWh | case.json technologies.storage.max_kwh
Storage cost per kW | 80 | USD/kW | case.json technologies.storage.installed_cost_per_kw
Storage cost per kWh | 120 | USD/kWh | case.json technologies.storage.installed_cost_per_kwh
Storage fixed cost | 0 | USD | case.json technologies.storage.installed_cost_constant
O&M (fraction of installed cost) | 1% | per year | case.json technologies.storage.om_cost_fraction_of_installed_cost
Currency & FX
Model currency | USD |  | EVN tariff converted VND→USD before REopt; see Model Basis
Contract exchange rate | 26300 | VND per USD | case.json tariff.exchange_rate_vnd_per_usd
FX treatment | Held flat over the analysis period |  | Simplification - see FX Sensitivity sheet
Capital Costs
PV capex | 2838720 | USD | REopt PV size_kw × installed_cost_per_kw
BESS capex | 189440 | USD | REopt ElectricStorage initial_capital_cost
Other capex | 0 | USD | case.json (developer overrides)
Total investment |  | USD | Formula: PV + BESS + Other
Operating Costs
Year-1 O&M | 37378.4 | USD/yr | REopt Financial.year_one_om_costs_before_tax
O&M escalation | 3% | per year | vietnam_defaults.json / case.json financial.om_escalation_rate
Replacement Policy
Battery replacement | Not scheduled inside the 20 year horizon |  | Client direction 2026-09-12: capacity fade is carried on the Battery SOH sheet and derates the battery's savings; REopt sent replace_cost 0. Opt in per case with technologies.storage.replacement
Battery cycle life (EFC to 80 percent) | 8000 | cycles | proforma_vietnam.defaults BESS_CYCLE_LIFE_EFC unless case.json technologies.storage.cycle_life_efc overrides (sets the SOH cycle fade: (1 - 0.80) / cycle life per kWh discharged)
Battery ageing treatment | derate |  | case.json technologies.storage.ageing_treatment (2026-09-13): derate multiplies the battery's savings by the year's SOH; augment keeps the capacity at nominal and books the daily top-up as an operating cost (Pro Forma row 'Battery augmentation')
Augmentation price declination | 3% | per year | proforma_vietnam.defaults BESS_AUGMENTATION_PRICE_DECLINATION_RATE unless technologies.storage.augmentation_price_declination_rate; the top-up is priced at the installed USD/kWh sent to REopt times (1 - rate)^(day/365), REopt's own degradation price path
PV inverter replacement year | 11 | year | proforma_vietnam.defaults replacement policy
PV inverter replacement fraction of PV capex | 10% | fraction | proforma_vietnam.defaults replacement policy
PV inverter replacement cost | 283872 | USD | Engine: fraction x solved PV capex (none booked when the run has no PV)
Tariff & Escalation
EVN energy escalation | 4% | per year | case.json tariff.evn_energy_escalation_rate
EVN capacity (demand) escalation | 4% | per year | case.json tariff.evn_capacity_escalation_rate
PV degradation | 0.5% | per year | REopt PV.degradation_fraction
Tariff currency fed to REopt | USD |  | case.json tariff.currency
Two-component tariff pilot | FALSE | yes/no | case.json tariff.two_component_pilot_enabled
Contract Terms
ESCO energy price (fraction of EVN tariff) | 90% | fraction | case.json esco_contract.esco_energy_discount_fraction
Demand savings share to ESCO | 80% | fraction | case.json esco_contract.demand_savings_esco_share
Grid charging enabled | FALSE | yes/no | case.json esco_contract.grid_charging_enabled
CfD strike price | 2000 | VND/kWh | case.json dppa.cfd_strike_per_kwh_vnd
CfD strike escalation | 4% | per year | case.json dppa.cfd_strike_escalation_rate
DPPA fee / FMP escalation | 4% | per year | case.json dppa.fee_escalation_rate
Annual CfD contract volume | 7896846.067 | kWh/yr | case.json dppa.cfd_contract_volume_kwh_per_hour
Transmission loss factor k (price-only) | 1.026 | ratio | ND57; CFMP = FMP × k
Distribution loss factor K_pp | 1.0273 | ratio | ND57 by voltage; Q_adj = Q_meter / K_pp
DPPA system service fee | 360 | VND/kWh | 2025 EVN published fee
Settlement adder C_CL | 163.3 | VND/kWh | 2025 EVN published adder
Allocation fraction δ | 1 | fraction | case.json dppa.allocation_fraction_delta
FMP / CFMP price series | DPPA DOC/fmp_cfmp_vn.json |  | case.json dppa.fmp_series_path (8760-hour VND/kWh)
Financing
Debt fraction | 70% | of total capex | vietnam_defaults.json / case.json financial.debt_fraction
Debt interest rate | 8.5% | per year | vietnam_defaults.json / case.json financial.debt_interest_rate_fraction
Debt term | 10 | years | vietnam_defaults.json / case.json financial.debt_term_years
Debt principal |  | USD | Formula: total investment × debt fraction
Equity investment |  | USD | Formula: total investment − debt
Annual debt payment (level) |  | USD/yr | Standard annuity over the debt term
Owner discount rate | 10% | per year | case.json financial.owner_discount_rate_fraction
Tax & Depreciation (Vietnam)
CIT regime | RE producer - Law 67/2025 preferential (10% / 15y) |  | proforma_vietnam.cash_flow (structure-dependent; explicit override wins)
CIT standard rate | 20% | of taxable income | Law 67/2025/QH15; vietnam_defaults.json
CIT preferential rate (RE producer) | 10% | of taxable income | Law 67/2025/QH15 + Decree 320/2025/NĐ-CP (first-15-year window)
CIT preferential-rate period | 15 | years (from year 1) | Law 67/2025/QH15
CIT holiday | 4 | years | Law 67/2025 (from first profitable year); Circular 78/2014 Art. 18 shape
CIT reduced-rate period | 9 | years | Law 67/2025; Circular 78/2014 Art. 18 shape
CIT reduction during period | 50% | of applicable base rate | Law 67/2025 (50% of base rate)
Tax-loss carryforward limit | 5 | years | Law 67/2025; Circular 78/2014 Art. 9 shape
Incentive clock cap | 4 | year (latest start) | Law 67/2025; Circular 78/2014 Art. 18 shape
PV depreciation (straight-line) | 20 | years | Circular 45/2013/TT-BTC (7–20 yr band)
BESS depreciation (straight-line) | 8 | years | Circular 45/2013/TT-BTC
Year-1 Engine Outputs (hardcoded - dispatch × tariff, not derivable in-sheet)
Year-1 BAU EVN bill | 731030.93 | USD | REopt ElectricTariff.year_one_bill_before_tax_bau
Year-1 optimized EVN bill | 410190.5467 | USD | REopt ElectricTariff.year_one_bill_before_tax
Year-1 BAU demand charge | 0 | USD | REopt year_one_demand_cost_before_tax_bau
Year-1 optimized demand charge | 0 | USD | REopt year_one_demand_cost_before_tax
Year-1 demand savings base | 0 | USD | max(BAU − optimized demand charge, 0)
Year-1 served-energy retail value | 320840.397 | USD | Σ project-served kWh × EVN TOU rate (8760 h)
Year-1 battery energy revenue base | 0 | USD | Battery-served kWh x TOU rate x ESCO discount (inside the served series (PV-charged storage))
Year-1 battery served-energy retail value | 41179.9596 | USD | Battery-served kWh x EVN TOU rate
Year-1 battery net energy value outside served | 0 | USD | Discharge at retail minus grid charging (direct ownership / battery-only cases)
Year-1 battery demand relief | 0 | USD | PV-only counterfactual demand charge minus solved (counterfactual)
Battery share of matched energy | 8.055% | fraction | Battery-served kWh / project-served kWh
Year-1 C_DN (spot energy) | 224087.0867 | USD | settle_dppa_year_one: Σ Q_Khc × CFMP × K_pp
Year-1 C_DPPA (system fee) | 57646.9108 | USD | Σ Q_Khc × f_dppa
Year-1 C_CL (settlement adder) | 26149.2792 | USD | Σ Q_Khc × f_cl
Year-1 C_BL (retail shortfall) | 421283.9956 | USD | Σ shortfall × EVN TOU rate
Year-1 CfD strike leg | 318944.2602 | USD | Σ P_c × min(Q_c, Q_Khc)
Year-1 CfD market offset | 211408.5517 | USD | Σ FMP × min(Q_c, Q_Khc)
Year-1 generator FMP revenue | 407550.1091 | USD | Σ Q_re_meter × FMP
Year-1 matched-energy retail value | 309746.9305 | USD | Σ Q_Khc × EVN TOU rate (degradation repurchase)
Other Assumptions (assumptions.json echo)
battery_ageing_treatment | derate |  | assumptions.json
bess_augmentation_price_declination_rate | 0.03 |  | assumptions.json
dppa_regulatory_source | NLDC/EVN 2025 announcements (EVN notice 08/05/2025, provisional); NSMO CD7 worked example |  | assumptions.json
dppa_regulatory_vintage_year | 2025 |  | assumptions.json
rate_vintage_source | EVN retail electricity tariff, Decision 1279/QD-BCT dated 2025-05-09 |  | assumptions.json
rate_vintage_year | 2025 |  | assumptions.json
tariff_category | manufacturing |  | assumptions.json

## Model Basis
Model Basis, Conventions & Simplifications
1. Model architecture
• REopt (NLR optimization engine) selects PV/BESS sizing and hourly dispatch against the EVN time-of-use tariff over an 8760-hour year.
• proforma_vietnam post-processes the REopt run: an hourly ND57/2025 DPPA settlement layer (when applicable) and a 20-year developer cash flow with Vietnam tax and debt.
• This workbook is generated from that engine. The Pro Forma (Audit) sheet re-derives the full cash flow with live Excel formulas from the named inputs on the Assumptions sheet; the Checks block ties every metric back to the engine (PASS/REVIEW).
2. Currency & FX
• All money flows are computed in USD at the fixed contract rate (26,300 VND/USD).
• Underlying revenue is VND-denominated (EVN tariff, FMP market, DPPA fees). Holding FX flat for the analysis period is a simplification: the FX Sensitivity sheet quantifies USD-reported returns under 0-3%/yr VND depreciation.
• Sheets that show VND amounts (Hourly/Monthly Settlement, DPPA fee inputs) are VND-native regulatory quantities, not conversions.
• Debt is assumed VND-denominated (local bank), so DSCR is FX-neutral.
3. Settlement math - ND57/2025 grid DPPA with CfD
• Q_adj[h] = Q_re_meter[h] / K_pp × delta - quantity conversion generator→customer uses K_pp only (CD7 Ví dụ 1); k is price-only.
• Q_Khc[h] = min(load[h], Q_adj[h]) - the buyer settles only matched consumption; surplus stays with the generator at FMP and is never billed to the buyer.
• C_DN = Q_Khc × CFMP × K_pp with CFMP = FMP × k; C_DPPA = Q_Khc × f_dppa; C_CL = Q_Khc × f_cl; C_BL = shortfall × EVN TOU retail.
• CfD settles on min(Q_c, Q_Khc) per CD7 Ví dụ 4: CfD[h] = (P_c − FMP[h]) × Q_cfd[h]. The strike leg escalates at the contracted strike escalation; the market legs at the fee escalation.
• Curtailed PV from the self-consumption REopt run is credited as grid export at FMP (the generator does not curtail under DPPA).
• Year-1 settlement is computed hourly; later years scale the year-1 totals by the escalation and degradation factors shown on the Pro Forma (Audit) sheet.
4. Multi-year mechanics
• PV degradation compounds on generation-linked terms; energy lost to degradation is repurchased from EVN at retail (added to the buyer's residual bill / C_BL).
• O&M escalates at its own rate. Battery: no scheduled replacement inside the horizon (client direction 2026-09-12); capacity fade is carried by the Battery SOH curve and derates the battery's savings each year. The PV inverter is booked in year 11 at 10 percent of the solved PV capex.
• Battery state of health: REopt.jl v0.57.0's daily fade recurrence (calendar fade on the average stored energy, cycle fade on the energy discharged) replayed over the horizon on the solved year-1 dispatch, with the hours-per-time-step factor removed so 15 minute and hourly solves age alike. Cycle life 8,000 EFC to 80 percent sets the cycle coefficient. Treatment: derate. The battery's share of energy revenue, retail repurchase, demand relief and grid arbitrage is multiplied by the year's average SOH; energy delivered is assumed to scale with capacity (the battery treated as capacity-bound every day), an upper bound on the loss. The cost of keeping the capacity by augmentation instead is shown on the Battery SOH sheet for comparison. The optimiser does not see the curve. See the Battery SOH sheet.
• Debt: level-payment annuity over the debt term (interest + principal split per the Debt Schedule block).
• CIT regime: renewable-energy producer (Law 67/2025/QH15 + Decree 320/2025/NĐ-CP) - 10% preferential base rate for the first 15 years counted from the first revenue-generating year, then 20%. The 4-year exemption and 9-year 50%-reduction periods count from the first profitable year, no later than year 4; the 50% reduction applies to the then-applicable base rate. Tax losses carry forward at most 5 consecutive years, consumed FIFO - the carryforward schedule is fully visible on the Pro Forma sheet.
• Straight-line depreciation: PV over the configured life within the 7-20y band of Circular 45/2013/TT-BTC; BESS over its own life.
• Battery replacement is CAPITALIZED, not expensed (VAS / Circular 45/2013): each replacement battery is a fixed asset depreciated straight-line over the 8-year BESS class life from its in-service (replacement) year, with each replacement year carrying its own schedule. The replacement cash outflow is unchanged - only the CIT deduction timing shifts from a single full deduction to the depreciation stream.
5. Simplifications register (disclosed for audit)
• Fixed FX over the analysis period - quantified on the FX Sensitivity sheet.
• Battery replacement depreciation is truncated at the analysis horizon: charges beyond the final year are simply not taken and the undepreciated remainder is not written off (no terminal disposal/salvage of the replaced or residual battery is modelled).
• VAT is out of scope (pass-through assumed for both parties).
• No working-capital, DSRA, or terminal/residual value is modelled.
• A single dispatch year (8760 h) is escalated; no re-dispatch in later years.
• REopt sizing is optimizer output and can vary slightly between solver versions; the financial post-processing is deterministic given results.json.
6. How to validate this workbook
• 1) Assumptions sheet: confirm every shaded input against the case file / contract term sheet.
• 2) Pro Forma (Audit): trace any line - formulas reference named cells (e.g. ESC_ENERGY, DEBT_RATE) and prior rows only.
• 3) Checks block: every metric shows Excel vs engine with PASS/REVIEW at stated tolerances (amounts $1, rates 5 bp, DSCR 0.005, payback 0.05 yr).
• 4) FX Sensitivity: rate cells are editable; Excel recomputes IRR/NPV live.
• 5) Technical sheets (Technical Results, Dispatch Profile, Load Duration, Settlement) are engine output for record. The Dispatch sheet's PV production factor (kWh/kW, PVWatts-derived) is the hourly solar-resource signal - REopt does not persist raw irradiance.
7. Key references
• ND57/2025 (DPPA decree) Art. 14-18 - settlement chain and eligibility.
• NSMO/CD7 simulation examples - k price-only conversion (Ví dụ 1), CfD cap on matched volume (Ví dụ 4).
• Law 67/2025/QH15 + Decree 320/2025/NĐ-CP - CIT rates, RE-producer preferential incentive, holiday & loss carryforward (legacy Circular 78/2014 Art. 9, 18 shape kept for the standard regime).
• Circular 45/2013/TT-BTC - fixed-asset depreciation bands.
• EVN retail tariff (current & QĐ963 TOU structures) as configured in the case file.

## Pro Forma (Audit)
Pro Forma (Audit) - every white cell is a live Excel formula
Shaded cells are hardcoded engine outputs (REopt dispatch / 8760-h settlement / tie-out reference). All other cells derive from the named cells on the Assumptions sheet. Currency: USD at the fixed contract FX rate.
TIMELINE & INDEXATION
Year | index | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
EVN energy escalation factor | index
EVN capacity escalation factor | index
O&M escalation factor | index
PV degradation factor | index
Battery SOH factor (year average) | index | 1 | 0.9905 | 0.97844 | 0.9682 | 0.95856 | 0.94927 | 0.94021 | 0.9313 | 0.92253 | 0.91385 | 0.90526 | 0.89673 | 0.88826 | 0.87985 | 0.87147 | 0.86314 | 0.85484 | 0.84658 | 0.83834 | 0.83013 | 0.82195
Generation factor (PV degradation, battery SOH) | index
DPPA fee / FMP escalation factor | index
CfD strike escalation factor | index
REVENUE (USD)
Generator FMP market revenue | USD
CfD strike leg (P_c × Q_cfd) | USD
CfD market offset (FMP × Q_cfd) | USD
CfD net settlement (to generator) | USD
Generator revenue (FMP + CfD net) | USD
Demand charge savings (total) | USD
ESCO share of demand savings | USD
Total developer revenue | USD
OPERATING COSTS (USD)
O&M | USD
Equipment replacement (engine schedule) | USD |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 283872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EBITDA | USD
DEBT SCHEDULE (USD)
Opening debt balance | USD
Interest | USD
Principal repayment | USD
Debt service | USD
Closing debt balance | USD
DEPRECIATION & VIETNAM CIT (USD)
PV depreciation (straight-line) | USD
BESS depreciation (straight-line) | USD
Replacement depreciation (in-service yr 11) | USD
Total depreciation | USD
Taxable income before loss relief (EBT) | USD
New tax loss arising | USD
Assessable income (pre-relief) | USD
Loss vintage aged 1y - available | USD | 1: 0
Loss vintage aged 2y - available | USD | 1: 0
Loss vintage aged 3y - available | USD | 1: 0
Loss vintage aged 4y - available | USD | 1: 0
Loss vintage aged 5y - available | USD | 1: 0
Loss vintage aged 5y - utilised | USD
Loss vintage aged 4y - utilised | USD
Loss vintage aged 3y - utilised | USD
Loss vintage aged 2y - utilised | USD
Loss vintage aged 1y - utilised | USD
Loss relief utilised (FIFO, ≤5y old) | USD
Taxable income after loss relief | USD
Profitable-to-date flag (starts CIT clock) | 0/1
CIT clock start year (first profit, capped) |  | 1: Circular 78/2014 Art. 18
Applicable base CIT rate (preferential window) | %
Applicable CIT rate | %
CIT payable | USD
CASH FLOW & COVERAGE (USD)
Cash available for debt service (CFADS) | USD
Project cash flow (unlevered, post-tax) | USD
Equity cash flow | USD
Cumulative equity cash flow | USD
DSCR (debt years) | x
OFFTAKER (BUYER) POSITION (USD)
BAU EVN bill (energy + demand) | USD
C_DN spot energy (Q_Khc × CFMP × K_pp) | USD
C_DPPA system service fee | USD
C_CL settlement adder | USD
C_BL retail shortfall (incl. degradation repurchase) | USD
Buyer cost with project | USD
Buyer savings vs BAU | USD
Buyer savings (% of BAU) | %
RETURN METRICS (Excel formulas)
Equity IRR
Project IRR (unlevered)
Equity NPV @ owner discount rate
Minimum DSCR (debt years) |  | 1: MIN ignores the blank non-debt years
Average DSCR (debt years)
First year cumulative equity CF ≥ 0
Simple equity payback |  | 1: years
ROI (cumulative equity CF / equity)
Buyer savings, years 1-10 (% of BAU)
CHECKS - EXCEL vs ENGINE (per-year tie-out)
Equity cash flow (engine) | USD | -908448 | 154335.1497 | 171444.5344 | 189229.606 | 207675.4042 | 213837.2665 | 231823.3694 | 250421.8826 | 269650.2606 | 288342.6739 | 308885.8486 | 371077.6172 | 678257.2984 | 702407.1843 | 698481.5969 | 723043.0537 | 685039.0263 | 708476.471 | 732759.9759 | 750823.1808 | 776891.23
CFADS (engine) | USD |  | 477395.5911 | 494504.9758 | 512290.0474 | 530735.8456 | 536897.7079 | 554883.8108 | 573482.3241 | 592710.702 | 611403.1153 | 631946.2901 | 371077.6172 | 678257.2984 | 702407.1843 | 698481.5969 | 723043.0537 | 685039.0263 | 708476.471 | 732759.9759 | 750823.1808 | 776891.23
CIT (engine) | USD |  | 0 | 0 | 0 | 0 | 12959.9778 | 14792.4862 | 16732.5258 | 18787.4156 | 22149.0565 | 24457.9688 | 25133.1377 | 26359.8578 | 27630.9044 | 57895.733 | 60624.7837 | 126904.7566 | 132764.1177 | 138834.994 | 152221.7952 | 158738.8075
Max ¦Excel − engine¦ this year | USD
Check |  | 0: Excel; 1: Engine; 2: Delta; 3: Status
Per-year cash flow tie-out (max delta, all years) |  | 1: 0
Equity IRR |  | 1: 25.97%
Project IRR |  | 1: 17.42%
Equity NPV |  | 1: 1982821.8524
Minimum DSCR |  | 1: 1.4777
Average DSCR |  | 1: 1.7075
Simple equity payback |  | 1: 4.8687
ROI |  | 1: 1003%
Buyer savings, years 1-10 (% of BAU) |  | 1: -14.46%

## FX Sensitivity
FX Sensitivity - VND depreciation vs USD returns
Cash flows are VND-denominated (EVN tariff / DPPA settlement) but reported in USD at the fixed contract rate. Each scenario deflates the year-t USD equity cash flow by (1+d)^t. Debt is assumed VND-denominated, so DSCR is unchanged. The rate cells are editable; engine columns validate the default scenarios.
VND depreciation (per year) | Equity IRR (USD) | Equity NPV (USD) | Equity IRR (engine) | Equity NPV (engine) | Status
0% |  |  | 25.97% | 1982821.8524
1% |  |  | 24.73% | 1697104.617
2% |  |  | 23.5% | 1449278.8028
3% |  |  | 22.3% | 1233569.388
Helper - FX-adjusted equity cash flow per scenario (USD): CF_t / (1 + d)^t
| 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20

## Buyer Analysis
Buyer Analysis - Cost vs Business-As-Usual
Annual electricity cost with the project compared against the EVN-only baseline (USD)
Year 1 Snapshot
| Year 1 BAU Cost (USD) | 731030.93
| Year 1 Cost With Project (USD) | 836704.4068
| Year 1 Savings (USD) | -105673.4768
| Year 1 Savings (% of BAU) | -14.46%
| of which C_DN spot energy (USD) | 223915.6322
| of which C_DPPA + C_CL fees (USD) | 83732.0755
| of which C_BL retail shortfall (USD) | 421520.9906
| of which CfD payment, net (USD) | 107535.7085 | Positive = buyer pays generator
| First 10 Years Savings (USD) | -1269302.3453 | Cumulative, years 1-10
| First 10 Years Savings (% of BAU) | -14.46%
| Lifetime Savings (USD) | -3149863.7182 | Cumulative over analysis period
| Lifetime Savings (% of BAU) | -14.47%
Year | BAU Cost (USD) | Cost With Project (USD) | Savings (USD) | Savings (% of BAU) | Cumulative Savings (USD)
1 | 731030.93 | 836704.4068 | -105673.4768 | -14.46% | -105673.4768
2 | 760272.1672 | 870183.376 | -109911.2088 | -14.46% | -215584.6856
3 | 790683.0539 | 905001.5949 | -114318.541 | -14.46% | -329903.2266
4 | 822310.376 | 941212.8271 | -118902.4511 | -14.46% | -448805.6777
5 | 855202.7911 | 978872.8456 | -123670.0545 | -14.46% | -572475.7322
6 | 889410.9027 | 1018039.6323 | -128628.7295 | -14.46% | -701104.4617
7 | 924987.3388 | 1058773.481 | -133786.1422 | -14.46% | -834890.6039
8 | 961986.8324 | 1101137.0945 | -139150.2621 | -14.46% | -974040.866
9 | 1000466.3057 | 1145195.682 | -144729.3764 | -14.47% | -1118770.2424
10 | 1040484.9579 | 1191017.0609 | -150532.103 | -14.47% | -1269302.3453
11 | 1082104.3562 | 1238671.7607 | -156567.4045 | -14.47% | -1425869.7498
12 | 1125388.5305 | 1288233.1327 | -162844.6022 | -14.47% | -1588714.352
13 | 1170404.0717 | 1339777.4621 | -169373.3904 | -14.47% | -1758087.7425
14 | 1217220.2346 | 1393384.0863 | -176163.8518 | -14.47% | -1934251.5942
15 | 1265909.044 | 1449135.5164 | -183226.4724 | -14.47% | -2117478.0667
16 | 1316545.4057 | 1507117.5645 | -190572.1588 | -14.48% | -2308050.2254
17 | 1369207.2219 | 1567419.4759 | -198212.254 | -14.48% | -2506262.4794
18 | 1423975.5108 | 1630134.0664 | -206158.5555 | -14.48% | -2712421.035
19 | 1480934.5312 | 1695357.8648 | -214423.3335 | -14.48% | -2926844.3685
20 | 1540171.9125 | 1763191.2621 | -223019.3496 | -14.48% | -3149863.7182

## Developer Returns
Developer Returns - Financing & Cash Flow
Seller/ESCO investment case: sources & uses, return metrics and annual equity cash flow (USD)
Sources & Uses
| Total Investment (USD) | 3028160
| Debt Principal (USD) | 2119712
| Equity Investment (USD) | 908448
Return Metrics
| Equity IRR | 25.97%
| Project IRR | 17.42%
| NPV (USD) | 1982821.8524 | At owner discount rate
| Minimum DSCR (debt years) | 1.4777
| Average DSCR | 1.7075
| Simple Payback (Years) | 4.8687
| ROI (cumulative equity CF / equity) | 1003%
Year | Revenue (USD) | O&M + Replacement (USD) | CIT (USD) | CFADS (USD) | Debt Service (USD) | DSCR | Equity Cash Flow (USD) | Cumulative Equity CF (USD)
1 | 514773.9911 | 37378.4 | 0 | 477395.5911 | 323060.4414 | 1.4777 | 154335.1497 | -754112.8503
2 | 533004.7278 | 38499.752 | 0 | 494504.9758 | 323060.4414 | 1.5307 | 171444.5344 | -582668.3159
3 | 551944.792 | 39654.7446 | 0 | 512290.0474 | 323060.4414 | 1.5857 | 189229.606 | -393438.7099
4 | 571580.2325 | 40844.3869 | 0 | 530735.8456 | 323060.4414 | 1.6428 | 207675.4042 | -185763.3057
5 | 591927.4042 | 42069.7185 | 12959.9778 | 536897.7079 | 323060.4414 | 1.6619 | 213837.2665 | 28073.9608
6 | 613008.1071 | 43331.8101 | 14792.4862 | 554883.8108 | 323060.4414 | 1.7176 | 231823.3694 | 259897.3302
7 | 634846.6142 | 44631.7644 | 16732.5258 | 573482.3241 | 323060.4414 | 1.7752 | 250421.8826 | 510319.2129
8 | 657468.8349 | 45970.7173 | 18787.4156 | 592710.702 | 323060.4414 | 1.8347 | 269650.2606 | 779969.4735
9 | 680902.0106 | 47349.8388 | 22149.0565 | 611403.1153 | 323060.4414 | 1.8925 | 288342.6739 | 1068312.1474
10 | 705174.5928 | 48770.334 | 24457.9688 | 631946.2901 | 323060.4414 | 1.9561 | 308885.8486 | 1377197.996
11 | 730316.199 | 334105.444 | 25133.1377 | 371077.6172 | 0 |  | 371077.6172 | 1748275.6133
12 | 756357.6035 | 51740.4473 | 26359.8578 | 678257.2984 | 0 |  | 678257.2984 | 2426532.9117
13 | 783330.7494 | 53292.6607 | 27630.9044 | 702407.1843 | 0 |  | 702407.1843 | 3128940.0959
14 | 811268.7704 | 54891.4406 | 57895.733 | 698481.5969 | 0 |  | 698481.5969 | 3827421.6928
15 | 840206.0212 | 56538.1838 | 60624.7837 | 723043.0537 | 0 |  | 723043.0537 | 4550464.7465
16 | 870178.1121 | 58234.3293 | 126904.7566 | 685039.0263 | 0 |  | 685039.0263 | 5235503.7728
17 | 901221.9479 | 59981.3592 | 132764.1177 | 708476.471 | 0 |  | 708476.471 | 5943980.2438
18 | 933375.7698 | 61780.7999 | 138834.994 | 732759.9759 | 0 |  | 732759.9759 | 6676740.2197
19 | 966679.1999 | 63634.2239 | 152221.7952 | 750823.1808 | 0 |  | 750823.1808 | 7427563.4005
20 | 1001173.2882 | 65543.2507 | 158738.8075 | 776891.23 | 0 |  | 776891.23 | 8204454.6305

## Technical Results
Metric | Value
System Sizing
PV Size (kW) | 5914
Battery Power (kW) | 592
Battery Energy (kWh) | 1184
Annual Energy Balance (Year 1)
PV to Load (kWh) | 4012585.6539
PV to Storage (kWh) | 390846.4887
PV to Grid (kWh) | 0
Storage to Load (kWh) | 351548.9195
Grid to Load (kWh) | 5138980.18
PV Curtailed (kWh) | 3923731.7224
Grid to Storage (kWh) | 0
Year-1 Utility Bill Comparison
BAU Utility Bill (USD) | 731030.93
Optimized Utility Bill (USD) | 410190.5467
Utility Bill Savings (USD) | 320840.3833
BAU Demand Charge (USD) | 0
Optimized Demand Charge (USD) | 0
Demand Charge Savings (USD) | 0
Solar Resource (Year 1)
Annual POA Irradiation (kWh/m²) | 1929.6822
Performance Ratio (Year 1) | 72.97%

## Battery SOH
Battery state of health
Method: REopt.jl v0.57.0 daily fade recurrence replayed over the horizon on the solved year-1 dispatch. SOH[d] = SOH[d-1] - (k_cal x a x Eavg[d-1] x d^(a-1) + k_cyc x E_discharged[d-1]), SOH in kWh, with the hours-per-time-step factor removed (h = 1) so 15 minute and hourly solves age alike.
Cycle fade: k_cyc = (1 - 0.80) / cycle life = 2.500e-05 kWh lost per kWh discharged (cycle life 8,000 EFC to 80 percent).
Calendar fade: k_cal = 1.16e-03, exponent a = 0.428 (NREL laboratory defaults, no chemistry or temperature calibration).
Use: the year-average SOH multiplies the battery's share of the savings on the Pro Forma (Audit) sheet (row 'Battery SOH factor'). Energy delivered is assumed to scale with capacity, the battery treated as capacity-bound every day: an upper bound on the loss. The cost of keeping the capacity by augmentation instead is shown for comparison. The optimiser does not see this curve; no battery replacement is scheduled unless the case opts in.
Energy attribution: inside the served series (PV-charged storage). Demand attribution: counterfactual.
Nominal capacity (kWh) | 1184
SOH end of year 10 | 90.1%
SOH end of year 20 | 81.79%
First year below 80 percent | Not within the 20 year horizon
Equivalent full cycles, year 1 | 296.9163
Equivalent full cycles, cumulative | 5938.3263
Average daily discharge, year 1 (kWh) | 963.1477
Ageing treatment | derate: the battery's savings are multiplied by the year-average SOH
Value lost to fade over the horizon, booked (USD) | 80787.7733
Augmentation cost over the horizon, not booked (USD) | 19823.6503
Augmentation price (USD/kWh, year 1; declining 3.0 percent a year) | 120
Year | SOH end of year | SOH year average (derate factor) | Usable capacity (kWh) | EFC in year | Cumulative EFC | Calendar fade (kWh) | Cycle fade (kWh) | Value lost to fade if derated (USD) | Augmentation cost if augmented (USD) | End of life (80 percent)
0 | 100% | 100% | 1184 | 0 | 0 | 0 | 0 | 0 | 0 | 80%
1 | 98.39% | 99.05% | 1164.9642 | 296.9163 | 296.9163 | 10.2704 | 8.7654 | 236.9949 | 2256.0959 | 80%
2 | 97.32% | 97.84% | 1152.247 | 296.9163 | 593.8326 | 3.9285 | 8.7887 | 559.3585 | 1458.4114 | 80%
3 | 96.33% | 96.82% | 1140.5574 | 296.9163 | 890.749 | 2.9008 | 8.7887 | 858.2061 | 1300.1279 | 80%
4 | 95.39% | 95.86% | 1129.3827 | 296.9163 | 1187.6653 | 2.386 | 8.7887 | 1162.9707 | 1205.515 | 80%
5 | 94.47% | 94.93% | 1118.5298 | 296.9163 | 1484.5816 | 2.0641 | 8.7887 | 1480.7432 | 1135.6333 | 80%
6 | 93.57% | 94.02% | 1107.9019 | 296.9163 | 1781.4979 | 1.8392 | 8.7887 | 1815.1923 | 1078.7185 | 80%
7 | 92.69% | 93.13% | 1097.4421 | 296.9163 | 2078.4142 | 1.6711 | 8.7887 | 2168.8496 | 1029.7899 | 80%
8 | 91.82% | 92.25% | 1087.1139 | 296.9163 | 2375.3305 | 1.5394 | 8.7887 | 2543.7732 | 986.3167 | 80%
9 | 90.95% | 91.39% | 1076.8923 | 296.9163 | 2672.2469 | 1.4329 | 8.7887 | 2941.8074 | 946.8519 | 80%
10 | 90.1% | 90.53% | 1066.7591 | 296.9163 | 2969.1632 | 1.3444 | 8.7887 | 3364.7042 | 910.4954 | 80%
11 | 89.25% | 89.67% | 1056.7009 | 296.9163 | 3266.0795 | 1.2695 | 8.7887 | 3814.1885 | 876.6507 | 80%
12 | 88.4% | 88.83% | 1046.707 | 296.9163 | 3562.9958 | 1.2051 | 8.7887 | 4291.9954 | 844.9019 | 80%
13 | 87.56% | 87.98% | 1036.7694 | 296.9163 | 3859.9121 | 1.1489 | 8.7887 | 4799.8952 | 814.9468 | 80%
14 | 86.73% | 87.15% | 1026.8812 | 296.9163 | 4156.8284 | 1.0994 | 8.7887 | 5339.7098 | 786.5585 | 80%
15 | 85.9% | 86.31% | 1017.0371 | 296.9163 | 4453.7448 | 1.0554 | 8.7887 | 5913.3259 | 759.5613 | 80%
16 | 85.07% | 85.48% | 1007.2326 | 296.9163 | 4750.6611 | 1.0159 | 8.7887 | 6522.7045 | 733.8157 | 80%
17 | 84.25% | 84.66% | 997.4637 | 296.9163 | 5047.5774 | 0.98015 | 8.7887 | 7169.8898 | 709.2086 | 80%
18 | 83.42% | 83.83% | 987.7273 | 296.9163 | 5344.4937 | 0.9477 | 8.7887 | 7857.0167 | 685.6465 | 80%
19 | 82.6% | 83.01% | 978.0205 | 296.9163 | 5641.41 | 0.91804 | 8.7887 | 8586.3177 | 663.0506 | 80%
20 | 81.79% | 82.19% | 968.341 | 296.9163 | 5938.3263 | 0.8908 | 8.7887 | 9360.1298 | 641.3538 | 80%

## Dispatch Profile
Hour | Load (kW) | PV Irradiation (W/m²) | PV Generation Total (kW) | PV to Load (kW) | PV to Storage (kW) | PV to Grid (kW) | PV Curtailed (kW) | Grid to Load (kW) | Grid to Storage (kW) | Storage to Load (kW)
1 | 1020 | 0 | 0 | 0 | 0 | 0 | 0 | 1020 | 0 | 0
2 | 1078.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1078.4 | 0 | 0
3 | 906.4 | 0 | 0 | 0 | 0 | 0 | 0 | 906.4 | 0 | 0
4 | 860.8 | 0 | 0 | 0 | 0 | 0 | 0 | 860.8 | 0 | 0
5 | 996.8 | 0 | 0 | 0 | 0 | 0 | 0 | 996.8 | 0 | 0
6 | 983.2 | 0 | 0 | 0 | 0 | 0 | 0 | 983.2 | 0 | 0
7 | 586.4 | 11.75 | 17.346 | 17.346 | 0 | 0 | 0 | 233 | 0 | 349.7687
8 | 104.269 | 120.27 | 536.7192 | 108.3151 | -428.4041 | 0 | 0 | 0 | 0 | 0
9 | 89.172 | 270.88 | 1255.9742 | 92.6323 | -609.607 | 0 | 553.7349 | 0 | 0 | 0
10 | 105.232 | 505.48 | 2330.1637 | 109.3155 | 0 | 0 | 2220.8482 | 0 | 0 | 0
11 | 89.626 | 573.07 | 2600.202 | 93.1039 | 0 | 0 | 2507.0981 | 0 | 0 | 0
12 | 119.641 | 477.66 | 2146.9715 | 124.2836 | 0 | 0 | 2022.6879 | 0 | 0 | 0
13 | 82.892 | 358.27 | 1602.3272 | 86.1086 | 0 | 0 | 1516.2186 | 0 | 0 | 0
14 | 87.738 | 333.19 | 1490.4999 | 91.1427 | 0 | 0 | 1399.3573 | 0 | 0 | 0
15 | 106.186 | 229.93 | 1025.5589 | 110.3065 | 0 | 0 | 915.2524 | 0 | 0 | 0
16 | 98.846 | 202.24 | 913.1634 | 102.6817 | 0 | 0 | 810.4817 | 0 | 0 | 0
17 | 88.262 | 121.2 | 529.8237 | 91.687 | 0 | 0 | 438.1367 | 0 | 0 | 0
18 | 94.791 | 11.75 | 8.8537 | 8.8537 | 0 | 0 | 0 | 0 | 0 | 89.6156
19 | 90.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.9079
20 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.7253
21 | 87.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.5838
22 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.57
23 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.4148
24 | 91.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.739
25 | 86.4 | 0 | 0 | 0 | 0 | 0 | 0 | 86.4 | 0 | 0
26 | 93.6 | 0 | 0 | 0 | 0 | 0 | 0 | 93.6 | 0 | 0
27 | 86.4 | 0 | 0 | 0 | 0 | 0 | 0 | 86.4 | 0 | 0
28 | 89.6 | 0 | 0 | 0 | 0 | 0 | 0 | 47.679 | 0 | 43.5477
29 | 83.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.4286
30 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.57
31 | 76.8 | 17.05 | 28.1682 | 28.1682 | 0 | 0 | 0 | 0 | 0 | 51.612
32 | 84.462 | 28.41 | 102.4365 | 87.7395 | -14.697 | 0 | 0 | 0 | 0 | 0
33 | 178.704 | 104.38 | 457.6724 | 185.6386 | -272.0339 | 0 | 0 | 0 | 0 | 0
34 | 122.023 | 121.1 | 528.227 | 126.7581 | -401.4689 | 0 | 0 | 0 | 0 | 0
35 | 151.211 | 155.66 | 681.9078 | 157.0787 | -349.8113 | 0 | 175.0178 | 0 | 0 | 0
36 | 234.813 | 203.34 | 896.5508 | 243.9249 | 0 | 0 | 652.626 | 0 | 0 | 0
37 | 410.829 | 266.08 | 1181.978 | 426.7711 | 0 | 0 | 755.2069 | 0 | 0 | 0
38 | 797.587 | 196.09 | 861.4569 | 828.5372 | 0 | 0 | 32.9197 | 0 | 0 | 0
39 | 1144.168 | 132.09 | 570.7245 | 570.7245 | 0 | 0 | 0 | 594.763 | 0 | 0
40 | 1195.968 | 35.28 | 129.5815 | 129.5815 | 0 | 0 | 0 | 1071.227 | 0 | 0
41 | 1539.811 | 39.2 | 149.1807 | 149.1807 | 0 | 0 | 0 | 1396.203 | 0 | 0
42 | 1385.46 | 5.87 | 0 | 0 | 0 | 0 | 0 | 1385.46 | 0 | 0
43 | 1622.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1622.4 | 0 | 0
44 | 953.6 | 0 | 0 | 0 | 0 | 0 | 0 | 953.6 | 0 | 0
45 | 1364 | 0 | 0 | 0 | 0 | 0 | 0 | 1364 | 0 | 0
46 | 1566.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1260.526 | 0 | 317.7434
47 | 1546.4 | 0 | 0 | 0 | 0 | 0 | 0 | 954.4 | 0 | 614.9724
48 | 1576 | 0 | 0 | 0 | 0 | 0 | 0 | 1576 | 0 | 0
49 | 1492 | 0 | 0 | 0 | 0 | 0 | 0 | 1492 | 0 | 0
50 | 1759.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1759.2 | 0 | 0
51 | 1702.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1702.4 | 0 | 0
52 | 1202.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1202.4 | 0 | 0
53 | 1508.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1508.8 | 0 | 0
54 | 1304 | 0 | 0 | 0 | 0 | 0 | 0 | 1304 | 0 | 0
55 | 1408 | 33.28 | 80.0752 | 80.0752 | 0 | 0 | 0 | 1330.916 | 0 | 0
56 | 1348.873 | 132.21 | 583.0499 | 583.0499 | 0 | 0 | 0 | 787.603 | 0 | 0
57 | 1465.448 | 278.69 | 1280.8774 | 1280.8774 | 0 | 0 | 0 | 232.418 | 0 | 0
58 | 1762.864 | 382.05 | 1735.1737 | 1735.1737 | 0 | 0 | 0 | 92.508 | 0 | 0
59 | 1691.064 | 277.02 | 1232.8504 | 1232.8504 | 0 | 0 | 0 | 504.267 | 0 | 0
60 | 1680.269 | 533.11 | 2378.9065 | 1745.4714 | -614.9724 | 0 | 18.4627 | 0 | 0 | 0
61 | 1623.593 | 450.13 | 2004.7332 | 1686.5961 | -318.1371 | 0 | 0 | 0 | 0 | 0
62 | 1593.084 | 499.13 | 2231.015 | 1654.9032 | -104.9016 | 0 | 471.2101 | 0 | 0 | 0
63 | 1600.536 | 137.97 | 595.2029 | 595.2029 | 0 | 0 | 0 | 1027.567 | 0 | 0
64 | 2071.826 | 199.75 | 896.5384 | 896.5384 | 0 | 0 | 0 | 1208.778 | 0 | 0
65 | 1766.78 | 172.64 | 758.1748 | 758.1748 | 0 | 0 | 0 | 1036.927 | 0 | 0
66 | 1972.144 | 24.34 | 45.6388 | 45.6388 | 0 | 0 | 0 | 1928.21 | 0 | 0
67 | 1702.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1702.4 | 0 | 0
68 | 1880.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1880.8 | 0 | 0
69 | 1820 | 0 | 0 | 0 | 0 | 0 | 0 | 1820 | 0 | 0
70 | 1544 | 0 | 0 | 0 | 0 | 0 | 0 | 1238.126 | 0 | 317.7434
71 | 1548 | 0 | 0 | 0 | 0 | 0 | 0 | 956 | 0 | 614.9724
72 | 1748 | 0 | 0 | 0 | 0 | 0 | 0 | 1748 | 0 | 0
73 | 1668.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1668.8 | 0 | 0
74 | 1640 | 0 | 0 | 0 | 0 | 0 | 0 | 1640 | 0 | 0
75 | 1404.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1404.8 | 0 | 0
76 | 1329.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1329.6 | 0 | 0
77 | 1424 | 0 | 0 | 0 | 0 | 0 | 0 | 1424 | 0 | 0
78 | 1144.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1144.8 | 0 | 0
79 | 1503.2 | 53.12 | 127.3814 | 127.3814 | 0 | 0 | 0 | 1380.577 | 0 | 0
80 | 1213.663 | 213.5 | 950.3505 | 950.3505 | 0 | 0 | 0 | 298.813 | 0 | 0
81 | 1603.942 | 491.73 | 2294.7384 | 1666.1826 | -614.9724 | 0 | 13.5834 | 0 | 0 | 0
82 | 1563.398 | 634.77 | 2903.667 | 1624.0653 | -423.0387 | 0 | 856.5631 | 0 | 0 | 0
83 | 1507.155 | 796.52 | 3587.2785 | 1565.6398 | 0 | 0 | 2021.6387 | 0 | 0 | 0
84 | 1580.699 | 787.57 | 3514.0458 | 1642.0376 | 0 | 0 | 1872.0082 | 0 | 0 | 0
85 | 1729.469 | 763.71 | 3414.3829 | 1796.5806 | 0 | 0 | 1617.8023 | 0 | 0 | 0
86 | 1487.795 | 798.76 | 3583.813 | 1545.5285 | 0 | 0 | 2038.2845 | 0 | 0 | 0
87 | 1353.09 | 576.57 | 2622.4927 | 1405.5963 | 0 | 0 | 1216.8964 | 0 | 0 | 0
88 | 1713.845 | 504.54 | 2341.5771 | 1780.3503 | 0 | 0 | 561.2267 | 0 | 0 | 0
89 | 1749.959 | 265.01 | 1160.6347 | 1160.6347 | 0 | 0 | 0 | 632.68 | 0 | 0
90 | 1614.836 | 38 | 85.7357 | 85.7357 | 0 | 0 | 0 | 1532.303 | 0 | 0
91 | 1603.201 | 0 | 0 | 0 | 0 | 0 | 0 | 1603.201 | 0 | 0
92 | 1192 | 0 | 0 | 0 | 0 | 0 | 0 | 1192 | 0 | 0
93 | 1322.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1322.4 | 0 | 0
94 | 1403.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1097.326 | 0 | 317.7434
95 | 1576.8 | 0 | 0 | 0 | 0 | 0 | 0 | 984.8 | 0 | 614.9724
96 | 1240.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1240.8 | 0 | 0
97 | 1476 | 0 | 0 | 0 | 0 | 0 | 0 | 1476 | 0 | 0
98 | 1014.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1014.4 | 0 | 0
99 | 1200.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1200.8 | 0 | 0
100 | 1056 | 0 | 0 | 0 | 0 | 0 | 0 | 1056 | 0 | 0
101 | 1512.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1512.8 | 0 | 0
102 | 1194.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1194.4 | 0 | 0
103 | 1352.8 | 52.8 | 124.3003 | 124.3003 | 0 | 0 | 0 | 1233.143 | 0 | 0
104 | 1276.497 | 282.7 | 1256.5652 | 1256.5652 | 0 | 0 | 0 | 66.871 | 0 | 0
105 | 1178.106 | 524.59 | 2456.6164 | 1223.8221 | -614.9724 | 0 | 617.8219 | 0 | 0 | 0
106 | 1381.448 | 729.17 | 3340.044 | 1435.0547 | -423.0387 | 0 | 1481.9505 | 0 | 0 | 0
107 | 1214.49 | 872.15 | 3918.1669 | 1261.618 | 0 | 0 | 2656.5489 | 0 | 0 | 0
108 | 1201.671 | 950.07 | 4215.7772 | 1248.3015 | 0 | 0 | 2967.4756 | 0 | 0 | 0
109 | 1248.417 | 949.58 | 4200.3353 | 1296.8615 | 0 | 0 | 2903.4738 | 0 | 0 | 0
110 | 1246.649 | 870.91 | 3881.9791 | 1295.0249 | 0 | 0 | 2586.9542 | 0 | 0 | 0
111 | 987.594 | 726.63 | 3290.5138 | 1025.9173 | 0 | 0 | 2264.5964 | 0 | 0 | 0
112 | 489.888 | 520.09 | 2406.4774 | 508.898 | 0 | 0 | 1897.5794 | 0 | 0 | 0
113 | 193.991 | 277.32 | 1210.2823 | 201.5188 | 0 | 0 | 1008.7636 | 0 | 0 | 0
114 | 170.644 | 43.35 | 93.6659 | 93.6659 | 0 | 0 | 0 | 0 | 0 | 83.5999
115 | 118.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.9945
116 | 127.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132.136
117 | 100.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.7115
118 | 94.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.0632
119 | 94.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.0632
120 | 99.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.0494
121 | 92.8 | 0 | 0 | 0 | 0 | 0 | 0 | 92.8 | 0 | 0
122 | 91.2 | 0 | 0 | 0 | 0 | 0 | 0 | 91.2 | 0 | 0
123 | 85.6 | 0 | 0 | 0 | 0 | 0 | 0 | 85.6 | 0 | 0
124 | 93.6 | 0 | 0 | 0 | 0 | 0 | 0 | 93.6 | 0 | 0
125 | 89.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0.203 | 0 | 92.866
126 | 93.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.2321
127 | 81.6 | 59.95 | 145.7568 | 84.7665 | -60.9903 | 0 | 0 | 0 | 0 | 0
128 | 95.06 | 231.48 | 1022.2233 | 98.7488 | -614.9724 | 0 | 308.5022 | 0 | 0 | 0
129 | 615.277 | 482.79 | 2246.2678 | 639.1537 | -362.0484 | 0 | 1245.0657 | 0 | 0 | 0
130 | 1487.855 | 454.39 | 2057.2915 | 1545.5908 | 0 | 0 | 511.7007 | 0 | 0 | 0
131 | 1570.749 | 865.42 | 3859.9377 | 1631.7015 | 0 | 0 | 2228.2362 | 0 | 0 | 0
132 | 1374.539 | 929.6 | 4106.2851 | 1427.8776 | 0 | 0 | 2678.4074 | 0 | 0 | 0
133 | 1744.337 | 768.74 | 3403.9388 | 1812.0256 | 0 | 0 | 1591.9132 | 0 | 0 | 0
134 | 1288.096 | 442.06 | 1968.0665 | 1338.0802 | 0 | 0 | 629.9863 | 0 | 0 | 0
135 | 1540.824 | 681.24 | 3086.3564 | 1600.6153 | 0 | 0 | 1485.7411 | 0 | 0 | 0
136 | 1378.996 | 392.63 | 1810.512 | 1432.5076 | 0 | 0 | 378.0044 | 0 | 0 | 0
137 | 1206.845 | 184.22 | 799.5369 | 799.5369 | 0 | 0 | 0 | 437.175 | 0 | 0
138 | 1353.643 | 38.87 | 88.1893 | 88.1893 | 0 | 0 | 0 | 1268.748 | 0 | 0
139 | 1672.005 | 0 | 0 | 0 | 0 | 0 | 0 | 1672.005 | 0 | 0
140 | 1202.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1202.4 | 0 | 0
141 | 1490.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1490.4 | 0 | 0
142 | 825.6 | 0 | 0 | 0 | 0 | 0 | 0 | 519.726 | 0 | 317.7434
143 | 1327.2 | 0 | 0 | 0 | 0 | 0 | 0 | 735.2 | 0 | 614.9724
144 | 1368.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1368.8 | 0 | 0
145 | 1056 | 0 | 0 | 0 | 0 | 0 | 0 | 1056 | 0 | 0
146 | 1168.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1168.8 | 0 | 0
147 | 1128 | 0 | 0 | 0 | 0 | 0 | 0 | 1128 | 0 | 0
148 | 982.4 | 0 | 0 | 0 | 0 | 0 | 0 | 982.4 | 0 | 0
149 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 904 | 0 | 0
150 | 892.8 | 0 | 0 | 0 | 0 | 0 | 0 | 892.8 | 0 | 0
151 | 1122.4 | 56.74 | 134.1647 | 134.1647 | 0 | 0 | 0 | 993.247 | 0 | 0
152 | 820.686 | 302.44 | 1340.5443 | 852.5325 | -488.0118 | 0 | 0 | 0 | 0 | 0
153 | 1276.219 | 548.14 | 2554.6297 | 1325.7434 | -549.9993 | 0 | 678.887 | 0 | 0 | 0
154 | 1102.819 | 756.42 | 3418.7656 | 1145.6136 | 0 | 0 | 2273.152 | 0 | 0 | 0
155 | 1394.158 | 904.1 | 3982.1739 | 1448.258 | 0 | 0 | 2533.9159 | 0 | 0 | 0
156 | 1343.063 | 978.5 | 4248.5525 | 1395.1802 | 0 | 0 | 2853.3723 | 0 | 0 | 0
157 | 1117.045 | 976.48 | 4225.5762 | 1160.3917 | 0 | 0 | 3065.1846 | 0 | 0 | 0
158 | 1320.721 | 893.64 | 3894.6473 | 1371.9712 | 0 | 0 | 2522.676 | 0 | 0 | 0
159 | 965.839 | 743.6 | 3300.2609 | 1003.3181 | 0 | 0 | 2296.9427 | 0 | 0 | 0
160 | 1201.115 | 536.56 | 2443.5939 | 1247.724 | 0 | 0 | 1195.8699 | 0 | 0 | 0
161 | 1181.242 | 289.74 | 1257.7006 | 1227.0798 | 0 | 0 | 30.6208 | 0 | 0 | 0
162 | 1081.511 | 49.78 | 121.0062 | 121.0062 | 0 | 0 | 0 | 965.025 | 0 | 0
163 | 1008 | 0 | 0 | 0 | 0 | 0 | 0 | 1008 | 0 | 0
164 | 1229.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1229.6 | 0 | 0
165 | 845.6 | 0 | 0 | 0 | 0 | 0 | 0 | 845.6 | 0 | 0
166 | 1182.4 | 0 | 0 | 0 | 0 | 0 | 0 | 876.526 | 0 | 317.7434
167 | 1105.6 | 0 | 0 | 0 | 0 | 0 | 0 | 513.6 | 0 | 614.9724
168 | 876.8 | 0 | 0 | 0 | 0 | 0 | 0 | 876.8 | 0 | 0
169 | 1152.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1152.8 | 0 | 0
170 | 1130.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1130.4 | 0 | 0
171 | 1128.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1128.8 | 0 | 0
172 | 1064.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1064.8 | 0 | 0
173 | 1179.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1179.2 | 0 | 0
174 | 769.6 | 0 | 0 | 0 | 0 | 0 | 0 | 769.6 | 0 | 0
175 | 1032.8 | 53.85 | 122.0003 | 122.0003 | 0 | 0 | 0 | 915.357 | 0 | 0
176 | 1022.571 | 223.67 | 979.4589 | 979.4589 | 0 | 0 | 0 | 79.7 | 0 | 0
177 | 1349.006 | 243.7 | 1097.2126 | 1097.2126 | 0 | 0 | 0 | 292.78 | 0 | 0
178 | 1477.914 | 188.21 | 820.4968 | 820.4968 | 0 | 0 | 0 | 688.067 | 0 | 0
179 | 1484.496 | 153.65 | 654.5852 | 654.5852 | 0 | 0 | 0 | 854.363 | 0 | 0
180 | 1349.631 | 240.6 | 1043.5905 | 1043.5905 | 0 | 0 | 0 | 345.024 | 0 | 0
181 | 1462.071 | 334.34 | 1462.7929 | 1462.7929 | 0 | 0 | 0 | 53.921 | 0 | 0
182 | 1295.145 | 645.92 | 2856.5863 | 1345.4028 | -614.9724 | 0 | 896.2111 | 0 | 0 | 0
183 | 1332.189 | 643.72 | 2899.1254 | 1383.8843 | -423.0387 | 0 | 1092.2024 | 0 | 0 | 0
184 | 1434.587 | 246.14 | 1109.3012 | 1109.3012 | 0 | 0 | 0 | 366.724 | 0 | 0
185 | 1105.581 | 157.18 | 688.8626 | 688.8626 | 0 | 0 | 0 | 442.451 | 0 | 0
186 | 1217.803 | 15.26 | 24.3537 | 24.3537 | 0 | 0 | 0 | 1194.359 | 0 | 0
187 | 1003.211 | 0 | 0 | 0 | 0 | 0 | 0 | 1003.211 | 0 | 0
188 | 1195.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1195.2 | 0 | 0
189 | 1054.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1054.4 | 0 | 0
190 | 1257.6 | 0 | 0 | 0 | 0 | 0 | 0 | 951.726 | 0 | 317.7434
191 | 1286.4 | 0 | 0 | 0 | 0 | 0 | 0 | 694.4 | 0 | 614.9724
192 | 1148 | 0 | 0 | 0 | 0 | 0 | 0 | 1148 | 0 | 0
193 | 1193.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1193.6 | 0 | 0
194 | 937.6 | 0 | 0 | 0 | 0 | 0 | 0 | 937.6 | 0 | 0
195 | 1222.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1222.4 | 0 | 0
196 | 1073.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1073.6 | 0 | 0
197 | 942.4 | 0 | 0 | 0 | 0 | 0 | 0 | 942.4 | 0 | 0
198 | 1051.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1051.2 | 0 | 0
199 | 951.2 | 50.52 | 111.0233 | 111.0233 | 0 | 0 | 0 | 844.324 | 0 | 0
200 | 1114.771 | 251.16 | 1105.2966 | 1105.2966 | 0 | 0 | 0 | 50.763 | 0 | 0
201 | 1167.854 | 534.22 | 2471.6915 | 1213.1723 | -614.9724 | 0 | 643.5468 | 0 | 0 | 0
202 | 1664.173 | 736.26 | 3301.3371 | 1728.7508 | -423.0387 | 0 | 1149.5476 | 0 | 0 | 0
203 | 1338.632 | 879.42 | 3841.0304 | 1390.5773 | 0 | 0 | 2450.4531 | 0 | 0 | 0
204 | 1317.153 | 957.52 | 4111.7616 | 1368.2648 | 0 | 0 | 2743.4968 | 0 | 0 | 0
205 | 1355.422 | 953.81 | 4082.4933 | 1408.0188 | 0 | 0 | 2674.4745 | 0 | 0 | 0
206 | 1226.996 | 674.24 | 2949.7972 | 1274.6093 | 0 | 0 | 1675.188 | 0 | 0 | 0
207 | 1258.144 | 534.86 | 2371.8333 | 1306.966 | 0 | 0 | 1064.8673 | 0 | 0 | 0
208 | 1216.588 | 276.81 | 1243.9801 | 1243.9801 | 0 | 0 | 0 | 19.077 | 0 | 0
209 | 1274.12 | 227.69 | 995.953 | 995.953 | 0 | 0 | 0 | 315.371 | 0 | 0
210 | 1113.621 | 41.65 | 102.2828 | 102.2828 | 0 | 0 | 0 | 1015.159 | 0 | 0
211 | 1163.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1163.2 | 0 | 0
212 | 1064 | 0 | 0 | 0 | 0 | 0 | 0 | 1064 | 0 | 0
213 | 1449.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1449.6 | 0 | 0
214 | 1246.4 | 0 | 0 | 0 | 0 | 0 | 0 | 940.526 | 0 | 317.7434
215 | 1491.2 | 0 | 0 | 0 | 0 | 0 | 0 | 899.2 | 0 | 614.9724
216 | 1336.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1336.8 | 0 | 0
217 | 1711.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1711.2 | 0 | 0
218 | 1122.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1122.4 | 0 | 0
219 | 1392 | 0 | 0 | 0 | 0 | 0 | 0 | 1392 | 0 | 0
220 | 1262.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.4 | 0 | 0
221 | 1117.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1117.6 | 0 | 0
222 | 1514.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1514.4 | 0 | 0
223 | 1350.4 | 47.44 | 98.7051 | 98.7051 | 0 | 0 | 0 | 1255.382 | 0 | 0
224 | 1353.11 | 288.76 | 1271.9894 | 1271.9894 | 0 | 0 | 0 | 128.636 | 0 | 0
225 | 1445.428 | 534.75 | 2489.4218 | 1501.5175 | -614.9724 | 0 | 372.9319 | 0 | 0 | 0
226 | 1336.752 | 734.82 | 3326.578 | 1388.6243 | -423.0387 | 0 | 1514.9149 | 0 | 0 | 0
227 | 1366.848 | 874.29 | 3864.6331 | 1419.8882 | 0 | 0 | 2444.7449 | 0 | 0 | 0
228 | 1423.45 | 954.03 | 4155.7446 | 1478.6866 | 0 | 0 | 2677.058 | 0 | 0 | 0
229 | 1626.909 | 542.36 | 2387.5172 | 1690.0408 | 0 | 0 | 697.4764 | 0 | 0 | 0
230 | 1552.301 | 666.6 | 2945.267 | 1612.5376 | 0 | 0 | 1332.7294 | 0 | 0 | 0
231 | 1372.937 | 710.42 | 3179.5383 | 1426.2135 | 0 | 0 | 1753.3248 | 0 | 0 | 0
232 | 1588.328 | 518.45 | 2379.0779 | 1649.9627 | 0 | 0 | 729.1152 | 0 | 0 | 0
233 | 1609.75 | 207.82 | 909.8745 | 909.8745 | 0 | 0 | 0 | 733.864 | 0 | 0
234 | 1634.626 | 42.19 | 106.0911 | 106.0911 | 0 | 0 | 0 | 1532.498 | 0 | 0
235 | 1760.002 | 0 | 0 | 0 | 0 | 0 | 0 | 1760.002 | 0 | 0
236 | 1500 | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 0 | 0
237 | 1500 | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 0 | 0
238 | 1466.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1160.526 | 0 | 317.7434
239 | 1682.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1090.4 | 0 | 614.9724
240 | 1397.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1397.6 | 0 | 0
241 | 1472.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1472.8 | 0 | 0
242 | 1350.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1350.4 | 0 | 0
243 | 1287.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1287.2 | 0 | 0
244 | 1179.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1179.2 | 0 | 0
245 | 1111.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1111.2 | 0 | 0
246 | 1189.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1189.6 | 0 | 0
247 | 1056 | 39.39 | 77.4325 | 77.4325 | 0 | 0 | 0 | 981.46 | 0 | 0
248 | 1007.057 | 218.76 | 967.3765 | 967.3765 | 0 | 0 | 0 | 75.817 | 0 | 0
249 | 1526.413 | 231.29 | 1044.1941 | 1044.1941 | 0 | 0 | 0 | 521.225 | 0 | 0
250 | 1751.451 | 590.39 | 2656.2913 | 1819.4156 | -614.9724 | 0 | 221.9032 | 0 | 0 | 0
251 | 1601.404 | 863.35 | 3778.189 | 1663.5471 | -423.0387 | 0 | 1691.6032 | 0 | 0 | 0
252 | 1468.113 | 804.31 | 3484.7713 | 1525.0828 | 0 | 0 | 1959.6885 | 0 | 0 | 0
253 | 1613.967 | 632.07 | 2747.195 | 1676.5966 | 0 | 0 | 1070.5984 | 0 | 0 | 0
254 | 1643.485 | 354.16 | 1547.6643 | 1547.6643 | 0 | 0 | 0 | 0 | 0 | 159.5957
255 | 1670.927 | 646.87 | 2858.13 | 1735.7669 | -177.6128 | 0 | 944.7503 | 0 | 0 | 0
256 | 1625.599 | 202.23 | 891.9313 | 891.9313 | 0 | 0 | 0 | 766.986 | 0 | 0
257 | 1615.953 | 102.83 | 435.8025 | 435.8025 | 0 | 0 | 0 | 1196.43 | 0 | 0
258 | 1849.735 | 20.67 | 46.2538 | 46.2538 | 0 | 0 | 0 | 1805.209 | 0 | 0
259 | 1528.006 | 0 | 0 | 0 | 0 | 0 | 0 | 1528.006 | 0 | 0
260 | 1338.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1338.4 | 0 | 0
261 | 1358.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1358.4 | 0 | 0
262 | 1418.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1112.526 | 0 | 317.7434
263 | 1347.2 | 0 | 0 | 0 | 0 | 0 | 0 | 755.2 | 0 | 614.9724
264 | 1475.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1475.2 | 0 | 0
265 | 1247.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1247.2 | 0 | 0
266 | 1436 | 0 | 0 | 0 | 0 | 0 | 0 | 1436 | 0 | 0
267 | 1268.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1268.8 | 0 | 0
268 | 1268.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1268.8 | 0 | 0
269 | 1345.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1345.6 | 0 | 0
270 | 1118.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1118.4 | 0 | 0
271 | 1312.8 | 19.09 | 29.8002 | 29.8002 | 0 | 0 | 0 | 1284.113 | 0 | 0
272 | 1080.054 | 274.64 | 1201.2748 | 1121.9652 | -79.3096 | 0 | 0 | 0 | 0 | 0
273 | 1017.97 | 438.49 | 2009.7963 | 1057.4721 | -614.9724 | 0 | 337.3518 | 0 | 0 | 0
274 | 1165.131 | 295.04 | 1300.4298 | 1210.3436 | -90.0862 | 0 | 0 | 0 | 0 | 0
275 | 1340.908 | 321.34 | 1395.8399 | 1392.9416 | -2.8983 | 0 | 0 | 0 | 0 | 0
276 | 1421.717 | 712.67 | 3039.5417 | 1476.8864 | -250.7446 | 0 | 1311.9107 | 0 | 0 | 0
277 | 1076.722 | 568.89 | 2436.8043 | 1118.5039 | 0 | 0 | 1318.3004 | 0 | 0 | 0
278 | 1233.429 | 706.63 | 3029.2575 | 1281.2919 | 0 | 0 | 1747.9656 | 0 | 0 | 0
279 | 966.192 | 208.75 | 899.5197 | 899.5197 | 0 | 0 | 0 | 100.274 | 0 | 0
280 | 1205.397 | 230.16 | 1016.0487 | 1016.0487 | 0 | 0 | 0 | 227.303 | 0 | 0
281 | 1237.532 | 9.79 | 16.009 | 16.009 | 0 | 0 | 0 | 1222.121 | 0 | 0
282 | 859.624 | 8.41 | 1.0232 | 1.0232 | 0 | 0 | 0 | 858.639 | 0 | 0
283 | 1175.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1175.2 | 0 | 0
284 | 1189.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1189.6 | 0 | 0
285 | 1346.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1346.4 | 0 | 0
286 | 1161.6 | 0 | 0 | 0 | 0 | 0 | 0 | 992.526 | 0 | 175.6349
287 | 1086.4 | 0 | 0 | 0 | 0 | 0 | 0 | 494.4 | 0 | 614.9724
288 | 136.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142.1085
289 | 106.4 | 0 | 0 | 0 | 0 | 0 | 0 | 106.4 | 0 | 0
290 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0
291 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 0
292 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0
293 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 92 | 0 | 0
294 | 84.8 | 0 | 0 | 0 | 0 | 0 | 0 | 84.8 | 0 | 0
295 | 82.4 | 45.81 | 99.1072 | 85.5975 | -13.5097 | 0 | 0 | 0 | 0 | 0
296 | 81.362 | 279.68 | 1218.5263 | 84.5192 | -614.9724 | 0 | 519.0346 | 0 | 0 | 0
297 | 804.961 | 524.59 | 2401.6106 | 836.1973 | -409.5301 | 0 | 1155.8832 | 0 | 0 | 0
298 | 971.201 | 727.41 | 3198.5453 | 1008.8882 | 0 | 0 | 2189.6571 | 0 | 0 | 0
299 | 1378.581 | 872.3 | 3704.0744 | 1432.0765 | 0 | 0 | 2271.9979 | 0 | 0 | 0
300 | 1301.865 | 951.32 | 3965.6205 | 1352.3835 | 0 | 0 | 2613.237 | 0 | 0 | 0
301 | 1411.199 | 911.94 | 3814.4297 | 1465.9602 | 0 | 0 | 2348.4695 | 0 | 0 | 0
302 | 1430.445 | 651.43 | 2791.367 | 1485.9531 | 0 | 0 | 1305.414 | 0 | 0 | 0
303 | 1147.683 | 392.72 | 1710.8906 | 1192.2185 | 0 | 0 | 518.6721 | 0 | 0 | 0
304 | 1193.172 | 225.94 | 991.0145 | 991.0145 | 0 | 0 | 0 | 239.177 | 0 | 0
305 | 1254.203 | 147.29 | 631.639 | 631.639 | 0 | 0 | 0 | 646.159 | 0 | 0
306 | 1409.776 | 32.57 | 81.382 | 81.382 | 0 | 0 | 0 | 1331.434 | 0 | 0
307 | 1164.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1164.8 | 0 | 0
308 | 1167.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1167.2 | 0 | 0
309 | 1375.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1375.2 | 0 | 0
310 | 1362.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1056.526 | 0 | 317.7434
311 | 1214.4 | 0 | 0 | 0 | 0 | 0 | 0 | 622.4 | 0 | 614.9724
312 | 949.6 | 0 | 0 | 0 | 0 | 0 | 0 | 949.6 | 0 | 0
313 | 1832.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1832.8 | 0 | 0
314 | 1784.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1784.8 | 0 | 0
315 | 1888 | 0 | 0 | 0 | 0 | 0 | 0 | 1888 | 0 | 0
316 | 2028.8 | 0 | 0 | 0 | 0 | 0 | 0 | 2028.8 | 0 | 0
317 | 2156.8 | 0 | 0 | 0 | 0 | 0 | 0 | 2156.8 | 0 | 0
318 | 2129.6 | 0 | 0 | 0 | 0 | 0 | 0 | 2129.6 | 0 | 0
319 | 1976.8 | 49.36 | 104.8434 | 104.8434 | 0 | 0 | 0 | 1875.873 | 0 | 0
320 | 1127.549 | 293.77 | 1287.5964 | 1171.3033 | -116.2932 | 0 | 0 | 0 | 0 | 0
321 | 1638.403 | 544.43 | 2490.2435 | 1701.9808 | -614.9724 | 0 | 173.2903 | 0 | 0 | 0
322 | 1940.862 | 730.38 | 3176.1788 | 2016.1767 | -306.7455 | 0 | 853.2566 | 0 | 0 | 0
323 | 2188.553 | 903.85 | 3734.0699 | 2273.4792 | 0 | 0 | 1460.5906 | 0 | 0 | 0
324 | 2025.649 | 789.39 | 3271.8849 | 2104.2538 | 0 | 0 | 1167.6311 | 0 | 0 | 0
325 | 1943.684 | 665.04 | 2784.7966 | 2019.1082 | 0 | 0 | 765.6884 | 0 | 0 | 0
326 | 2335.268 | 678.67 | 2845.415 | 2425.8875 | 0 | 0 | 419.5275 | 0 | 0 | 0
327 | 2168.745 | 433.48 | 1869.3447 | 1869.3447 | 0 | 0 | 0 | 186.091 | 0 | 190.2457
328 | 1973.613 | 513.85 | 2261.9215 | 2050.1986 | -211.723 | 0 | 0 | 0 | 0 | 0
329 | 2279.797 | 303.55 | 1304.8001 | 1304.8001 | 0 | 0 | 0 | 1023.738 | 0 | 0
330 | 1609.172 | 63.35 | 175.5923 | 175.5923 | 0 | 0 | 0 | 1440.139 | 0 | 0
331 | 2156.812 | 0 | 0 | 0 | 0 | 0 | 0 | 2156.812 | 0 | 0
332 | 2172.8 | 0 | 0 | 0 | 0 | 0 | 0 | 2172.8 | 0 | 0
333 | 2000 | 0 | 0 | 0 | 0 | 0 | 0 | 2000 | 0 | 0
334 | 1667.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1361.326 | 0 | 317.7434
335 | 2352 | 0 | 0 | 0 | 0 | 0 | 0 | 1760 | 0 | 614.9724
336 | 2075.2 | 0 | 0 | 0 | 0 | 0 | 0 | 2075.2 | 0 | 0
337 | 1518.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1518.4 | 0 | 0
338 | 1494.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1494.4 | 0 | 0
339 | 1260 | 0 | 0 | 0 | 0 | 0 | 0 | 1260 | 0 | 0
340 | 1234.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.4 | 0 | 0
341 | 1272 | 0 | 0 | 0 | 0 | 0 | 0 | 1272 | 0 | 0
342 | 1414.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1414.4 | 0 | 0
343 | 1373.6 | 34.39 | 68.1643 | 68.1643 | 0 | 0 | 0 | 1307.982 | 0 | 0
344 | 996.612 | 237.33 | 1034.0626 | 1034.0626 | 0 | 0 | 0 | 1.177 | 0 | 0
345 | 1176.84 | 221.71 | 980.4759 | 980.4759 | 0 | 0 | 0 | 232.99 | 0 | 0
346 | 1297.88 | 399.42 | 1733.7132 | 1348.2439 | -385.4693 | 0 | 0 | 0 | 0 | 0
347 | 1357.844 | 537.12 | 2280.3322 | 1410.5348 | -614.9724 | 0 | 254.825 | 0 | 0 | 0
348 | 1435.047 | 662.41 | 2766.2612 | 1490.7326 | -37.5705 | 0 | 1237.9582 | 0 | 0 | 0
349 | 1435.033 | 558.37 | 2358.7225 | 1490.7191 | 0 | 0 | 868.0034 | 0 | 0 | 0
350 | 1087.883 | 609.01 | 2596.1694 | 1130.098 | 0 | 0 | 1466.0714 | 0 | 0 | 0
351 | 1211.392 | 398.02 | 1742.2761 | 1258.3998 | 0 | 0 | 483.8763 | 0 | 0 | 0
352 | 1440.601 | 115.06 | 486.7694 | 486.7694 | 0 | 0 | 0 | 972.015 | 0 | 0
353 | 1275.894 | 25.47 | 84.6532 | 84.6532 | 0 | 0 | 0 | 1194.403 | 0 | 0
354 | 1244.187 | 3.91 | 0 | 0 | 0 | 0 | 0 | 1244.187 | 0 | 0
355 | 798.4 | 0 | 0 | 0 | 0 | 0 | 0 | 798.4 | 0 | 0
356 | 1210.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1210.4 | 0 | 0
357 | 1458.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1458.4 | 0 | 0
358 | 1131.2 | 0 | 0 | 0 | 0 | 0 | 0 | 825.326 | 0 | 317.7434
359 | 1050.4 | 0 | 0 | 0 | 0 | 0 | 0 | 458.4 | 0 | 614.9724
360 | 949.6 | 0 | 0 | 0 | 0 | 0 | 0 | 949.6 | 0 | 0
361 | 1194.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1194.4 | 0 | 0
362 | 1084.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1084.8 | 0 | 0
363 | 1221.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1221.6 | 0 | 0
364 | 1077.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1077.6 | 0 | 0
365 | 1200.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1200.8 | 0 | 0
366 | 1140 | 0 | 0 | 0 | 0 | 0 | 0 | 1140 | 0 | 0
367 | 1037.6 | 11.89 | 11.1474 | 11.1474 | 0 | 0 | 0 | 1026.869 | 0 | 0
368 | 866.892 | 129.2 | 562.5689 | 562.5689 | 0 | 0 | 0 | 325.338 | 0 | 0
369 | 1066.826 | 340.25 | 1546.9309 | 1108.2239 | -438.707 | 0 | 0 | 0 | 0 | 0
370 | 1366.055 | 562.96 | 2499.4401 | 1419.0644 | -599.3041 | 0 | 481.0715 | 0 | 0 | 0
371 | 1574.613 | 770.93 | 3324.9335 | 1635.7155 | 0 | 0 | 1689.2181 | 0 | 0 | 0
372 | 1515.751 | 699.2 | 2994.6424 | 1574.5693 | 0 | 0 | 1420.0731 | 0 | 0 | 0
373 | 1570.042 | 422.53 | 1826.8701 | 1630.9671 | 0 | 0 | 195.903 | 0 | 0 | 0
374 | 1584.014 | 793.05 | 3399.1717 | 1645.4813 | 0 | 0 | 1753.6904 | 0 | 0 | 0
375 | 1443.606 | 481.16 | 2120.0156 | 1499.6248 | 0 | 0 | 620.3908 | 0 | 0 | 0
376 | 1857.159 | 430.66 | 1943.2453 | 1929.2256 | 0 | 0 | 14.0197 | 0 | 0 | 0
377 | 2051.354 | 144.93 | 631.8343 | 631.8343 | 0 | 0 | 0 | 1443.122 | 0 | 0
378 | 1864.668 | 26.75 | 70.5068 | 70.5068 | 0 | 0 | 0 | 1796.795 | 0 | 0
379 | 1687.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1687.2 | 0 | 0
380 | 1437.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1437.6 | 0 | 0
381 | 1798.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1798.4 | 0 | 0
382 | 1439.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1133.326 | 0 | 317.7434
383 | 1318.4 | 0 | 0 | 0 | 0 | 0 | 0 | 726.4 | 0 | 614.9724
384 | 1333.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1333.6 | 0 | 0
385 | 1427.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1427.2 | 0 | 0
386 | 1464.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1464.8 | 0 | 0
387 | 1109.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1109.6 | 0 | 0
388 | 1159.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1159.2 | 0 | 0
389 | 1433.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1433.6 | 0 | 0
390 | 1189.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1189.6 | 0 | 0
391 | 1440 | 34.43 | 64.0787 | 64.0787 | 0 | 0 | 0 | 1378.315 | 0 | 0
392 | 1042.494 | 226.37 | 988.3531 | 988.3531 | 0 | 0 | 0 | 91.061 | 0 | 0
393 | 1260.412 | 511.56 | 2370.8038 | 1309.322 | -614.9724 | 0 | 446.5094 | 0 | 0 | 0
394 | 1528.29 | 689.89 | 3115.9624 | 1587.5949 | -423.0387 | 0 | 1105.3288 | 0 | 0 | 0
395 | 1634.053 | 832.88 | 3680.5839 | 1697.462 | 0 | 0 | 1983.1219 | 0 | 0 | 0
396 | 1747.764 | 947.37 | 4125.8842 | 1815.5855 | 0 | 0 | 2310.2986 | 0 | 0 | 0
397 | 1461.828 | 534.8 | 2339.0289 | 1518.5539 | 0 | 0 | 820.475 | 0 | 0 | 0
398 | 1421.187 | 618.7 | 2718.4762 | 1476.3358 | 0 | 0 | 1242.1404 | 0 | 0 | 0
399 | 1580.373 | 605.48 | 2700.2618 | 1641.699 | 0 | 0 | 1058.5628 | 0 | 0 | 0
400 | 1462.36 | 87.1 | 361.1031 | 361.1031 | 0 | 0 | 0 | 1114.746 | 0 | 0
401 | 1717.244 | 32.33 | 115.7249 | 115.7249 | 0 | 0 | 0 | 1605.842 | 0 | 0
402 | 1611.558 | 14.71 | 28.671 | 28.671 | 0 | 0 | 0 | 1583.958 | 0 | 0
403 | 1616.357 | 0 | 0 | 0 | 0 | 0 | 0 | 1616.357 | 0 | 0
404 | 1480.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1480.8 | 0 | 0
405 | 1845.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1845.6 | 0 | 0
406 | 1497.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1191.726 | 0 | 317.7434
407 | 1532 | 0 | 0 | 0 | 0 | 0 | 0 | 940 | 0 | 614.9724
408 | 1503.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1503.2 | 0 | 0
409 | 1740.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1740.8 | 0 | 0
410 | 1453.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1453.6 | 0 | 0
411 | 1256 | 0 | 0 | 0 | 0 | 0 | 0 | 1256 | 0 | 0
412 | 1274.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.4 | 0 | 0
413 | 1436.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1436.8 | 0 | 0
414 | 1512.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1512.8 | 0 | 0
415 | 1361.6 | 31.79 | 58.2292 | 58.2292 | 0 | 0 | 0 | 1305.546 | 0 | 0
416 | 1307.476 | 282.57 | 1234.9612 | 1234.9612 | 0 | 0 | 0 | 118.647 | 0 | 0
417 | 1117.404 | 531.66 | 2458.0946 | 1160.7646 | -614.9724 | 0 | 682.3576 | 0 | 0 | 0
418 | 1558.331 | 725.51 | 3252.0614 | 1618.8016 | -423.0387 | 0 | 1210.221 | 0 | 0 | 0
419 | 1635.582 | 887.31 | 3867.6612 | 1699.0503 | 0 | 0 | 2168.6109 | 0 | 0 | 0
420 | 1614.236 | 972.14 | 4168.4295 | 1676.876 | 0 | 0 | 2491.5535 | 0 | 0 | 0
421 | 1599.883 | 875.32 | 3747.7665 | 1661.9661 | 0 | 0 | 2085.8005 | 0 | 0 | 0
422 | 1534.321 | 821.25 | 3544.0767 | 1593.8599 | 0 | 0 | 1950.2167 | 0 | 0 | 0
423 | 1869.297 | 702.38 | 3096.8899 | 1941.8346 | 0 | 0 | 1155.0553 | 0 | 0 | 0
424 | 1731.41 | 548.21 | 2484.099 | 1798.5969 | 0 | 0 | 685.5021 | 0 | 0 | 0
425 | 1852.086 | 301.42 | 1323.1807 | 1323.1807 | 0 | 0 | 0 | 578.333 | 0 | 0
426 | 1824.781 | 43.96 | 125.3941 | 125.3941 | 0 | 0 | 0 | 1704.071 | 0 | 0
427 | 1772.851 | 0 | 0 | 0 | 0 | 0 | 0 | 1772.851 | 0 | 0
428 | 1725.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1725.6 | 0 | 0
429 | 1548.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1548.8 | 0 | 0
430 | 1660 | 0 | 0 | 0 | 0 | 0 | 0 | 1354.126 | 0 | 317.7434
431 | 1914.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1322.4 | 0 | 614.9724
432 | 1842.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1842.4 | 0 | 0
433 | 1708 | 0 | 0 | 0 | 0 | 0 | 0 | 1708 | 0 | 0
434 | 1356.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1356.8 | 0 | 0
435 | 1073.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1073.6 | 0 | 0
436 | 1288.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1288.8 | 0 | 0
437 | 1396.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1396.8 | 0 | 0
438 | 1372 | 0 | 0 | 0 | 0 | 0 | 0 | 1372 | 0 | 0
439 | 1415.2 | 47.67 | 90.6856 | 90.6856 | 0 | 0 | 0 | 1327.902 | 0 | 0
440 | 1131.076 | 288.38 | 1260.5272 | 1174.9671 | -85.5601 | 0 | 0 | 0 | 0 | 0
441 | 1241.663 | 537.33 | 2478.2266 | 1289.8454 | -614.9724 | 0 | 573.4088 | 0 | 0 | 0
442 | 856.555 | 749.24 | 3318.9074 | 889.7934 | -337.4786 | 0 | 2091.6354 | 0 | 0 | 0
443 | 1284.095 | 904.69 | 3863.078 | 1333.924 | 0 | 0 | 2529.154 | 0 | 0 | 0
444 | 1493.401 | 985.72 | 4103.0263 | 1551.352 | 0 | 0 | 2551.6743 | 0 | 0 | 0
445 | 1383.033 | 972.52 | 4017.1078 | 1436.7012 | 0 | 0 | 2580.4066 | 0 | 0 | 0
446 | 1395.108 | 734.89 | 3093.3891 | 1449.2448 | 0 | 0 | 1644.1443 | 0 | 0 | 0
447 | 1147.015 | 538.33 | 2324.7339 | 1191.5246 | 0 | 0 | 1133.2092 | 0 | 0 | 0
448 | 1254.993 | 336.97 | 1492.4747 | 1303.6927 | 0 | 0 | 188.782 | 0 | 0 | 0
449 | 1593.632 | 106.79 | 454.0003 | 454.0003 | 0 | 0 | 0 | 1156.591 | 0 | 0
450 | 1540.045 | 22.7 | 62.0914 | 62.0914 | 0 | 0 | 0 | 1480.273 | 0 | 0
451 | 1594.407 | 0 | 0 | 0 | 0 | 0 | 0 | 1594.407 | 0 | 0
452 | 1601.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1601.6 | 0 | 0
453 | 1628.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1628.8 | 0 | 0
454 | 1475.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1475.2 | 0 | 0
455 | 1756 | 0 | 0 | 0 | 0 | 0 | 0 | 1756 | 0 | 0
456 | 1347.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1208.553 | 0 | 144.0272
457 | 1464 | 0 | 0 | 0 | 0 | 0 | 0 | 1464 | 0 | 0
458 | 1484 | 0 | 0 | 0 | 0 | 0 | 0 | 1484 | 0 | 0
459 | 1376.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1376.8 | 0 | 0
460 | 1298.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1298.4 | 0 | 0
461 | 1472 | 0 | 0 | 0 | 0 | 0 | 0 | 1472 | 0 | 0
462 | 1540.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1540.8 | 0 | 0
463 | 1121.6 | 41.47 | 74.7887 | 74.7887 | 0 | 0 | 0 | 457.605 | 0 | 614.9724
464 | 1325.723 | 277.07 | 1203.4522 | 1203.4522 | 0 | 0 | 0 | 0 | 0 | 173.7152
465 | 1431.814 | 525.68 | 2404.9161 | 1487.3752 | -614.9724 | 0 | 302.5685 | 0 | 0 | 0
466 | 1750.511 | 729.16 | 3194.6072 | 1818.4402 | -423.0387 | 0 | 953.1283 | 0 | 0 | 0
467 | 1780.377 | 626.87 | 2681.1592 | 1849.4641 | 0 | 0 | 831.6951 | 0 | 0 | 0
468 | 1557.127 | 577.21 | 2436.396 | 1617.5509 | 0 | 0 | 818.8451 | 0 | 0 | 0
469 | 1473.887 | 578.18 | 2427.2182 | 1531.0808 | 0 | 0 | 896.1374 | 0 | 0 | 0
470 | 1373.544 | 768.56 | 3187.1911 | 1426.844 | 0 | 0 | 1760.3471 | 0 | 0 | 0
471 | 1430.954 | 439.18 | 1884.744 | 1486.4818 | 0 | 0 | 398.2622 | 0 | 0 | 0
472 | 1796.545 | 398.27 | 1758.871 | 1758.871 | 0 | 0 | 0 | 103.377 | 0 | 0
473 | 1678.349 | 258.76 | 1131.088 | 1131.088 | 0 | 0 | 0 | 589.513 | 0 | 0
474 | 1629.66 | 50.79 | 152.108 | 152.108 | 0 | 0 | 0 | 1483.234 | 0 | 0
475 | 1404.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1404.8 | 0 | 0
476 | 1388.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1388.8 | 0 | 0
477 | 1344.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1344.8 | 0 | 0
478 | 1680.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1374.926 | 0 | 317.7434
479 | 1447.2 | 0 | 0 | 0 | 0 | 0 | 0 | 855.2 | 0 | 614.9724
480 | 1506.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1506.4 | 0 | 0
481 | 1360.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1360.8 | 0 | 0
482 | 1408 | 0 | 0 | 0 | 0 | 0 | 0 | 1408 | 0 | 0
483 | 1103.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1103.2 | 0 | 0
484 | 1368 | 0 | 0 | 0 | 0 | 0 | 0 | 1368 | 0 | 0
485 | 1242.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1242.4 | 0 | 0
486 | 1268.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1268.8 | 0 | 0
487 | 1385.6 | 10.77 | 6.0209 | 6.0209 | 0 | 0 | 0 | 1379.804 | 0 | 0
488 | 1391.679 | 116.92 | 506.57 | 506.57 | 0 | 0 | 0 | 904.032 | 0 | 0
489 | 1424.117 | 406.32 | 1843.2811 | 1479.3795 | -363.9016 | 0 | 0 | 0 | 0 | 0
490 | 1612.774 | 698.41 | 3055.1725 | 1675.3573 | -614.9724 | 0 | 764.8428 | 0 | 0 | 0
491 | 1401.019 | 848.07 | 3623.0996 | 1455.3852 | -59.1371 | 0 | 2108.5773 | 0 | 0 | 0
492 | 1755.972 | 956.11 | 4039.2448 | 1824.1121 | 0 | 0 | 2215.1327 | 0 | 0 | 0
493 | 1074.33 | 967.68 | 4091.3107 | 1116.0191 | 0 | 0 | 2975.2916 | 0 | 0 | 0
494 | 1159.81 | 896.44 | 3835.6307 | 1204.8161 | 0 | 0 | 2630.8146 | 0 | 0 | 0
495 | 1567.968 | 537.28 | 2358.0245 | 1628.8126 | 0 | 0 | 729.2118 | 0 | 0 | 0
496 | 1342.539 | 456.45 | 2051.442 | 1394.6359 | 0 | 0 | 656.8061 | 0 | 0 | 0
497 | 1562.161 | 291.72 | 1276.9268 | 1276.9268 | 0 | 0 | 0 | 332.934 | 0 | 0
498 | 1560.409 | 64.28 | 190.6788 | 190.6788 | 0 | 0 | 0 | 1376.853 | 0 | 0
499 | 918.411 | 0 | 0 | 0 | 0 | 0 | 0 | 918.411 | 0 | 0
500 | 1270.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1270.4 | 0 | 0
501 | 1204 | 0 | 0 | 0 | 0 | 0 | 0 | 1204 | 0 | 0
502 | 1369.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1063.726 | 0 | 317.7434
503 | 1345.6 | 0 | 0 | 0 | 0 | 0 | 0 | 753.6 | 0 | 614.9724
504 | 1280 | 0 | 0 | 0 | 0 | 0 | 0 | 1280 | 0 | 0
505 | 2330.4 | 0 | 0 | 0 | 0 | 0 | 0 | 2330.4 | 0 | 0
506 | 2057.6 | 0 | 0 | 0 | 0 | 0 | 0 | 2057.6 | 0 | 0
507 | 2428 | 0 | 0 | 0 | 0 | 0 | 0 | 2428 | 0 | 0
508 | 2208.8 | 0 | 0 | 0 | 0 | 0 | 0 | 2208.8 | 0 | 0
509 | 2004 | 0 | 0 | 0 | 0 | 0 | 0 | 2004 | 0 | 0
510 | 2379.2 | 0 | 0 | 0 | 0 | 0 | 0 | 2379.2 | 0 | 0
511 | 2040.8 | 42.25 | 74.2143 | 74.2143 | 0 | 0 | 0 | 1969.358 | 0 | 0
512 | 1723.786 | 242.61 | 1061.433 | 1061.433 | 0 | 0 | 0 | 702.003 | 0 | 0
513 | 1825.298 | 475.76 | 2184.8921 | 1896.1282 | -288.7638 | 0 | 0 | 0 | 0 | 0
514 | 2095.805 | 733.6 | 3242.1262 | 2177.1322 | -614.9724 | 0 | 450.0216 | 0 | 0 | 0
515 | 2297.304 | 878.74 | 3757.8564 | 2386.4513 | -134.2749 | 0 | 1237.1302 | 0 | 0 | 0
516 | 2286.452 | 952.14 | 3998.0416 | 2375.1772 | 0 | 0 | 1622.8644 | 0 | 0 | 0
517 | 2261.298 | 941.52 | 3949.1264 | 2349.0471 | 0 | 0 | 1600.0793 | 0 | 0 | 0
518 | 2390.381 | 744.71 | 3180.4898 | 2483.1391 | 0 | 0 | 697.3507 | 0 | 0 | 0
519 | 2181.431 | 512.33 | 2239.1945 | 2239.1945 | 0 | 0 | 0 | 0 | 0 | 26.8863
520 | 1853.049 | 519.28 | 2319.009 | 1924.9561 | -29.9217 | 0 | 364.1312 | 0 | 0 | 0
521 | 2387.844 | 237.65 | 1038.0256 | 1038.0256 | 0 | 0 | 0 | 1388.594 | 0 | 0
522 | 2256.255 | 55.79 | 170.9322 | 170.9322 | 0 | 0 | 0 | 2091.708 | 0 | 0
523 | 2414.4 | 0 | 0 | 0 | 0 | 0 | 0 | 2414.4 | 0 | 0
524 | 1896.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1896.8 | 0 | 0
525 | 2389.6 | 0 | 0 | 0 | 0 | 0 | 0 | 2389.6 | 0 | 0
526 | 2215.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1909.326 | 0 | 317.7434
527 | 2295.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1703.2 | 0 | 614.9724
528 | 1956 | 0 | 0 | 0 | 0 | 0 | 0 | 1956 | 0 | 0
529 | 1812 | 0 | 0 | 0 | 0 | 0 | 0 | 1812 | 0 | 0
530 | 1850.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1850.4 | 0 | 0
531 | 1248.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1248.8 | 0 | 0
532 | 1303.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1303.2 | 0 | 0
533 | 1569.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1569.6 | 0 | 0
534 | 1165.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1165.6 | 0 | 0
535 | 1127.2 | 30.2 | 51.4759 | 51.4759 | 0 | 0 | 0 | 1077.647 | 0 | 0
536 | 845.369 | 223.22 | 984.5158 | 878.1733 | -106.3424 | 0 | 0 | 0 | 0 | 0
537 | 1178.36 | 421.39 | 1934.3448 | 1224.086 | -614.9724 | 0 | 95.2864 | 0 | 0 | 0
538 | 1572.128 | 655.92 | 2897.7947 | 1633.133 | -316.6973 | 0 | 947.9644 | 0 | 0 | 0
539 | 1408.437 | 900.3 | 3830.847 | 1463.091 | 0 | 0 | 2367.756 | 0 | 0 | 0
540 | 1438.896 | 988.28 | 4111.2173 | 1494.732 | 0 | 0 | 2616.4853 | 0 | 0 | 0
541 | 1516.32 | 994.09 | 4108.8582 | 1575.1604 | 0 | 0 | 2533.6978 | 0 | 0 | 0
542 | 1377.594 | 550.04 | 2355.3454 | 1431.0512 | 0 | 0 | 924.2942 | 0 | 0 | 0
543 | 1550.943 | 629.08 | 2707.7422 | 1611.127 | 0 | 0 | 1096.6153 | 0 | 0 | 0
544 | 1543.534 | 528.13 | 2340.7315 | 1603.4304 | 0 | 0 | 737.301 | 0 | 0 | 0
545 | 1201.14 | 290.26 | 1275.1474 | 1247.7499 | 0 | 0 | 27.3974 | 0 | 0 | 0
546 | 1293.095 | 65.15 | 207.7474 | 207.7474 | 0 | 0 | 0 | 1093.108 | 0 | 0
547 | 1413.61 | 0 | 0 | 0 | 0 | 0 | 0 | 1413.61 | 0 | 0
548 | 1265.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1265.6 | 0 | 0
549 | 1180.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1180.8 | 0 | 0
550 | 1695.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1389.326 | 0 | 317.7434
551 | 1346.4 | 0 | 0 | 0 | 0 | 0 | 0 | 754.4 | 0 | 614.9724
552 | 1211.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1211.2 | 0 | 0
553 | 1408 | 0 | 0 | 0 | 0 | 0 | 0 | 1408 | 0 | 0
554 | 1139.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1139.2 | 0 | 0
555 | 1446.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1446.4 | 0 | 0
556 | 1142.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1142.4 | 0 | 0
557 | 880 | 0 | 0 | 0 | 0 | 0 | 0 | 880 | 0 | 0
558 | 1145.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1145.6 | 0 | 0
559 | 943.2 | 18.04 | 24.3122 | 24.3122 | 0 | 0 | 0 | 919.796 | 0 | 0
560 | 1274.438 | 236.93 | 1050.6637 | 1050.6637 | 0 | 0 | 0 | 263.022 | 0 | 0
561 | 1429.443 | 544.5 | 2530.3881 | 1484.9122 | -614.9724 | 0 | 430.5035 | 0 | 0 | 0
562 | 1547.522 | 765.42 | 3402.4782 | 1607.5732 | -423.0387 | 0 | 1371.8663 | 0 | 0 | 0
563 | 1405.725 | 917.17 | 3907.1607 | 1460.2738 | 0 | 0 | 2446.8869 | 0 | 0 | 0
564 | 1431.852 | 1012.26 | 4184.1487 | 1487.4147 | 0 | 0 | 2696.734 | 0 | 0 | 0
565 | 1367.56 | 1019.86 | 4183.2854 | 1420.6278 | 0 | 0 | 2762.6576 | 0 | 0 | 0
566 | 1673.787 | 943.36 | 3920.071 | 1738.7379 | 0 | 0 | 2181.3331 | 0 | 0 | 0
567 | 1642.84 | 797.16 | 3397.7942 | 1706.59 | 0 | 0 | 1691.2043 | 0 | 0 | 0
568 | 1902.457 | 583.86 | 2580.3785 | 1976.2814 | 0 | 0 | 604.0972 | 0 | 0 | 0
569 | 1899.267 | 327.08 | 1434.606 | 1434.606 | 0 | 0 | 0 | 518.251 | 0 | 0
570 | 1621.58 | 74.14 | 229.0606 | 229.0606 | 0 | 0 | 0 | 1401.076 | 0 | 0
571 | 1806.403 | 0 | 0 | 0 | 0 | 0 | 0 | 1806.403 | 0 | 0
572 | 1360.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1360.8 | 0 | 0
573 | 1477.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1477.6 | 0 | 0
574 | 1830.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1524.526 | 0 | 317.7434
575 | 1500.8 | 0 | 0 | 0 | 0 | 0 | 0 | 908.8 | 0 | 614.9724
576 | 1522.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1522.4 | 0 | 0
577 | 1083.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1083.2 | 0 | 0
578 | 1204 | 0 | 0 | 0 | 0 | 0 | 0 | 1204 | 0 | 0
579 | 1488.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1488.8 | 0 | 0
580 | 1076 | 0 | 0 | 0 | 0 | 0 | 0 | 1076 | 0 | 0
581 | 1073.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1073.6 | 0 | 0
582 | 912 | 0 | 0 | 0 | 0 | 0 | 0 | 912 | 0 | 0
583 | 964.8 | 33.07 | 57.7503 | 57.7503 | 0 | 0 | 0 | 909.207 | 0 | 0
584 | 1236.892 | 270.68 | 1186.8687 | 1186.8687 | 0 | 0 | 0 | 94.359 | 0 | 0
585 | 902.102 | 530.08 | 2403.361 | 937.1078 | -614.9724 | 0 | 851.2808 | 0 | 0 | 0
586 | 1643.977 | 748.13 | 3243.0071 | 1707.7711 | -423.0387 | 0 | 1112.1973 | 0 | 0 | 0
587 | 1404.929 | 901.78 | 3771.819 | 1459.4469 | 0 | 0 | 2312.3721 | 0 | 0 | 0
588 | 1257.977 | 993.06 | 4051.0134 | 1306.7925 | 0 | 0 | 2744.2209 | 0 | 0 | 0
589 | 1143.986 | 996.99 | 4021.3191 | 1188.3781 | 0 | 0 | 2832.9411 | 0 | 0 | 0
590 | 1063.922 | 911.29 | 3718.9896 | 1105.2072 | 0 | 0 | 2613.7823 | 0 | 0 | 0
591 | 1565.032 | 765.44 | 3210.6692 | 1625.7627 | 0 | 0 | 1584.9065 | 0 | 0 | 0
592 | 1529.519 | 554 | 2420.5179 | 1588.8716 | 0 | 0 | 831.6463 | 0 | 0 | 0
593 | 1548.768 | 276.08 | 1208.0406 | 1208.0406 | 0 | 0 | 0 | 385.854 | 0 | 0
594 | 954.794 | 57.88 | 180.9452 | 180.9452 | 0 | 0 | 0 | 780.608 | 0 | 0
595 | 979.933 | 0 | 0 | 0 | 0 | 0 | 0 | 979.933 | 0 | 0
596 | 1248.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1248.8 | 0 | 0
597 | 1226.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1226.4 | 0 | 0
598 | 1332 | 0 | 0 | 0 | 0 | 0 | 0 | 1026.126 | 0 | 317.7434
599 | 1236.8 | 0 | 0 | 0 | 0 | 0 | 0 | 644.8 | 0 | 614.9724
600 | 1285.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1285.6 | 0 | 0
601 | 1532.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1532.8 | 0 | 0
602 | 1344.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1344.8 | 0 | 0
603 | 1204.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1204.8 | 0 | 0
604 | 1120.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1120.8 | 0 | 0
605 | 1085.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1085.6 | 0 | 0
606 | 1070.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1070.4 | 0 | 0
607 | 1341.6 | 24.56 | 38.3111 | 38.3111 | 0 | 0 | 0 | 1304.72 | 0 | 0
608 | 915.255 | 209.46 | 927.1021 | 927.1021 | 0 | 0 | 0 | 22.785 | 0 | 0
609 | 1043.557 | 285.87 | 1293.4927 | 1084.052 | -209.4407 | 0 | 0 | 0 | 0 | 0
610 | 1135.797 | 541.42 | 2368.693 | 1179.8713 | -614.9724 | 0 | 573.8492 | 0 | 0 | 0
611 | 1052.302 | 820.06 | 3414.7257 | 1093.1363 | -213.598 | 0 | 2107.9914 | 0 | 0 | 0
612 | 1010.911 | 838.81 | 3421.8166 | 1050.1391 | 0 | 0 | 2371.6775 | 0 | 0 | 0
613 | 907.915 | 864.12 | 3486.9299 | 943.1464 | 0 | 0 | 2543.7835 | 0 | 0 | 0
614 | 1041.693 | 730.19 | 3013.0999 | 1082.1156 | 0 | 0 | 1930.9843 | 0 | 0 | 0
615 | 1029.977 | 555.48 | 2376.2565 | 1069.945 | 0 | 0 | 1306.3115 | 0 | 0 | 0
616 | 1033.486 | 307.94 | 1356.5294 | 1073.5902 | 0 | 0 | 282.9392 | 0 | 0 | 0
617 | 1376.376 | 275.51 | 1210.3478 | 1210.3478 | 0 | 0 | 0 | 211.241 | 0 | 0
618 | 1168.446 | 70.96 | 223.8032 | 223.8032 | 0 | 0 | 0 | 953.003 | 0 | 0
619 | 1198.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1198.4 | 0 | 0
620 | 1109.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1109.6 | 0 | 0
621 | 1098.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1098.4 | 0 | 0
622 | 1179.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1179.2 | 0 | 0
623 | 1169.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1042.295 | 0 | 132.245
624 | 497.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 516.9092
625 | 369.6 | 0 | 0 | 0 | 0 | 0 | 0 | 369.6 | 0 | 0
626 | 342.4 | 0 | 0 | 0 | 0 | 0 | 0 | 342.4 | 0 | 0
627 | 378.4 | 0 | 0 | 0 | 0 | 0 | 0 | 378.4 | 0 | 0
628 | 387.2 | 0 | 0 | 0 | 0 | 0 | 0 | 387.2 | 0 | 0
629 | 368.8 | 0 | 0 | 0 | 0 | 0 | 0 | 368.8 | 0 | 0
630 | 325.6 | 0 | 0 | 0 | 0 | 0 | 0 | 325.6 | 0 | 0
631 | 335.2 | 37.26 | 64.6459 | 64.6459 | 0 | 0 | 0 | 0 | 0 | 283.5615
632 | 281.28 | 276.08 | 1206.6808 | 292.195 | -614.9724 | 0 | 299.5134 | 0 | 0 | 0
633 | 812.402 | 514.96 | 2372.6082 | 843.9271 | -423.0387 | 0 | 1105.6425 | 0 | 0 | 0
634 | 1193.029 | 741.39 | 3273.2457 | 1239.3242 | 0 | 0 | 2033.9215 | 0 | 0 | 0
635 | 997.388 | 780.25 | 3342.7231 | 1036.0914 | 0 | 0 | 2306.6317 | 0 | 0 | 0
636 | 1238.61 | 970.09 | 4030.2487 | 1286.6739 | 0 | 0 | 2743.5748 | 0 | 0 | 0
637 | 1158.511 | 963.97 | 3991.2998 | 1203.4667 | 0 | 0 | 2787.833 | 0 | 0 | 0
638 | 1234.863 | 906.88 | 3802.7847 | 1282.7815 | 0 | 0 | 2520.0032 | 0 | 0 | 0
639 | 1047.104 | 541.27 | 2365.6358 | 1087.7366 | 0 | 0 | 1277.8992 | 0 | 0 | 0
640 | 1281.661 | 459.77 | 2059.822 | 1331.3955 | 0 | 0 | 728.4265 | 0 | 0 | 0
641 | 1055.169 | 280.95 | 1237.203 | 1096.1146 | 0 | 0 | 141.0884 | 0 | 0 | 0
642 | 1044.091 | 62.59 | 201.4128 | 201.4128 | 0 | 0 | 0 | 850.202 | 0 | 0
643 | 1088.323 | 0 | 0 | 0 | 0 | 0 | 0 | 1088.323 | 0 | 0
644 | 898.4 | 0 | 0 | 0 | 0 | 0 | 0 | 456.526 | 0 | 459.0208
645 | 270.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280.8928
646 | 91.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.739
647 | 94.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.0632
648 | 91.2 | 0 | 0 | 0 | 0 | 0 | 0 | 91.2 | 0 | 0
649 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0
650 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0
651 | 94.4 | 0 | 0 | 0 | 0 | 0 | 0 | 94.4 | 0 | 0
652 | 85.6 | 0 | 0 | 0 | 0 | 0 | 0 | 85.6 | 0 | 0
653 | 95.2 | 0 | 0 | 0 | 0 | 0 | 0 | 95.2 | 0 | 0
654 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0
655 | 93.6 | 33.47 | 57.3005 | 57.3005 | 0 | 0 | 0 | 38.44 | 0 | 0
656 | 77.076 | 267.48 | 1169.3638 | 80.0669 | -614.9724 | 0 | 474.3245 | 0 | 0 | 0
657 | 83.396 | 374.02 | 1696.2767 | 86.6322 | -423.0387 | 0 | 1186.6059 | 0 | 0 | 0
658 | 78.901 | 737.64 | 3180.8513 | 81.9627 | 0 | 0 | 3098.8886 | 0 | 0 | 0
659 | 86.02 | 892.64 | 3684.1023 | 89.358 | 0 | 0 | 3594.7444 | 0 | 0 | 0
660 | 80.475 | 981.44 | 3955.0112 | 83.5978 | 0 | 0 | 3871.4134 | 0 | 0 | 0
661 | 88.61 | 987.83 | 3961.3032 | 92.0485 | 0 | 0 | 3869.2547 | 0 | 0 | 0
662 | 80.761 | 912.69 | 3713.7197 | 83.8949 | 0 | 0 | 3629.8248 | 0 | 0 | 0
663 | 95.362 | 767.22 | 3248.2822 | 99.0625 | 0 | 0 | 3149.2197 | 0 | 0 | 0
664 | 84.557 | 417.68 | 1851.7328 | 87.8382 | 0 | 0 | 1763.8946 | 0 | 0 | 0
665 | 90.093 | 312.19 | 1375.738 | 93.589 | 0 | 0 | 1282.1489 | 0 | 0 | 0
666 | 80.774 | 72.29 | 232.4139 | 83.9084 | 0 | 0 | 148.5054 | 0 | 0 | 0
667 | 96.805 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.5615
668 | 86.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.7527
669 | 93.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.2321
670 | 87.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.5838
671 | 92.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.4011
672 | 87.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.5838
673 | 93.6 | 0 | 0 | 0 | 0 | 0 | 0 | 93.6 | 0 | 0
674 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 0 | 0
675 | 92.8 | 0 | 0 | 0 | 0 | 0 | 0 | 35.89 | 0 | 59.1184
676 | 87.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.5838
677 | 93.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.2321
678 | 83.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.4286
679 | 84.8 | 30.91 | 53.8527 | 53.8527 | 0 | 0 | 0 | 0 | 0 | 34.238
680 | 79.796 | 261.14 | 1137.9898 | 82.8925 | -614.9724 | 0 | 440.125 | 0 | 0 | 0
681 | 84.042 | 514.37 | 2339.5607 | 87.3032 | -423.0387 | 0 | 1829.2188 | 0 | 0 | 0
682 | 80.506 | 718.13 | 3123.1415 | 83.63 | 0 | 0 | 3039.5115 | 0 | 0 | 0
683 | 81.184 | 846.67 | 3549.6363 | 84.3343 | 0 | 0 | 3465.302 | 0 | 0 | 0
684 | 80.078 | 938.94 | 3847.6663 | 83.1854 | 0 | 0 | 3764.4809 | 0 | 0 | 0
685 | 81.515 | 906.31 | 3706.1738 | 84.6782 | 0 | 0 | 3621.4957 | 0 | 0 | 0
686 | 74.649 | 581.33 | 2457.4744 | 77.5457 | 0 | 0 | 2379.9287 | 0 | 0 | 0
687 | 88.307 | 487.37 | 2103.0426 | 91.7337 | 0 | 0 | 2011.3088 | 0 | 0 | 0
688 | 79.067 | 261.89 | 1155.075 | 82.1352 | 0 | 0 | 1072.9399 | 0 | 0 | 0
689 | 84.323 | 61.57 | 247.5243 | 87.5951 | 0 | 0 | 159.9292 | 0 | 0 | 0
690 | 79.24 | 53.16 | 174.2969 | 82.3149 | 0 | 0 | 91.982 | 0 | 0 | 0
691 | 95.215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.9098
692 | 89.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.0769
693 | 93.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.2321
694 | 87.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.5838
695 | 96.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.5563
696 | 87.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.5838
697 | 93.6 | 0 | 0 | 0 | 0 | 0 | 0 | 93.6 | 0 | 0
698 | 88.8 | 0 | 0 | 0 | 0 | 0 | 0 | 88.8 | 0 | 0
699 | 87.2 | 0 | 0 | 0 | 0 | 0 | 0 | 87.2 | 0 | 0
700 | 87.2 | 0 | 0 | 0 | 0 | 0 | 0 | 3.741 | 0 | 86.6976
701 | 93.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.2321
702 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.2596
703 | 87.2 | 4.89 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.5838
704 | 76.02 | 61.95 | 251.238 | 78.9699 | -172.2681 | 0 | 0 | 0 | 0 | 0
705 | 84.507 | 452.81 | 2092.4852 | 87.7863 | -614.9724 | 0 | 1389.7265 | 0 | 0 | 0
706 | 72.771 | 630.48 | 2832.297 | 75.5938 | -250.7706 | 0 | 2505.9326 | 0 | 0 | 0
707 | 81.102 | 885.69 | 3867.709 | 84.2491 | 0 | 0 | 3783.4599 | 0 | 0 | 0
708 | 75.163 | 935.02 | 4009.2659 | 78.0797 | 0 | 0 | 3931.1862 | 0 | 0 | 0
709 | 86.617 | 992.8 | 4204.1675 | 89.9782 | 0 | 0 | 4114.1893 | 0 | 0 | 0
710 | 78.42 | 833.11 | 3557.4897 | 81.4631 | 0 | 0 | 3476.0266 | 0 | 0 | 0
711 | 78.853 | 670.66 | 2922.3437 | 81.9129 | 0 | 0 | 2840.4308 | 0 | 0 | 0
712 | 79.653 | 542.49 | 2431.5178 | 82.7439 | 0 | 0 | 2348.7739 | 0 | 0 | 0
713 | 88.652 | 233.88 | 1032.7859 | 92.0921 | 0 | 0 | 940.6938 | 0 | 0 | 0
714 | 82.665 | 74.21 | 240.6526 | 85.8728 | 0 | 0 | 154.7798 | 0 | 0 | 0
715 | 97.636 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.4247
716 | 88.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.2459
717 | 94.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.0632
718 | 87.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.5838
719 | 91.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.739
720 | 84.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.0906
721 | 93.6 | 0 | 0 | 0 | 0 | 0 | 0 | 93.6 | 0 | 0
722 | 81.6 | 0 | 0 | 0 | 0 | 0 | 0 | 81.6 | 0 | 0
723 | 92.8 | 0 | 0 | 0 | 0 | 0 | 0 | 62.885 | 0 | 31.0758
724 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.1044
725 | 90.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.9079
726 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.1044
727 | 86.4 | 13.11 | 13.3777 | 13.3777 | 0 | 0 | 0 | 0 | 0 | 76.375
728 | 75.453 | 138.53 | 606.4095 | 78.3809 | -528.0286 | 0 | 0 | 0 | 0 | 0
729 | 85.467 | 379.57 | 1721.8438 | 88.7835 | -509.9825 | 0 | 1123.0778 | 0 | 0 | 0
730 | 74.454 | 608.48 | 2657.2553 | 77.3432 | 0 | 0 | 2579.9121 | 0 | 0 | 0
731 | 80.579 | 882.91 | 3691.7438 | 83.7058 | 0 | 0 | 3608.0379 | 0 | 0 | 0
732 | 73.28 | 818.78 | 3376.7346 | 76.1236 | 0 | 0 | 3300.6109 | 0 | 0 | 0
733 | 82.654 | 871.42 | 3550.6596 | 85.8614 | 0 | 0 | 3464.7982 | 0 | 0 | 0
734 | 74.961 | 498.71 | 2123.238 | 77.8698 | 0 | 0 | 2045.3681 | 0 | 0 | 0
735 | 86.787 | 372.83 | 1625.451 | 90.1547 | 0 | 0 | 1535.2963 | 0 | 0 | 0
736 | 81.253 | 356.51 | 1581.7766 | 84.406 | 0 | 0 | 1497.3706 | 0 | 0 | 0
737 | 87.089 | 156.94 | 680.7963 | 90.4685 | 0 | 0 | 590.3278 | 0 | 0 | 0
738 | 79.66 | 68.92 | 224.1876 | 82.7512 | 0 | 0 | 141.4364 | 0 | 0 | 0
739 | 96.821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.5781
740 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.4148
741 | 91.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.739
742 | 86.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.7527
743 | 92.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.4011
744 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.4148
745 | 94.4 | 0 | 0 | 0 | 0 | 0 | 0 | 94.4 | 0 | 0
746 | 87.2 | 0 | 0 | 0 | 0 | 0 | 0 | 87.2 | 0 | 0
747 | 93.6 | 0 | 0 | 0 | 0 | 0 | 0 | 29.421 | 0 | 66.6694
748 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.1044
749 | 88.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.2459
750 | 86.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.7527
751 | 88.8 | 31.54 | 55.6031 | 55.6031 | 0 | 0 | 0 | 0 | 0 | 36.6428
752 | 79.281 | 246.98 | 1073.7813 | 82.3575 | -614.9724 | 0 | 376.4514 | 0 | 0 | 0
753 | 84.741 | 499.19 | 2263.8848 | 88.0294 | -423.0387 | 0 | 1752.8168 | 0 | 0 | 0
754 | 75.611 | 714.96 | 3117.7959 | 78.5451 | 0 | 0 | 3039.2508 | 0 | 0 | 0
755 | 86.655 | 869.28 | 3673.5876 | 90.0176 | 0 | 0 | 3583.5699 | 0 | 0 | 0
756 | 74.903 | 937.72 | 3886.2132 | 77.8096 | 0 | 0 | 3808.4036 | 0 | 0 | 0
757 | 87.642 | 940.93 | 3865.9285 | 91.0429 | 0 | 0 | 3774.8856 | 0 | 0 | 0
758 | 82.638 | 759.19 | 3176.2671 | 85.8447 | 0 | 0 | 3090.4223 | 0 | 0 | 0
759 | 89.332 | 735.19 | 3150.9971 | 92.7985 | 0 | 0 | 3058.1986 | 0 | 0 | 0
760 | 81.435 | 548.96 | 2443.3633 | 84.5951 | 0 | 0 | 2358.7682 | 0 | 0 | 0
761 | 83.254 | 313.13 | 1381.5698 | 86.4847 | 0 | 0 | 1295.0852 | 0 | 0 | 0
762 | 82.933 | 72.52 | 237.3461 | 86.1512 | 0 | 0 | 151.1949 | 0 | 0 | 0
763 | 96.007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.7325
764 | 91.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.739
765 | 93.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.2321
766 | 88.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.2459
767 | 97.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.3873
768 | 90.4 | 0 | 0 | 0 | 0 | 0 | 0 | 90.4 | 0 | 0
769 | 92.8 | 0 | 0 | 0 | 0 | 0 | 0 | 92.8 | 0 | 0
770 | 86.4 | 0 | 0 | 0 | 0 | 0 | 0 | 28.292 | 0 | 60.3629
771 | 91.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.739
772 | 87.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.5838
773 | 92.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.4011
774 | 85.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.9217
775 | 76.8 | 34.75 | 63.4097 | 63.4097 | 0 | 0 | 0 | 0 | 0 | 16.3705
776 | 82.775 | 231 | 1002.512 | 85.9871 | -614.9724 | 0 | 301.5526 | 0 | 0 | 0
777 | 646.748 | 469.86 | 2133.7413 | 671.8449 | -423.0387 | 0 | 1038.8577 | 0 | 0 | 0
778 | 552.934 | 745.6 | 3243.6689 | 574.3905 | 0 | 0 | 2669.2784 | 0 | 0 | 0
779 | 876.383 | 715.32 | 3011.604 | 910.3908 | 0 | 0 | 2101.2132 | 0 | 0 | 0
780 | 949.841 | 819.63 | 3356.7864 | 986.6993 | 0 | 0 | 2370.0871 | 0 | 0 | 0
781 | 1244.374 | 814.07 | 3314.3356 | 1292.6616 | 0 | 0 | 2021.674 | 0 | 0 | 0
782 | 1169.848 | 765.59 | 3170.3656 | 1215.2437 | 0 | 0 | 1955.122 | 0 | 0 | 0
783 | 1381.741 | 732.82 | 3124.2188 | 1435.3591 | 0 | 0 | 1688.8597 | 0 | 0 | 0
784 | 889.368 | 464.44 | 2056.475 | 923.8797 | 0 | 0 | 1132.5953 | 0 | 0 | 0
785 | 1360.953 | 225.64 | 987.413 | 987.413 | 0 | 0 | 0 | 410.425 | 0 | 0
786 | 1095.157 | 62.35 | 209.3794 | 209.3794 | 0 | 0 | 0 | 893.599 | 0 | 0
787 | 1127.015 | 0 | 0 | 0 | 0 | 0 | 0 | 1127.015 | 0 | 0
788 | 1211.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1211.2 | 0 | 0
789 | 1118.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1118.4 | 0 | 0
790 | 1337.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1217.117 | 0 | 125.1583
791 | 1112 | 0 | 0 | 0 | 0 | 0 | 0 | 520 | 0 | 614.9724
792 | 163.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169.5329
793 | 108.8 | 0 | 0 | 0 | 0 | 0 | 0 | 108.8 | 0 | 0
794 | 94.4 | 0 | 0 | 0 | 0 | 0 | 0 | 94.4 | 0 | 0
795 | 105.6 | 0 | 0 | 0 | 0 | 0 | 0 | 105.6 | 0 | 0
796 | 101.6 | 0 | 0 | 0 | 0 | 0 | 0 | 101.6 | 0 | 0
797 | 105.6 | 0 | 0 | 0 | 0 | 0 | 0 | 105.6 | 0 | 0
798 | 95.2 | 0 | 0 | 0 | 0 | 0 | 0 | 95.2 | 0 | 0
799 | 87.2 | 35.69 | 67.5317 | 67.5317 | 0 | 0 | 0 | 0 | 0 | 23.0521
800 | 82.403 | 270.2 | 1168.0684 | 85.6006 | -614.9724 | 0 | 467.4954 | 0 | 0 | 0
801 | 835.519 | 515.91 | 2342.7187 | 867.9411 | -423.0387 | 0 | 1051.7389 | 0 | 0 | 0
802 | 1039.674 | 737.97 | 3207.239 | 1080.0183 | 0 | 0 | 2127.2207 | 0 | 0 | 0
803 | 891.524 | 890.23 | 3719.6045 | 926.1194 | 0 | 0 | 2793.4852 | 0 | 0 | 0
804 | 1352.422 | 946.64 | 3865.9046 | 1404.9024 | 0 | 0 | 2461.0022 | 0 | 0 | 0
805 | 1341.667 | 968.5 | 3943.3433 | 1393.7301 | 0 | 0 | 2549.6133 | 0 | 0 | 0
806 | 1194.461 | 857.72 | 3556.7802 | 1240.8118 | 0 | 0 | 2315.9684 | 0 | 0 | 0
807 | 1481.371 | 628.4 | 2684.767 | 1538.8552 | 0 | 0 | 1145.9118 | 0 | 0 | 0
808 | 1646.336 | 167.53 | 712.5899 | 712.5899 | 0 | 0 | 0 | 960.365 | 0 | 0
809 | 1713.488 | 165.47 | 713.1218 | 713.1218 | 0 | 0 | 0 | 1027.005 | 0 | 0
810 | 1434.101 | 39.27 | 121.9172 | 121.9172 | 0 | 0 | 0 | 1316.738 | 0 | 0
811 | 1539.509 | 0 | 0 | 0 | 0 | 0 | 0 | 1539.509 | 0 | 0
812 | 1661.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1661.6 | 0 | 0
813 | 1616 | 0 | 0 | 0 | 0 | 0 | 0 | 1616 | 0 | 0
814 | 1728.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1422.926 | 0 | 317.7434
815 | 1469.6 | 0 | 0 | 0 | 0 | 0 | 0 | 877.6 | 0 | 614.9724
816 | 1761.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1761.6 | 0 | 0
817 | 1354.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1354.4 | 0 | 0
818 | 1331.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1331.2 | 0 | 0
819 | 1416.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1416.8 | 0 | 0
820 | 1299.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1299.2 | 0 | 0
821 | 1488 | 0 | 0 | 0 | 0 | 0 | 0 | 1488 | 0 | 0
822 | 1488.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1488.8 | 0 | 0
823 | 1292.8 | 34.28 | 66.0711 | 66.0711 | 0 | 0 | 0 | 1229.197 | 0 | 0
824 | 1289.506 | 263.66 | 1130.4377 | 1130.4377 | 0 | 0 | 0 | 201.296 | 0 | 0
825 | 1526.73 | 485.55 | 2158.0005 | 1585.9744 | -572.0261 | 0 | 0 | 0 | 0 | 0
826 | 1083.978 | 589.42 | 2509.3284 | 1126.0415 | -465.985 | 0 | 917.302 | 0 | 0 | 0
827 | 1402.913 | 650.37 | 2705.7965 | 1457.3527 | 0 | 0 | 1248.4439 | 0 | 0 | 0
828 | 1305.329 | 872.38 | 3529.7588 | 1355.982 | 0 | 0 | 2173.7768 | 0 | 0 | 0
829 | 1517.919 | 801.76 | 3266.2608 | 1576.8215 | 0 | 0 | 1689.4393 | 0 | 0 | 0
830 | 1335.878 | 748.45 | 3094.6128 | 1387.7164 | 0 | 0 | 1706.8964 | 0 | 0 | 0
831 | 1360.865 | 568.31 | 2423.0838 | 1413.673 | 0 | 0 | 1009.4107 | 0 | 0 | 0
832 | 1604.627 | 472.85 | 2083.6616 | 1666.8941 | 0 | 0 | 416.7674 | 0 | 0 | 0
833 | 1501.802 | 272.93 | 1195.817 | 1195.817 | 0 | 0 | 0 | 350.655 | 0 | 0
834 | 1303.802 | 60.41 | 199.4204 | 199.4204 | 0 | 0 | 0 | 1111.831 | 0 | 0
835 | 1407.738 | 0 | 0 | 0 | 0 | 0 | 0 | 1407.738 | 0 | 0
836 | 1397.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1397.6 | 0 | 0
837 | 1207.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1207.2 | 0 | 0
838 | 1357.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1051.726 | 0 | 317.7434
839 | 1300.8 | 0 | 0 | 0 | 0 | 0 | 0 | 708.8 | 0 | 614.9724
840 | 1248.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1248.8 | 0 | 0
841 | 1178.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1178.4 | 0 | 0
842 | 1225.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1225.6 | 0 | 0
843 | 1224.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1224.8 | 0 | 0
844 | 903.2 | 0 | 0 | 0 | 0 | 0 | 0 | 903.2 | 0 | 0
845 | 1121.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1121.6 | 0 | 0
846 | 1310.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1310.4 | 0 | 0
847 | 1152 | 5.87 | 0 | 0 | 0 | 0 | 0 | 1152 | 0 | 0
848 | 933.17 | 57.87 | 230.7165 | 230.7165 | 0 | 0 | 0 | 711.072 | 0 | 0
849 | 1215.698 | 261.6 | 1146.5704 | 1146.5704 | 0 | 0 | 0 | 111.958 | 0 | 0
850 | 1139.46 | 373.8 | 1600.8314 | 1183.6765 | -417.1549 | 0 | 0 | 0 | 0 | 0
851 | 1551.141 | 486.79 | 2040.4005 | 1611.3326 | -429.0679 | 0 | 0 | 0 | 0 | 0
852 | 1338.153 | 591.12 | 2436.6807 | 1390.0797 | -191.7883 | 0 | 854.8127 | 0 | 0 | 0
853 | 1140.835 | 976.35 | 3873.8774 | 1185.1048 | 0 | 0 | 2688.7726 | 0 | 0 | 0
854 | 1315.264 | 714.68 | 2944.9709 | 1366.3025 | 0 | 0 | 1578.6685 | 0 | 0 | 0
855 | 1361.037 | 555.05 | 2355.5874 | 1413.8517 | 0 | 0 | 941.7357 | 0 | 0 | 0
856 | 1270.539 | 377 | 1653.3533 | 1319.8419 | 0 | 0 | 333.5114 | 0 | 0 | 0
857 | 1377.713 | 246.62 | 1074.7453 | 1074.7453 | 0 | 0 | 0 | 343.115 | 0 | 0
858 | 1430.203 | 70.44 | 231.7573 | 231.7573 | 0 | 0 | 0 | 1207.103 | 0 | 0
859 | 1135.9 | 0 | 0 | 0 | 0 | 0 | 0 | 1135.9 | 0 | 0
860 | 1324 | 0 | 0 | 0 | 0 | 0 | 0 | 1324 | 0 | 0
861 | 1216.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1216.8 | 0 | 0
862 | 1368.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1062.926 | 0 | 317.7434
863 | 1304 | 0 | 0 | 0 | 0 | 0 | 0 | 712 | 0 | 614.9724
864 | 504 | 0 | 0 | 0 | 0 | 0 | 0 | 504 | 0 | 0
865 | 308.8 | 0 | 0 | 0 | 0 | 0 | 0 | 308.8 | 0 | 0
866 | 223.2 | 0 | 0 | 0 | 0 | 0 | 0 | 223.2 | 0 | 0
867 | 305.6 | 0 | 0 | 0 | 0 | 0 | 0 | 305.6 | 0 | 0
868 | 234.4 | 0 | 0 | 0 | 0 | 0 | 0 | 234.4 | 0 | 0
869 | 284.8 | 0 | 0 | 0 | 0 | 0 | 0 | 284.8 | 0 | 0
870 | 280.8 | 0 | 0 | 0 | 0 | 0 | 0 | 280.8 | 0 | 0
871 | 279.2 | 30.51 | 60.7015 | 60.7015 | 0 | 0 | 0 | 220.766 | 0 | 0
872 | 207.884 | 261.96 | 1140.8164 | 215.9509 | -614.9724 | 0 | 309.8931 | 0 | 0 | 0
873 | 1383.408 | 517.78 | 2343.1031 | 1437.0908 | -423.0387 | 0 | 482.9736 | 0 | 0 | 0
874 | 1305.53 | 736.83 | 3160.3765 | 1356.1908 | 0 | 0 | 1804.1857 | 0 | 0 | 0
875 | 1615.041 | 829.29 | 3429.4695 | 1677.7123 | 0 | 0 | 1751.7572 | 0 | 0 | 0
876 | 1779.002 | 861.64 | 3526.7484 | 1848.0357 | 0 | 0 | 1678.7126 | 0 | 0 | 0
877 | 1624.258 | 831.04 | 3425.2405 | 1687.2869 | 0 | 0 | 1737.9536 | 0 | 0 | 0
878 | 1539.01 | 770.61 | 3222.1957 | 1598.7309 | 0 | 0 | 1623.4648 | 0 | 0 | 0
879 | 1787.689 | 537.56 | 2312.4625 | 1857.0598 | 0 | 0 | 455.4027 | 0 | 0 | 0
880 | 1354.304 | 407.35 | 1795.3777 | 1406.8574 | 0 | 0 | 388.5202 | 0 | 0 | 0
881 | 1620.241 | 171.76 | 741.7637 | 741.7637 | 0 | 0 | 0 | 906.186 | 0 | 0
882 | 1300.99 | 56.77 | 183.0384 | 183.0384 | 0 | 0 | 0 | 1124.789 | 0 | 0
883 | 1394.069 | 0 | 0 | 0 | 0 | 0 | 0 | 1394.069 | 0 | 0
884 | 1272 | 0 | 0 | 0 | 0 | 0 | 0 | 1272 | 0 | 0
885 | 1471.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1471.2 | 0 | 0
886 | 1444 | 0 | 0 | 0 | 0 | 0 | 0 | 1138.126 | 0 | 317.7434
887 | 1357.6 | 0 | 0 | 0 | 0 | 0 | 0 | 765.6 | 0 | 614.9724
888 | 576.8 | 0 | 0 | 0 | 0 | 0 | 0 | 576.8 | 0 | 0
889 | 498.4 | 0 | 0 | 0 | 0 | 0 | 0 | 498.4 | 0 | 0
890 | 498.4 | 0 | 0 | 0 | 0 | 0 | 0 | 498.4 | 0 | 0
891 | 504 | 0 | 0 | 0 | 0 | 0 | 0 | 504 | 0 | 0
892 | 421.6 | 0 | 0 | 0 | 0 | 0 | 0 | 421.6 | 0 | 0
893 | 485.6 | 0 | 0 | 0 | 0 | 0 | 0 | 485.6 | 0 | 0
894 | 467.2 | 0 | 0 | 0 | 0 | 0 | 0 | 467.2 | 0 | 0
895 | 472 | 29.23 | 60.9498 | 60.9498 | 0 | 0 | 0 | 413.327 | 0 | 0
896 | 385.522 | 254.82 | 1136.2748 | 400.4821 | -614.9724 | 0 | 120.8203 | 0 | 0 | 0
897 | 1044.814 | 512.13 | 2375.0681 | 1085.3577 | -423.0387 | 0 | 866.6717 | 0 | 0 | 0
898 | 1692.649 | 738.73 | 3279.4432 | 1758.3318 | 0 | 0 | 1521.1114 | 0 | 0 | 0
899 | 1873.143 | 903.12 | 3870.5948 | 1945.8298 | 0 | 0 | 1924.765 | 0 | 0 | 0
900 | 1814.753 | 999.36 | 4197.7809 | 1885.174 | 0 | 0 | 2312.6069 | 0 | 0 | 0
901 | 1605.764 | 969.82 | 4069.6662 | 1668.0753 | 0 | 0 | 2401.5909 | 0 | 0 | 0
902 | 1656.929 | 939.51 | 3973.5809 | 1721.2257 | 0 | 0 | 2252.3552 | 0 | 0 | 0
903 | 1959.966 | 789.59 | 3414.7735 | 2036.022 | 0 | 0 | 1378.7515 | 0 | 0 | 0
904 | 1925.128 | 572.86 | 2556.2087 | 1999.8321 | 0 | 0 | 556.3766 | 0 | 0 | 0
905 | 1644.797 | 316.01 | 1399.8611 | 1399.8611 | 0 | 0 | 0 | 297.228 | 0 | 0
906 | 1796.832 | 69.43 | 234.1653 | 234.1653 | 0 | 0 | 0 | 1571.414 | 0 | 0
907 | 1564.005 | 0 | 0 | 0 | 0 | 0 | 0 | 1564.005 | 0 | 0
908 | 1423.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1423.2 | 0 | 0
909 | 1762.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1762.4 | 0 | 0
910 | 1525.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1219.726 | 0 | 317.7434
911 | 1706.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1114.4 | 0 | 614.9724
912 | 526.4 | 0 | 0 | 0 | 0 | 0 | 0 | 526.4 | 0 | 0
913 | 477.6 | 0 | 0 | 0 | 0 | 0 | 0 | 477.6 | 0 | 0
914 | 487.2 | 0 | 0 | 0 | 0 | 0 | 0 | 487.2 | 0 | 0
915 | 450.4 | 0 | 0 | 0 | 0 | 0 | 0 | 450.4 | 0 | 0
916 | 410.4 | 0 | 0 | 0 | 0 | 0 | 0 | 410.4 | 0 | 0
917 | 498.4 | 0 | 0 | 0 | 0 | 0 | 0 | 498.4 | 0 | 0
918 | 480.8 | 0 | 0 | 0 | 0 | 0 | 0 | 480.8 | 0 | 0
919 | 402.4 | 12.68 | 16.0506 | 16.0506 | 0 | 0 | 0 | 386.949 | 0 | 0
920 | 183.582 | 260.62 | 1166.4655 | 190.7059 | -614.9724 | 0 | 360.7873 | 0 | 0 | 0
921 | 1361.436 | 523.11 | 2400.5282 | 1414.2662 | -423.0387 | 0 | 563.2233 | 0 | 0 | 0
922 | 1498.899 | 749.82 | 3227.8375 | 1557.0634 | 0 | 0 | 1670.7741 | 0 | 0 | 0
923 | 1608.087 | 919.71 | 3743.657 | 1670.4884 | 0 | 0 | 2073.1686 | 0 | 0 | 0
924 | 1399.808 | 1018.64 | 4028.4339 | 1454.1272 | 0 | 0 | 2574.3067 | 0 | 0 | 0
925 | 1724.006 | 1031.69 | 4068.2347 | 1790.9056 | 0 | 0 | 2277.3291 | 0 | 0 | 0
926 | 1255.265 | 959.58 | 3865.9638 | 1303.9752 | 0 | 0 | 2561.9886 | 0 | 0 | 0
927 | 1125.5 | 808.74 | 3392.247 | 1169.1747 | 0 | 0 | 2223.0723 | 0 | 0 | 0
928 | 1614.058 | 596.08 | 2619.6007 | 1676.6911 | 0 | 0 | 942.9096 | 0 | 0 | 0
929 | 1453.859 | 339.87 | 1498.347 | 1498.347 | 0 | 0 | 0 | 11.483 | 0 | 0
930 | 1370.109 | 67.82 | 228.9962 | 228.9962 | 0 | 0 | 0 | 1149.667 | 0 | 0
931 | 1452.169 | 0 | 0 | 0 | 0 | 0 | 0 | 1452.169 | 0 | 0
932 | 1032 | 0 | 0 | 0 | 0 | 0 | 0 | 1032 | 0 | 0
933 | 1212.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1212.8 | 0 | 0
934 | 1396.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1090.926 | 0 | 317.7434
935 | 964 | 0 | 0 | 0 | 0 | 0 | 0 | 372 | 0 | 614.9724
936 | 1384.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1384.8 | 0 | 0
937 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 1120 | 0 | 0
938 | 1568.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1568.8 | 0 | 0
939 | 1411.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1411.2 | 0 | 0
940 | 1482.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1482.4 | 0 | 0
941 | 1182.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1182.4 | 0 | 0
942 | 1132 | 0 | 0 | 0 | 0 | 0 | 0 | 1132 | 0 | 0
943 | 1137.6 | 19.83 | 35.0939 | 35.0939 | 0 | 0 | 0 | 1103.817 | 0 | 0
944 | 182.01 | 204.43 | 897.4255 | 189.0729 | -614.9724 | 0 | 93.3802 | 0 | 0 | 0
945 | 481.147 | 396.23 | 1772.4731 | 499.8178 | -423.0387 | 0 | 849.6166 | 0 | 0 | 0
946 | 455.687 | 596.65 | 2558.3486 | 473.3698 | 0 | 0 | 2084.9788 | 0 | 0 | 0
947 | 498.735 | 762.24 | 3175.2563 | 518.0883 | 0 | 0 | 2657.168 | 0 | 0 | 0
948 | 415.99 | 892.34 | 3638.8073 | 432.1324 | 0 | 0 | 3206.675 | 0 | 0 | 0
949 | 320.018 | 906.97 | 3708.1133 | 332.4362 | 0 | 0 | 3375.6771 | 0 | 0 | 0
950 | 335.666 | 768.52 | 3213.0231 | 348.6914 | 0 | 0 | 2864.3317 | 0 | 0 | 0
951 | 408.03 | 521.02 | 2239.7087 | 423.8635 | 0 | 0 | 1815.8452 | 0 | 0 | 0
952 | 329.489 | 460.16 | 2033.1923 | 342.2747 | 0 | 0 | 1690.9175 | 0 | 0 | 0
953 | 413.609 | 270.86 | 1192.5167 | 429.659 | 0 | 0 | 762.8577 | 0 | 0 | 0
954 | 285.122 | 82.77 | 276.3844 | 276.3844 | 0 | 0 | 0 | 19.062 | 0 | 0
955 | 304.539 | 0 | 0 | 0 | 0 | 0 | 0 | 304.539 | 0 | 0
956 | 261.6 | 0 | 0 | 0 | 0 | 0 | 0 | 261.6 | 0 | 0
957 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 204 | 0 | 0
958 | 331.2 | 0 | 0 | 0 | 0 | 0 | 0 | 230.648 | 0 | 104.4539
959 | 296.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308.3172
960 | 302.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 314.1346
961 | 324.8 | 0 | 0 | 0 | 0 | 0 | 0 | 324.8 | 0 | 0
962 | 296.8 | 0 | 0 | 0 | 0 | 0 | 0 | 296.8 | 0 | 0
963 | 296.8 | 0 | 0 | 0 | 0 | 0 | 0 | 296.8 | 0 | 0
964 | 316 | 0 | 0 | 0 | 0 | 0 | 0 | 316 | 0 | 0
965 | 227.2 | 0 | 0 | 0 | 0 | 0 | 0 | 227.2 | 0 | 0
966 | 276 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 0 | 0
967 | 256.8 | 29.15 | 60.956 | 60.956 | 0 | 0 | 0 | 0 | 0 | 205.809
968 | 246.146 | 259.03 | 1134.3644 | 255.6976 | -614.9724 | 0 | 263.6944 | 0 | 0 | 0
969 | 460.316 | 518.3 | 2348.562 | 478.1784 | -423.0387 | 0 | 1447.3448 | 0 | 0 | 0
970 | 1172.832 | 730.62 | 3178.568 | 1218.3435 | 0 | 0 | 1960.2246 | 0 | 0 | 0
971 | 1566.318 | 874.27 | 3658.4657 | 1627.0986 | 0 | 0 | 2031.3671 | 0 | 0 | 0
972 | 1214.229 | 972.42 | 3937.1926 | 1261.3469 | 0 | 0 | 2675.8457 | 0 | 0 | 0
973 | 1567.117 | 982.82 | 3903.3639 | 1627.9286 | 0 | 0 | 2275.4353 | 0 | 0 | 0
974 | 1509.312 | 845.02 | 3400.6333 | 1567.8805 | 0 | 0 | 1832.7528 | 0 | 0 | 0
975 | 1604.899 | 675.52 | 2821.1963 | 1667.1767 | 0 | 0 | 1154.0196 | 0 | 0 | 0
976 | 1215.644 | 487.04 | 2121.3754 | 1262.8168 | 0 | 0 | 858.5586 | 0 | 0 | 0
977 | 1300.307 | 241.46 | 1055.4537 | 1055.4537 | 0 | 0 | 0 | 284.28 | 0 | 0
978 | 1151.05 | 63.09 | 214.2462 | 214.2462 | 0 | 0 | 0 | 944.807 | 0 | 0
979 | 1456.677 | 0 | 0 | 0 | 0 | 0 | 0 | 1456.677 | 0 | 0
980 | 1494.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1494.4 | 0 | 0
981 | 1808.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1808.8 | 0 | 0
982 | 1650.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1344.526 | 0 | 317.7434
983 | 1209.6 | 0 | 0 | 0 | 0 | 0 | 0 | 617.6 | 0 | 614.9724
984 | 1028 | 0 | 0 | 0 | 0 | 0 | 0 | 1028 | 0 | 0
985 | 1335.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1335.2 | 0 | 0
986 | 1325.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1325.6 | 0 | 0
987 | 1358.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1358.4 | 0 | 0
988 | 1510.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1510.4 | 0 | 0
989 | 1220.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1220.8 | 0 | 0
990 | 1460.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1460.8 | 0 | 0
991 | 1494.4 | 24.35 | 48.2348 | 48.2348 | 0 | 0 | 0 | 1447.967 | 0 | 0
992 | 1213.91 | 244.21 | 1068.5592 | 1068.5592 | 0 | 0 | 0 | 185.267 | 0 | 0
993 | 1285.355 | 496.32 | 2246.9534 | 1335.2329 | -614.9724 | 0 | 296.7481 | 0 | 0 | 0
994 | 1854.487 | 711.27 | 3095.3878 | 1926.4499 | -423.0387 | 0 | 745.8992 | 0 | 0 | 0
995 | 1700.494 | 776.71 | 3285.7592 | 1766.4812 | 0 | 0 | 1519.2779 | 0 | 0 | 0
996 | 1593.166 | 875.74 | 3612.1236 | 1654.9884 | 0 | 0 | 1957.1352 | 0 | 0 | 0
997 | 1302.813 | 670.01 | 2784.0985 | 1353.3683 | 0 | 0 | 1430.7302 | 0 | 0 | 0
998 | 1470.149 | 726.56 | 2995.6002 | 1527.1978 | 0 | 0 | 1468.4025 | 0 | 0 | 0
999 | 1044.668 | 690.15 | 2893.7257 | 1085.2061 | 0 | 0 | 1808.5196 | 0 | 0 | 0
1000 | 1161.083 | 495.27 | 2164.3705 | 1206.1385 | 0 | 0 | 958.2319 | 0 | 0 | 0
1001 | 1434.037 | 265.81 | 1171.0373 | 1171.0373 | 0 | 0 | 0 | 306.744 | 0 | 0
1002 | 1519.101 | 47.93 | 158.6369 | 158.6369 | 0 | 0 | 0 | 1366.39 | 0 | 0
1003 | 1470.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1470.4 | 0 | 0
1004 | 1118.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1118.4 | 0 | 0
1005 | 1686.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1686.4 | 0 | 0
1006 | 1632 | 0 | 0 | 0 | 0 | 0 | 0 | 1326.126 | 0 | 317.7434
1007 | 1343.2 | 0 | 0 | 0 | 0 | 0 | 0 | 751.2 | 0 | 614.9724
1008 | 1206.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1206.4 | 0 | 0
1009 | 1653.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1653.6 | 0 | 0
1010 | 1780 | 0 | 0 | 0 | 0 | 0 | 0 | 1780 | 0 | 0
1011 | 1225.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1225.6 | 0 | 0
1012 | 1333.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1333.6 | 0 | 0
1013 | 1466.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1466.4 | 0 | 0
1014 | 1376 | 0 | 0 | 0 | 0 | 0 | 0 | 1376 | 0 | 0
1015 | 1212 | 17.86 | 31.1195 | 31.1195 | 0 | 0 | 0 | 1182.043 | 0 | 0
1016 | 1119.408 | 206.28 | 910.4718 | 910.4718 | 0 | 0 | 0 | 242.947 | 0 | 0
1017 | 1135.205 | 424.03 | 1936.6281 | 1179.2563 | -614.9724 | 0 | 142.3994 | 0 | 0 | 0
1018 | 1502.098 | 615.75 | 2712.7046 | 1560.3865 | -423.0387 | 0 | 729.2794 | 0 | 0 | 0
1019 | 1740.14 | 688.35 | 2935.3838 | 1807.6657 | 0 | 0 | 1127.7181 | 0 | 0 | 0
1020 | 1403.041 | 787.7 | 3269.3066 | 1457.4857 | 0 | 0 | 1811.8209 | 0 | 0 | 0
1021 | 1200.195 | 790.73 | 3246.1298 | 1246.7683 | 0 | 0 | 1999.3615 | 0 | 0 | 0
1022 | 1044.046 | 752.27 | 3112.1655 | 1084.5599 | 0 | 0 | 2027.6056 | 0 | 0 | 0
1023 | 1298.188 | 661.08 | 2816.5903 | 1348.5639 | 0 | 0 | 1468.0264 | 0 | 0 | 0
1024 | 1559.024 | 461.17 | 2036.9528 | 1619.5215 | 0 | 0 | 417.4312 | 0 | 0 | 0
1025 | 1238.191 | 245.1 | 1080.7891 | 1080.7891 | 0 | 0 | 0 | 197.775 | 0 | 0
1026 | 1380.315 | 57.47 | 194.7655 | 194.7655 | 0 | 0 | 0 | 1192.825 | 0 | 0
1027 | 886.366 | 0 | 0 | 0 | 0 | 0 | 0 | 886.366 | 0 | 0
1028 | 1113.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1113.6 | 0 | 0
1029 | 1129.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1129.6 | 0 | 0
1030 | 1440.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1134.926 | 0 | 317.7434
1031 | 1332.8 | 0 | 0 | 0 | 0 | 0 | 0 | 740.8 | 0 | 614.9724
1032 | 138.4 | 0 | 0 | 0 | 0 | 0 | 0 | 138.4 | 0 | 0
1033 | 97.6 | 0 | 0 | 0 | 0 | 0 | 0 | 97.6 | 0 | 0
1034 | 94.4 | 0 | 0 | 0 | 0 | 0 | 0 | 94.4 | 0 | 0
1035 | 103.2 | 0 | 0 | 0 | 0 | 0 | 0 | 103.2 | 0 | 0
1036 | 92.8 | 0 | 0 | 0 | 0 | 0 | 0 | 92.8 | 0 | 0
1037 | 98.4 | 0 | 0 | 0 | 0 | 0 | 0 | 98.4 | 0 | 0
1038 | 89.6 | 0 | 0 | 0 | 0 | 0 | 0 | 89.6 | 0 | 0
1039 | 84.8 | 21.63 | 42.403 | 42.403 | 0 | 0 | 0 | 43.981 | 0 | 0
1040 | 86.437 | 212.69 | 935.7667 | 89.7912 | -614.9724 | 0 | 231.0032 | 0 | 0 | 0
1041 | 660.137 | 439.94 | 2006.467 | 685.7545 | -423.0387 | 0 | 897.6738 | 0 | 0 | 0
1042 | 1046.053 | 652.88 | 2879.8046 | 1086.6448 | 0 | 0 | 1793.1598 | 0 | 0 | 0
1043 | 1011.485 | 762.49 | 3258.744 | 1050.7354 | 0 | 0 | 2208.0086 | 0 | 0 | 0
1044 | 1077.866 | 855.52 | 3573.1383 | 1119.6923 | 0 | 0 | 2453.4459 | 0 | 0 | 0
1045 | 1280.894 | 824.72 | 3440.8423 | 1330.5988 | 0 | 0 | 2110.2435 | 0 | 0 | 0
1046 | 1305.495 | 796.25 | 3363.5989 | 1356.1544 | 0 | 0 | 2007.4445 | 0 | 0 | 0
1047 | 1222.683 | 641.77 | 2783.1106 | 1270.1289 | 0 | 0 | 1512.9817 | 0 | 0 | 0
1048 | 1378.71 | 516.09 | 2300.9723 | 1432.2105 | 0 | 0 | 868.7618 | 0 | 0 | 0
1049 | 1442.884 | 291.87 | 1297.7923 | 1297.7923 | 0 | 0 | 0 | 193.571 | 0 | 0
1050 | 1317.715 | 64.92 | 223.0407 | 223.0407 | 0 | 0 | 0 | 1103.006 | 0 | 0
1051 | 1407.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1407.2 | 0 | 0
1052 | 1616.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1616.8 | 0 | 0
1053 | 1705.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1705.6 | 0 | 0
1054 | 1624 | 0 | 0 | 0 | 0 | 0 | 0 | 1318.126 | 0 | 317.7434
1055 | 1382.4 | 0 | 0 | 0 | 0 | 0 | 0 | 790.4 | 0 | 614.9724
1056 | 136.8 | 0 | 0 | 0 | 0 | 0 | 0 | 136.8 | 0 | 0
1057 | 104.8 | 0 | 0 | 0 | 0 | 0 | 0 | 104.8 | 0 | 0
1058 | 96.8 | 0 | 0 | 0 | 0 | 0 | 0 | 96.8 | 0 | 0
1059 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0
1060 | 98.4 | 0 | 0 | 0 | 0 | 0 | 0 | 98.4 | 0 | 0
1061 | 101.6 | 0 | 0 | 0 | 0 | 0 | 0 | 101.6 | 0 | 0
1062 | 95.2 | 0 | 0 | 0 | 0 | 0 | 0 | 95.2 | 0 | 0
1063 | 92.8 | 20.2 | 39.0736 | 39.0736 | 0 | 0 | 0 | 55.186 | 0 | 0
1064 | 85.97 | 217.98 | 959.4993 | 89.306 | -614.9724 | 0 | 255.2208 | 0 | 0 | 0
1065 | 932.616 | 468.34 | 2130.5657 | 968.8059 | -423.0387 | 0 | 738.7211 | 0 | 0 | 0
1066 | 1383.414 | 687.6 | 3031.037 | 1437.097 | 0 | 0 | 1593.9399 | 0 | 0 | 0
1067 | 1261.111 | 861.93 | 3692.1157 | 1310.0481 | 0 | 0 | 2382.0676 | 0 | 0 | 0
1068 | 1457.305 | 948.48 | 3997.5918 | 1513.8554 | 0 | 0 | 2483.7364 | 0 | 0 | 0
1069 | 1348.064 | 952.84 | 4015.1445 | 1400.3753 | 0 | 0 | 2614.7692 | 0 | 0 | 0
1070 | 1417.335 | 866.52 | 3699.8454 | 1472.3343 | 0 | 0 | 2227.5111 | 0 | 0 | 0
1071 | 1553.989 | 726.8 | 3178.9638 | 1614.2912 | 0 | 0 | 1564.6726 | 0 | 0 | 0
1072 | 1478.554 | 528.49 | 2378.0848 | 1535.9289 | 0 | 0 | 842.1559 | 0 | 0 | 0
1073 | 1282.839 | 291.5 | 1304.6162 | 1304.6162 | 0 | 0 | 0 | 26.957 | 0 | 0
1074 | 1716.587 | 63.24 | 219.1608 | 219.1608 | 0 | 0 | 0 | 1505.613 | 0 | 0
1075 | 1229.933 | 0 | 0 | 0 | 0 | 0 | 0 | 1229.933 | 0 | 0
1076 | 828.8 | 0 | 0 | 0 | 0 | 0 | 0 | 828.8 | 0 | 0
1077 | 1254.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1254.4 | 0 | 0
1078 | 1271.2 | 0 | 0 | 0 | 0 | 0 | 0 | 965.326 | 0 | 317.7434
1079 | 1333.6 | 0 | 0 | 0 | 0 | 0 | 0 | 741.6 | 0 | 614.9724
1080 | 1302.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1302.4 | 0 | 0
1081 | 1362.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1362.4 | 0 | 0
1082 | 933.6 | 0 | 0 | 0 | 0 | 0 | 0 | 933.6 | 0 | 0
1083 | 1361.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1361.6 | 0 | 0
1084 | 1337.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1337.6 | 0 | 0
1085 | 996 | 0 | 0 | 0 | 0 | 0 | 0 | 996 | 0 | 0
1086 | 1271.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1271.2 | 0 | 0
1087 | 1043.2 | 22.88 | 49.5531 | 49.5531 | 0 | 0 | 0 | 995.498 | 0 | 0
1088 | 860.551 | 239.86 | 1058.7602 | 893.9445 | -164.8157 | 0 | 0 | 0 | 0 | 0
1089 | 1094.398 | 492.38 | 2243.5409 | 1136.8658 | -614.9724 | 0 | 491.7026 | 0 | 0 | 0
1090 | 1122.775 | 711.32 | 3125.3656 | 1166.344 | -258.224 | 0 | 1700.7976 | 0 | 0 | 0
1091 | 1142.288 | 863.37 | 3672.1384 | 1186.6142 | 0 | 0 | 2485.5242 | 0 | 0 | 0
1092 | 987.833 | 954.13 | 3975.8164 | 1026.1656 | 0 | 0 | 2949.6508 | 0 | 0 | 0
1093 | 1098.997 | 964.5 | 4011.4308 | 1141.6433 | 0 | 0 | 2869.7875 | 0 | 0 | 0
1094 | 1323.29 | 891.46 | 3765.125 | 1374.6399 | 0 | 0 | 2390.485 | 0 | 0 | 0
1095 | 1200.589 | 742.9 | 3230.2205 | 1247.1776 | 0 | 0 | 1983.0429 | 0 | 0 | 0
1096 | 1175.229 | 443.57 | 1988.3751 | 1220.8335 | 0 | 0 | 767.5417 | 0 | 0 | 0
1097 | 1183.22 | 290.78 | 1303.0549 | 1229.1346 | 0 | 0 | 73.9203 | 0 | 0 | 0
1098 | 1286.45 | 58.84 | 207.6404 | 207.6404 | 0 | 0 | 0 | 1086.566 | 0 | 0
1099 | 1205.541 | 0 | 0 | 0 | 0 | 0 | 0 | 1205.541 | 0 | 0
1100 | 1044 | 0 | 0 | 0 | 0 | 0 | 0 | 1044 | 0 | 0
1101 | 1465.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1465.6 | 0 | 0
1102 | 1054.4 | 0 | 0 | 0 | 0 | 0 | 0 | 748.526 | 0 | 317.7434
1103 | 1262.4 | 0 | 0 | 0 | 0 | 0 | 0 | 670.4 | 0 | 614.9724
1104 | 936 | 0 | 0 | 0 | 0 | 0 | 0 | 936 | 0 | 0
1105 | 1169.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1169.6 | 0 | 0
1106 | 1276 | 0 | 0 | 0 | 0 | 0 | 0 | 1276 | 0 | 0
1107 | 1006.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1006.4 | 0 | 0
1108 | 1429.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1429.6 | 0 | 0
1109 | 1362.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1362.4 | 0 | 0
1110 | 1094.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1094.4 | 0 | 0
1111 | 1244 | 28.46 | 62.2628 | 62.2628 | 0 | 0 | 0 | 1184.063 | 0 | 0
1112 | 182.026 | 249.35 | 1091.0618 | 189.0895 | -614.9724 | 0 | 286.9999 | 0 | 0 | 0
1113 | 152.29 | 505.37 | 2286.6721 | 158.1996 | -423.0387 | 0 | 1705.4338 | 0 | 0 | 0
1114 | 181.165 | 723.41 | 3139.4591 | 188.1951 | 0 | 0 | 2951.264 | 0 | 0 | 0
1115 | 170.605 | 878.59 | 3671.5889 | 177.2253 | 0 | 0 | 3494.3636 | 0 | 0 | 0
1116 | 185.42 | 971.68 | 3956.9392 | 192.6152 | 0 | 0 | 3764.324 | 0 | 0 | 0
1117 | 195.463 | 985.06 | 3986.7456 | 203.0479 | 0 | 0 | 3783.6977 | 0 | 0 | 0
1118 | 197.058 | 912.62 | 3770.5891 | 204.7048 | 0 | 0 | 3565.8843 | 0 | 0 | 0
1119 | 129.537 | 690.53 | 2961.7788 | 134.5637 | 0 | 0 | 2827.2152 | 0 | 0 | 0
1120 | 177.796 | 504.78 | 2244.5465 | 184.6953 | 0 | 0 | 2059.8511 | 0 | 0 | 0
1121 | 117.348 | 307.43 | 1369.2444 | 121.9017 | 0 | 0 | 1247.3427 | 0 | 0 | 0
1122 | 99.261 | 72.69 | 257.4781 | 103.1128 | 0 | 0 | 154.3653 | 0 | 0 | 0
1123 | 110.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.4191
1124 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.1909
1125 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.8805
1126 | 91.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.739
1127 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.8805
1128 | 93.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.2321
1129 | 98.4 | 0 | 0 | 0 | 0 | 0 | 0 | 98.4 | 0 | 0
1130 | 90.4 | 0 | 0 | 0 | 0 | 0 | 0 | 90.4 | 0 | 0
1131 | 96.8 | 0 | 0 | 0 | 0 | 0 | 0 | 79.471 | 0 | 18.0014
1132 | 91.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.739
1133 | 96.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.5563
1134 | 89.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.0769
1135 | 92.8 | 52.38 | 123.9045 | 96.4011 | -27.5034 | 0 | 0 | 0 | 0 | 0
1136 | 86.74 | 296.87 | 1294.2136 | 90.1059 | -614.9724 | 0 | 589.1353 | 0 | 0 | 0
1137 | 858.247 | 562.2 | 2557.6744 | 891.5511 | -395.5353 | 0 | 1270.5881 | 0 | 0 | 0
1138 | 1207.142 | 781.64 | 3404.0395 | 1253.9848 | 0 | 0 | 2150.0547 | 0 | 0 | 0
1139 | 1636.944 | 937.76 | 3940.5926 | 1700.4652 | 0 | 0 | 2240.1274 | 0 | 0 | 0
1140 | 1392.639 | 1032.72 | 4248.4289 | 1446.68 | 0 | 0 | 2801.7489 | 0 | 0 | 0
1141 | 1733.618 | 1041.05 | 4269.5062 | 1800.8906 | 0 | 0 | 2468.6156 | 0 | 0 | 0
1142 | 1461.298 | 683.26 | 2893.2416 | 1518.0033 | 0 | 0 | 1375.2383 | 0 | 0 | 0
1143 | 1523.695 | 400.31 | 1724.3806 | 1582.8216 | 0 | 0 | 141.559 | 0 | 0 | 0
1144 | 1550.416 | 521.12 | 2318.1759 | 1610.5795 | 0 | 0 | 707.5964 | 0 | 0 | 0
1145 | 1733.837 | 332.61 | 1472.6096 | 1472.6096 | 0 | 0 | 0 | 316.237 | 0 | 0
1146 | 1717.427 | 87.99 | 297.4036 | 297.4036 | 0 | 0 | 0 | 1431.133 | 0 | 0
1147 | 1575.959 | 0 | 0 | 0 | 0 | 0 | 0 | 1575.959 | 0 | 0
1148 | 1707.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1707.2 | 0 | 0
1149 | 1400 | 0 | 0 | 0 | 0 | 0 | 0 | 1400 | 0 | 0
1150 | 1287.2 | 0 | 0 | 0 | 0 | 0 | 0 | 981.326 | 0 | 317.7434
1151 | 1057.6 | 0 | 0 | 0 | 0 | 0 | 0 | 465.6 | 0 | 614.9724
1152 | 1536.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1536.8 | 0 | 0
1153 | 997.6 | 0 | 0 | 0 | 0 | 0 | 0 | 997.6 | 0 | 0
1154 | 1274.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.4 | 0 | 0
1155 | 1188.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1188.8 | 0 | 0
1156 | 1111.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1111.2 | 0 | 0
1157 | 1072.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1072.8 | 0 | 0
1158 | 1068.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1068.8 | 0 | 0
1159 | 1287.2 | 44.08 | 110.5153 | 110.5153 | 0 | 0 | 0 | 1180.813 | 0 | 0
1160 | 1071.05 | 280.99 | 1230.4611 | 1112.6118 | -117.8493 | 0 | 0 | 0 | 0 | 0
1161 | 1356.959 | 545.73 | 2471.8214 | 1409.6155 | -614.9724 | 0 | 447.2335 | 0 | 0 | 0
1162 | 1375.012 | 770.57 | 3339.5412 | 1428.369 | -305.1894 | 0 | 1605.9828 | 0 | 0 | 0
1163 | 1335.484 | 933.17 | 3910.2065 | 1387.3071 | 0 | 0 | 2522.8994 | 0 | 0 | 0
1164 | 1194.744 | 955.48 | 3962.4511 | 1241.1057 | 0 | 0 | 2721.3454 | 0 | 0 | 0
1165 | 1239.472 | 597.13 | 2525.5681 | 1287.5694 | 0 | 0 | 1237.9987 | 0 | 0 | 0
1166 | 1494.782 | 626.66 | 2674.0205 | 1552.7866 | 0 | 0 | 1121.2339 | 0 | 0 | 0
1167 | 1663.536 | 575.81 | 2507.3464 | 1728.0891 | 0 | 0 | 779.2573 | 0 | 0 | 0
1168 | 1380.276 | 413.86 | 1847.9183 | 1433.8373 | 0 | 0 | 414.0811 | 0 | 0 | 0
1169 | 1448.549 | 340.36 | 1519.6145 | 1504.7596 | 0 | 0 | 14.8549 | 0 | 0 | 0
1170 | 1689.979 | 87.15 | 300.8867 | 300.8867 | 0 | 0 | 0 | 1400.332 | 0 | 0
1171 | 1823.205 | 0 | 0 | 0 | 0 | 0 | 0 | 1823.205 | 0 | 0
1172 | 855.2 | 0 | 0 | 0 | 0 | 0 | 0 | 855.2 | 0 | 0
1173 | 1082.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1082.4 | 0 | 0
1174 | 1165.6 | 0 | 0 | 0 | 0 | 0 | 0 | 859.726 | 0 | 317.7434
1175 | 1396.8 | 0 | 0 | 0 | 0 | 0 | 0 | 804.8 | 0 | 614.9724
1176 | 754.4 | 0 | 0 | 0 | 0 | 0 | 0 | 754.4 | 0 | 0
1177 | 602.4 | 0 | 0 | 0 | 0 | 0 | 0 | 602.4 | 0 | 0
1178 | 580.8 | 0 | 0 | 0 | 0 | 0 | 0 | 580.8 | 0 | 0
1179 | 700.8 | 0 | 0 | 0 | 0 | 0 | 0 | 700.8 | 0 | 0
1180 | 725.6 | 0 | 0 | 0 | 0 | 0 | 0 | 725.6 | 0 | 0
1181 | 505.6 | 0 | 0 | 0 | 0 | 0 | 0 | 505.6 | 0 | 0
1182 | 723.2 | 0 | 0 | 0 | 0 | 0 | 0 | 723.2 | 0 | 0
1183 | 676.8 | 37.51 | 96.4873 | 96.4873 | 0 | 0 | 0 | 583.917 | 0 | 0
1184 | 771.604 | 266.87 | 1169.5113 | 801.5459 | -367.9654 | 0 | 0 | 0 | 0 | 0
1185 | 658.296 | 529.04 | 2382.4197 | 683.841 | -614.9724 | 0 | 1083.6063 | 0 | 0 | 0
1186 | 829.986 | 755.16 | 3253.5697 | 862.1944 | -55.0733 | 0 | 2336.302 | 0 | 0 | 0
1187 | 571.13 | 921.88 | 3814.1867 | 593.2926 | 0 | 0 | 3220.8941 | 0 | 0 | 0
1188 | 704.878 | 1017.48 | 4092.5645 | 732.2306 | 0 | 0 | 3360.3339 | 0 | 0 | 0
1189 | 802.622 | 1020.79 | 4099.4373 | 833.7675 | 0 | 0 | 3265.6697 | 0 | 0 | 0
1190 | 845.333 | 932.84 | 3832.319 | 878.1359 | 0 | 0 | 2954.1831 | 0 | 0 | 0
1191 | 810.397 | 782.15 | 3333.0414 | 841.8443 | 0 | 0 | 2491.1971 | 0 | 0 | 0
1192 | 948.631 | 570.43 | 2533.1732 | 985.4424 | 0 | 0 | 1547.7308 | 0 | 0 | 0
1193 | 863.605 | 290.05 | 1288.9562 | 897.117 | 0 | 0 | 391.8392 | 0 | 0 | 0
1194 | 870.304 | 75.83 | 263.4565 | 263.4565 | 0 | 0 | 0 | 616.689 | 0 | 0
1195 | 797.6 | 0 | 0 | 0 | 0 | 0 | 0 | 797.6 | 0 | 0
1196 | 838.4 | 0 | 0 | 0 | 0 | 0 | 0 | 838.4 | 0 | 0
1197 | 759.2 | 0 | 0 | 0 | 0 | 0 | 0 | 759.2 | 0 | 0
1198 | 689.6 | 0 | 0 | 0 | 0 | 0 | 0 | 342.926 | 0 | 360.1266
1199 | 551.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 572.5892
1200 | 689.6 | 0 | 0 | 0 | 0 | 0 | 0 | 689.6 | 0 | 0
1201 | 1026.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1026.4 | 0 | 0
1202 | 1103.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1103.2 | 0 | 0
1203 | 797.6 | 0 | 0 | 0 | 0 | 0 | 0 | 797.6 | 0 | 0
1204 | 818.4 | 0 | 0 | 0 | 0 | 0 | 0 | 818.4 | 0 | 0
1205 | 779.2 | 0 | 0 | 0 | 0 | 0 | 0 | 779.2 | 0 | 0
1206 | 741.6 | 0 | 0 | 0 | 0 | 0 | 0 | 741.6 | 0 | 0
1207 | 836.8 | 40.5 | 107.2566 | 107.2566 | 0 | 0 | 0 | 733.55 | 0 | 0
1208 | 625.816 | 271.67 | 1193.4391 | 650.1006 | -543.3385 | 0 | 0 | 0 | 0 | 0
1209 | 296.104 | 533.8 | 2415.3665 | 307.5942 | -494.6726 | 0 | 1613.0996 | 0 | 0 | 0
1210 | 281.168 | 761.17 | 3290.8805 | 292.0787 | 0 | 0 | 2998.8018 | 0 | 0 | 0
1211 | 221.19 | 931.04 | 3869.477 | 229.7732 | 0 | 0 | 3639.7038 | 0 | 0 | 0
1212 | 299.592 | 1025.95 | 4181.8602 | 311.2176 | 0 | 0 | 3870.6426 | 0 | 0 | 0
1213 | 888.252 | 1032.8 | 4210.017 | 922.7204 | 0 | 0 | 3287.2966 | 0 | 0 | 0
1214 | 1121.586 | 950.77 | 3962.0366 | 1165.1089 | 0 | 0 | 2796.9278 | 0 | 0 | 0
1215 | 839.555 | 803.08 | 3457.6554 | 872.1337 | 0 | 0 | 2585.5217 | 0 | 0 | 0
1216 | 1363.969 | 588.21 | 2630.0677 | 1416.8975 | 0 | 0 | 1213.1702 | 0 | 0 | 0
1217 | 1384.49 | 331.72 | 1481.4041 | 1438.2148 | 0 | 0 | 43.1893 | 0 | 0 | 0
1218 | 1247.034 | 81.71 | 283.3631 | 283.3631 | 0 | 0 | 0 | 974.256 | 0 | 0
1219 | 1191.158 | 0 | 0 | 0 | 0 | 0 | 0 | 1191.158 | 0 | 0
1220 | 1089.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1089.6 | 0 | 0
1221 | 1178.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1178.4 | 0 | 0
1222 | 1048 | 0 | 0 | 0 | 0 | 0 | 0 | 742.126 | 0 | 317.7434
1223 | 1239.2 | 0 | 0 | 0 | 0 | 0 | 0 | 647.2 | 0 | 614.9724
1224 | 1102.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1102.4 | 0 | 0
1225 | 1004 | 0 | 0 | 0 | 0 | 0 | 0 | 1004 | 0 | 0
1226 | 894.4 | 0 | 0 | 0 | 0 | 0 | 0 | 894.4 | 0 | 0
1227 | 741.6 | 0 | 0 | 0 | 0 | 0 | 0 | 741.6 | 0 | 0
1228 | 812 | 0 | 0 | 0 | 0 | 0 | 0 | 812 | 0 | 0
1229 | 906.4 | 0 | 0 | 0 | 0 | 0 | 0 | 906.4 | 0 | 0
1230 | 1295.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1295.2 | 0 | 0
1231 | 1083.2 | 43.49 | 111.6029 | 111.6029 | 0 | 0 | 0 | 975.766 | 0 | 0
1232 | 928.89 | 280.31 | 1234.553 | 964.9353 | -269.6176 | 0 | 0 | 0 | 0 | 0
1233 | 1047.146 | 542.81 | 2475.7428 | 1087.7802 | -614.9724 | 0 | 772.9902 | 0 | 0 | 0
1234 | 1458.486 | 770.57 | 3376.9589 | 1515.0822 | -153.4211 | 0 | 1708.4557 | 0 | 0 | 0
1235 | 1341.872 | 940.15 | 3979.5717 | 1393.943 | 0 | 0 | 2585.6286 | 0 | 0 | 0
1236 | 1455.678 | 1030.73 | 4278.8326 | 1512.1652 | 0 | 0 | 2766.6674 | 0 | 0 | 0
1237 | 1622.4 | 1037.56 | 4303.097 | 1685.3568 | 0 | 0 | 2617.7402 | 0 | 0 | 0
1238 | 1434.147 | 957.32 | 4038.2807 | 1489.7987 | 0 | 0 | 2548.482 | 0 | 0 | 0
1239 | 1627.379 | 773.32 | 3362.1144 | 1690.529 | 0 | 0 | 1671.5854 | 0 | 0 | 0
1240 | 1212.806 | 589.47 | 2652.3999 | 1259.8686 | 0 | 0 | 1392.5313 | 0 | 0 | 0
1241 | 1458.823 | 334.13 | 1498.4416 | 1498.4416 | 0 | 0 | 0 | 16.356 | 0 | 0
1242 | 1503.121 | 82.8 | 289.1233 | 289.1233 | 0 | 0 | 0 | 1224.798 | 0 | 0
1243 | 1519.235 | 0 | 0 | 0 | 0 | 0 | 0 | 1519.235 | 0 | 0
1244 | 1223.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1223.2 | 0 | 0
1245 | 1371.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1371.2 | 0 | 0
1246 | 1432.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1126.926 | 0 | 317.7434
1247 | 1228 | 0 | 0 | 0 | 0 | 0 | 0 | 636 | 0 | 614.9724
1248 | 1250.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1250.4 | 0 | 0
1249 | 1195.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1195.2 | 0 | 0
1250 | 1082.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1082.4 | 0 | 0
1251 | 1088.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1088.8 | 0 | 0
1252 | 1428 | 0 | 0 | 0 | 0 | 0 | 0 | 1428 | 0 | 0
1253 | 942.4 | 0 | 0 | 0 | 0 | 0 | 0 | 942.4 | 0 | 0
1254 | 957.6 | 0 | 0 | 0 | 0 | 0 | 0 | 957.6 | 0 | 0
1255 | 1361.6 | 40.54 | 107.5402 | 107.5402 | 0 | 0 | 0 | 1258.077 | 0 | 0
1256 | 1216.436 | 273.09 | 1201.7548 | 1201.7548 | 0 | 0 | 0 | 59.573 | 0 | 0
1257 | 1066.076 | 534.16 | 2417.3714 | 1107.4448 | -614.9724 | 0 | 694.9541 | 0 | 0 | 0
1258 | 1100.807 | 759.98 | 3285.5223 | 1143.5235 | -423.0387 | 0 | 1718.9601 | 0 | 0 | 0
1259 | 1411.611 | 926.82 | 3858.9384 | 1466.3882 | 0 | 0 | 2392.5502 | 0 | 0 | 0
1260 | 1365.056 | 1016.5 | 4098.3247 | 1418.0267 | 0 | 0 | 2680.298 | 0 | 0 | 0
1261 | 1239.767 | 1022.1 | 4046.1279 | 1287.8758 | 0 | 0 | 2758.252 | 0 | 0 | 0
1262 | 1146.147 | 880.6 | 3585.3504 | 1190.6229 | 0 | 0 | 2394.7275 | 0 | 0 | 0
1263 | 1181.115 | 595.4 | 2550.2116 | 1226.9479 | 0 | 0 | 1323.2638 | 0 | 0 | 0
1264 | 1267.883 | 450.46 | 1995.5252 | 1317.0829 | 0 | 0 | 678.4423 | 0 | 0 | 0
1265 | 1187.464 | 319.28 | 1420.4066 | 1233.5432 | 0 | 0 | 186.8633 | 0 | 0 | 0
1266 | 1008.407 | 76.93 | 270.1869 | 270.1869 | 0 | 0 | 0 | 748.313 | 0 | 0
1267 | 1409.602 | 0 | 0 | 0 | 0 | 0 | 0 | 1409.602 | 0 | 0
1268 | 946.4 | 0 | 0 | 0 | 0 | 0 | 0 | 946.4 | 0 | 0
1269 | 1150.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1150.4 | 0 | 0
1270 | 1396 | 0 | 0 | 0 | 0 | 0 | 0 | 1090.126 | 0 | 317.7434
1271 | 1171.2 | 0 | 0 | 0 | 0 | 0 | 0 | 579.2 | 0 | 614.9724
1272 | 1109.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1109.6 | 0 | 0
1273 | 1380.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1380.8 | 0 | 0
1274 | 1206.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1206.4 | 0 | 0
1275 | 1380.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1380.8 | 0 | 0
1276 | 1010.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1010.4 | 0 | 0
1277 | 960 | 0 | 0 | 0 | 0 | 0 | 0 | 960 | 0 | 0
1278 | 1000 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 | 0 | 0
1279 | 1016 | 35.87 | 97.2082 | 97.2082 | 0 | 0 | 0 | 922.423 | 0 | 0
1280 | 231.095 | 263.88 | 1160.3678 | 240.0626 | -614.9724 | 0 | 305.3328 | 0 | 0 | 0
1281 | 181.355 | 523.62 | 2355.9718 | 188.3924 | -423.0387 | 0 | 1744.5406 | 0 | 0 | 0
1282 | 156.897 | 750.6 | 3230.1976 | 162.9853 | 0 | 0 | 3067.2123 | 0 | 0 | 0
1283 | 202.713 | 918 | 3812.0872 | 210.5792 | 0 | 0 | 3601.508 | 0 | 0 | 0
1284 | 193.831 | 1012.53 | 4133.0229 | 201.3526 | 0 | 0 | 3931.6703 | 0 | 0 | 0
1285 | 194.696 | 682.43 | 2858.9278 | 202.2511 | 0 | 0 | 2656.6767 | 0 | 0 | 0
1286 | 147.249 | 677.73 | 2876.2499 | 152.963 | 0 | 0 | 2723.2869 | 0 | 0 | 0
1287 | 149.362 | 733.89 | 3189.4443 | 155.158 | 0 | 0 | 3034.2863 | 0 | 0 | 0
1288 | 167.046 | 495.68 | 2226.9813 | 173.5282 | 0 | 0 | 2053.4531 | 0 | 0 | 0
1289 | 135.46 | 325.79 | 1462.9934 | 140.7165 | 0 | 0 | 1322.2769 | 0 | 0 | 0
1290 | 134.638 | 81.02 | 285.5757 | 139.8626 | 0 | 0 | 145.7131 | 0 | 0 | 0
1291 | 106.102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.2193
1292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1294 | 85.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.9217
1295 | 87.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.5838
1296 | 90.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.9079
1297 | 84.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.0906
1298 | 87.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.5838
1299 | 80.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9354
1300 | 86.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.7527
1301 | 81.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.7665
1302 | 86.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.7527
1303 | 68.8 | 46.8 | 129.4756 | 71.4698 | -58.0058 | 0 | 0 | 0 | 0 | 0
1304 | 94.436 | 281.42 | 1230.0882 | 98.1006 | -614.9724 | 0 | 517.0152 | 0 | 0 | 0
1305 | 767.602 | 543.57 | 2446.7041 | 797.3886 | -340.3259 | 0 | 1308.9896 | 0 | 0 | 0
1306 | 1311.495 | 769.07 | 3317.2214 | 1362.3872 | 0 | 0 | 1954.8342 | 0 | 0 | 0
1307 | 1454.312 | 934.48 | 3899.6564 | 1510.7462 | 0 | 0 | 2388.9102 | 0 | 0 | 0
1308 | 1278.237 | 1025.82 | 4202.0327 | 1327.8387 | 0 | 0 | 2874.1941 | 0 | 0 | 0
1309 | 1477.846 | 1030.3 | 4217.6937 | 1535.1934 | 0 | 0 | 2682.5003 | 0 | 0 | 0
1310 | 1606.507 | 952.25 | 3968.2996 | 1668.8471 | 0 | 0 | 2299.4525 | 0 | 0 | 0
1311 | 1514.242 | 760.91 | 3282.2231 | 1573.0018 | 0 | 0 | 1709.2213 | 0 | 0 | 0
1312 | 1656.625 | 559.99 | 2499.5107 | 1720.9099 | 0 | 0 | 778.6008 | 0 | 0 | 0
1313 | 1550.847 | 323.88 | 1439.131 | 1439.131 | 0 | 0 | 0 | 165.475 | 0 | 0
1314 | 1602.881 | 77.23 | 274.9186 | 274.9186 | 0 | 0 | 0 | 1338.232 | 0 | 0
1315 | 1592.239 | 0 | 0 | 0 | 0 | 0 | 0 | 1592.239 | 0 | 0
1316 | 1521.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1521.6 | 0 | 0
1317 | 1444 | 0 | 0 | 0 | 0 | 0 | 0 | 1444 | 0 | 0
1318 | 1625.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1319.726 | 0 | 317.7434
1319 | 1578.4 | 0 | 0 | 0 | 0 | 0 | 0 | 986.4 | 0 | 614.9724
1320 | 1232.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1232.8 | 0 | 0
1321 | 1146.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1146.4 | 0 | 0
1322 | 1488 | 0 | 0 | 0 | 0 | 0 | 0 | 1488 | 0 | 0
1323 | 1347.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1347.2 | 0 | 0
1324 | 1243.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1243.2 | 0 | 0
1325 | 1531.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1531.2 | 0 | 0
1326 | 1331.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1331.2 | 0 | 0
1327 | 1144.8 | 61.03 | 159.6072 | 159.6072 | 0 | 0 | 0 | 991.155 | 0 | 0
1328 | 1010.871 | 305.62 | 1336.8482 | 1050.0976 | -286.7506 | 0 | 0 | 0 | 0 | 0
1329 | 1203.916 | 566.07 | 2585.2817 | 1250.6337 | -614.9724 | 0 | 719.6756 | 0 | 0 | 0
1330 | 1503.542 | 789.79 | 3485.7239 | 1561.8866 | -136.2891 | 0 | 1787.5482 | 0 | 0 | 0
1331 | 1515.135 | 748.89 | 3262.7953 | 1573.9294 | 0 | 0 | 1688.8659 | 0 | 0 | 0
1332 | 1556.164 | 111.22 | 445.8737 | 445.8737 | 0 | 0 | 0 | 1112.922 | 0 | 14.5682
1333 | 1211.064 | 299.42 | 1274.2717 | 1258.059 | -16.2126 | 0 | 0 | 0 | 0 | 0
1334 | 1410.099 | 270.48 | 1153.1948 | 1153.1948 | 0 | 0 | 0 | 299.982 | 0 | 0
1335 | 1317.507 | 185.89 | 786.8105 | 786.8105 | 0 | 0 | 0 | 560.088 | 0 | 0
1336 | 1520.142 | 111.94 | 465.2007 | 465.2007 | 0 | 0 | 0 | 1072.319 | 0 | 0
1337 | 1602.996 | 37.24 | 135.0051 | 135.0051 | 0 | 0 | 0 | 1473.034 | 0 | 0
1338 | 1509.998 | 4.89 | 0 | 0 | 0 | 0 | 0 | 1509.998 | 0 | 0
1339 | 1268.157 | 0 | 0 | 0 | 0 | 0 | 0 | 1268.157 | 0 | 0
1340 | 1219.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1219.2 | 0 | 0
1341 | 1537.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1537.6 | 0 | 0
1342 | 1788 | 0 | 0 | 0 | 0 | 0 | 0 | 1482.126 | 0 | 317.7434
1343 | 1920 | 0 | 0 | 0 | 0 | 0 | 0 | 1328 | 0 | 614.9724
1344 | 1416 | 0 | 0 | 0 | 0 | 0 | 0 | 1416 | 0 | 0
1345 | 1318.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1318.4 | 0 | 0
1346 | 1386.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1386.4 | 0 | 0
1347 | 1447.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1447.2 | 0 | 0
1348 | 1560.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1560.8 | 0 | 0
1349 | 1575.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1575.2 | 0 | 0
1350 | 1132 | 0 | 0 | 0 | 0 | 0 | 0 | 1132 | 0 | 0
1351 | 1085.6 | 59.12 | 154.3913 | 154.3913 | 0 | 0 | 0 | 936.976 | 0 | 0
1352 | 972.737 | 299.7 | 1311.4889 | 1010.4838 | -301.0051 | 0 | 0 | 0 | 0 | 0
1353 | 1002.649 | 542.28 | 2470.633 | 1041.5565 | -614.9724 | 0 | 814.104 | 0 | 0 | 0
1354 | 1224.946 | 777.35 | 3424.076 | 1272.4808 | -122.0336 | 0 | 2029.5617 | 0 | 0 | 0
1355 | 1629.851 | 939.11 | 4031.7394 | 1693.097 | 0 | 0 | 2338.6424 | 0 | 0 | 0
1356 | 1267.651 | 827.52 | 3542.1133 | 1316.8419 | 0 | 0 | 2225.2714 | 0 | 0 | 0
1357 | 1387.724 | 634.65 | 2708.8195 | 1441.5743 | 0 | 0 | 1267.2452 | 0 | 0 | 0
1358 | 1508.577 | 538.5 | 2321.8605 | 1567.117 | 0 | 0 | 754.7436 | 0 | 0 | 0
1359 | 1492.205 | 379.76 | 1654.388 | 1550.1096 | 0 | 0 | 104.2783 | 0 | 0 | 0
1360 | 1115.506 | 190.58 | 821.4255 | 821.4255 | 0 | 0 | 0 | 324.765 | 0 | 0
1361 | 1715.058 | 309.52 | 1370.4982 | 1370.4982 | 0 | 0 | 0 | 395.755 | 0 | 0
1362 | 1580.662 | 50.54 | 172.0146 | 172.0146 | 0 | 0 | 0 | 1415.073 | 0 | 0
1363 | 1152.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1152.8 | 0 | 0
1364 | 1612 | 0 | 0 | 0 | 0 | 0 | 0 | 1612 | 0 | 0
1365 | 1400.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1400.8 | 0 | 0
1366 | 1607.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1301.326 | 0 | 317.7434
1367 | 1369.6 | 0 | 0 | 0 | 0 | 0 | 0 | 777.6 | 0 | 614.9724
1368 | 1172 | 0 | 0 | 0 | 0 | 0 | 0 | 1172 | 0 | 0
1369 | 1296.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1296.8 | 0 | 0
1370 | 1394.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1394.4 | 0 | 0
1371 | 1192 | 0 | 0 | 0 | 0 | 0 | 0 | 1192 | 0 | 0
1372 | 1368.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1368.8 | 0 | 0
1373 | 1286.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1286.4 | 0 | 0
1374 | 717.6 | 0 | 0 | 0 | 0 | 0 | 0 | 717.6 | 0 | 0
1375 | 961.6 | 60.56 | 160.4766 | 160.4766 | 0 | 0 | 0 | 807.118 | 0 | 0
1376 | 858.742 | 300.98 | 1317.9763 | 892.0653 | -425.911 | 0 | 0 | 0 | 0 | 0
1377 | 924.647 | 560.52 | 2541.6301 | 960.5277 | -612.1001 | 0 | 969.0023 | 0 | 0 | 0
1378 | 1261.322 | 780.12 | 3375.8173 | 1310.2673 | 0 | 0 | 2065.55 | 0 | 0 | 0
1379 | 921.625 | 942.29 | 3906.1552 | 957.3884 | 0 | 0 | 2948.7667 | 0 | 0 | 0
1380 | 1166.42 | 1030.25 | 4160.6 | 1211.6826 | 0 | 0 | 2948.9174 | 0 | 0 | 0
1381 | 1425.732 | 1007.97 | 4058.66 | 1481.0572 | 0 | 0 | 2577.6028 | 0 | 0 | 0
1382 | 1270.075 | 642.08 | 2682.0287 | 1319.3599 | 0 | 0 | 1362.6687 | 0 | 0 | 0
1383 | 1409.846 | 397.26 | 1697.7196 | 1464.5547 | 0 | 0 | 233.1649 | 0 | 0 | 0
1384 | 1503.303 | 198.31 | 848.2038 | 848.2038 | 0 | 0 | 0 | 686.784 | 0 | 0
1385 | 1426.651 | 150.75 | 647.1982 | 647.1982 | 0 | 0 | 0 | 803.629 | 0 | 0
1386 | 1530.718 | 72 | 248.6722 | 248.6722 | 0 | 0 | 0 | 1291.335 | 0 | 0
1387 | 1079.591 | 0 | 0 | 0 | 0 | 0 | 0 | 1079.591 | 0 | 0
1388 | 1292 | 0 | 0 | 0 | 0 | 0 | 0 | 1292 | 0 | 0
1389 | 1392.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1392.8 | 0 | 0
1390 | 1493.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1187.726 | 0 | 317.7434
1391 | 1524 | 0 | 0 | 0 | 0 | 0 | 0 | 932 | 0 | 614.9724
1392 | 1385.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1385.6 | 0 | 0
1393 | 1531.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1531.2 | 0 | 0
1394 | 1497.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1497.6 | 0 | 0
1395 | 1485.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1485.6 | 0 | 0
1396 | 1413.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1413.6 | 0 | 0
1397 | 1488.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1488.8 | 0 | 0
1398 | 1299.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1299.2 | 0 | 0
1399 | 1104 | 23.73 | 58.8566 | 58.8566 | 0 | 0 | 0 | 1047.342 | 0 | 0
1400 | 1358.071 | 291.96 | 1272.4382 | 1272.4382 | 0 | 0 | 0 | 133.165 | 0 | 0
1401 | 1671.657 | 271.18 | 1195.6092 | 1195.6092 | 0 | 0 | 0 | 520.71 | 0 | 0
1402 | 1400.192 | 774.18 | 3274.0736 | 1454.5261 | -614.9724 | 0 | 1204.5751 | 0 | 0 | 0
1403 | 1499.733 | 938.68 | 3804.2214 | 1557.9298 | -423.0387 | 0 | 1823.253 | 0 | 0 | 0
1404 | 1335.797 | 766.33 | 3139.4819 | 1387.6323 | 0 | 0 | 1751.8497 | 0 | 0 | 0
1405 | 1593.236 | 693.17 | 2855.8997 | 1655.0611 | 0 | 0 | 1200.8386 | 0 | 0 | 0
1406 | 1620.676 | 772.16 | 3160.5541 | 1683.5659 | 0 | 0 | 1476.9882 | 0 | 0 | 0
1407 | 1525.559 | 604.12 | 2539.4839 | 1584.7579 | 0 | 0 | 954.726 | 0 | 0 | 0
1408 | 1514.83 | 319.48 | 1378.79 | 1378.79 | 0 | 0 | 0 | 187.545 | 0 | 0
1409 | 1822.304 | 230.12 | 999.2003 | 999.2003 | 0 | 0 | 0 | 860.429 | 0 | 0
1410 | 1605.867 | 80.83 | 273.9899 | 273.9899 | 0 | 0 | 0 | 1342.112 | 0 | 0
1411 | 1954.45 | 0 | 0 | 0 | 0 | 0 | 0 | 1954.45 | 0 | 0
1412 | 1688.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1688.8 | 0 | 0
1413 | 1488.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1488.8 | 0 | 0
1414 | 1700 | 0 | 0 | 0 | 0 | 0 | 0 | 1394.126 | 0 | 317.7434
1415 | 1531.2 | 0 | 0 | 0 | 0 | 0 | 0 | 939.2 | 0 | 614.9724
1416 | 1661.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1661.6 | 0 | 0
1417 | 677.6 | 0 | 0 | 0 | 0 | 0 | 0 | 677.6 | 0 | 0
1418 | 501.6 | 0 | 0 | 0 | 0 | 0 | 0 | 501.6 | 0 | 0
1419 | 592.8 | 0 | 0 | 0 | 0 | 0 | 0 | 592.8 | 0 | 0
1420 | 738.4 | 0 | 0 | 0 | 0 | 0 | 0 | 738.4 | 0 | 0
1421 | 784.8 | 0 | 0 | 0 | 0 | 0 | 0 | 784.8 | 0 | 0
1422 | 656.8 | 0 | 0 | 0 | 0 | 0 | 0 | 656.8 | 0 | 0
1423 | 596 | 52.01 | 150.7773 | 150.7773 | 0 | 0 | 0 | 450.855 | 0 | 0
1424 | 458.959 | 273.92 | 1207.4848 | 476.7688 | -614.9724 | 0 | 115.7436 | 0 | 0 | 0
1425 | 545.507 | 530.28 | 2396.7251 | 566.6753 | -423.0387 | 0 | 1407.0112 | 0 | 0 | 0
1426 | 657.357 | 702.67 | 3049.1579 | 682.8656 | 0 | 0 | 2366.2923 | 0 | 0 | 0
1427 | 784.747 | 903.07 | 3754.9883 | 815.1989 | 0 | 0 | 2939.7894 | 0 | 0 | 0
1428 | 756.627 | 968.22 | 3917.7347 | 785.9877 | 0 | 0 | 3131.747 | 0 | 0 | 0
1429 | 915.603 | 830.53 | 3361.0922 | 951.1327 | 0 | 0 | 2409.9595 | 0 | 0 | 0
1430 | 833.363 | 724.63 | 2981.0289 | 865.7014 | 0 | 0 | 2115.3275 | 0 | 0 | 0
1431 | 642.919 | 523.75 | 2223.2915 | 667.8673 | 0 | 0 | 1555.4242 | 0 | 0 | 0
1432 | 667.766 | 449.28 | 1966.34 | 693.6785 | 0 | 0 | 1272.6615 | 0 | 0 | 0
1433 | 671.56 | 258.69 | 1134.7664 | 697.6197 | 0 | 0 | 437.1467 | 0 | 0 | 0
1434 | 759.475 | 61.27 | 214.5308 | 214.5308 | 0 | 0 | 0 | 552.958 | 0 | 0
1435 | 768.029 | 0 | 0 | 0 | 0 | 0 | 0 | 768.029 | 0 | 0
1436 | 534.4 | 0 | 0 | 0 | 0 | 0 | 0 | 534.4 | 0 | 0
1437 | 708.8 | 0 | 0 | 0 | 0 | 0 | 0 | 708.8 | 0 | 0
1438 | 805.6 | 0 | 0 | 0 | 0 | 0 | 0 | 499.726 | 0 | 317.7434
1439 | 713.6 | 0 | 0 | 0 | 0 | 0 | 0 | 121.6 | 0 | 614.9724
1440 | 728.8 | 0 | 0 | 0 | 0 | 0 | 0 | 728.8 | 0 | 0
1441 | 1704 | 0 | 0 | 0 | 0 | 0 | 0 | 1704 | 0 | 0
1442 | 1666.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1666.4 | 0 | 0
1443 | 1551.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1551.2 | 0 | 0
1444 | 1624 | 0 | 0 | 0 | 0 | 0 | 0 | 1624 | 0 | 0
1445 | 1580.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1580.8 | 0 | 0
1446 | 1460 | 0 | 0 | 0 | 0 | 0 | 0 | 1460 | 0 | 0
1447 | 1464 | 27.5 | 78.7092 | 78.7092 | 0 | 0 | 0 | 1388.231 | 0 | 0
1448 | 110.259 | 184.92 | 815.7235 | 114.5376 | -614.9724 | 0 | 86.2135 | 0 | 0 | 0
1449 | 89.69 | 441.59 | 1992.6155 | 93.1704 | -423.0387 | 0 | 1476.4064 | 0 | 0 | 0
1450 | 0 | 604.12 | 2642.0202 | 0 | 0 | 0 | 2642.0202 | 0 | 0 | 0
1451 | 0 | 806.34 | 3424.7149 | 0 | 0 | 0 | 3424.7149 | 0 | 0 | 0
1452 | 0 | 807.44 | 3384.1797 | 0 | 0 | 0 | 3384.1797 | 0 | 0 | 0
1453 | 0 | 619.36 | 2609.2448 | 0 | 0 | 0 | 2609.2448 | 0 | 0 | 0
1454 | 87.814 | 646.51 | 2740.5176 | 91.2216 | 0 | 0 | 2649.296 | 0 | 0 | 0
1455 | 71.433 | 478.07 | 2066.085 | 74.2049 | 0 | 0 | 1991.8801 | 0 | 0 | 0
1456 | 76.614 | 549.13 | 2442.1687 | 79.587 | 0 | 0 | 2362.5817 | 0 | 0 | 0
1457 | 71.47 | 308.59 | 1369.0854 | 74.2434 | 0 | 0 | 1294.8421 | 0 | 0 | 0
1458 | 83.419 | 75.39 | 270.5889 | 86.6561 | 0 | 0 | 183.9328 | 0 | 0 | 0
1459 | 77.625 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.6372
1460 | 86.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.7527
1461 | 79.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.2733
1462 | 86.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.7527
1463 | 79.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.2733
1464 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.2596
1465 | 75.2 | 0 | 0 | 0 | 0 | 0 | 0 | 67.983 | 0 | 7.4971
1466 | 81.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.7665
1467 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.9492
1468 | 80 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.1044
1469 | 76.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.7802
1470 | 81.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.7665
1471 | 67.2 | 24.11 | 67.9046 | 67.9046 | 0 | 0 | 0 | 0 | 0 | 1.9031
1472 | 79.057 | 122.97 | 533.2953 | 82.1248 | -451.1706 | 0 | 0 | 0 | 0 | 0
1473 | 544.574 | 314.68 | 1400.3524 | 565.7061 | -586.8416 | 0 | 247.8048 | 0 | 0 | 0
1474 | 1505.096 | 457.58 | 1990.8537 | 1563.5009 | 0 | 0 | 427.3528 | 0 | 0 | 0
1475 | 1673.221 | 716.95 | 3027.879 | 1738.1499 | 0 | 0 | 1289.7291 | 0 | 0 | 0
1476 | 1557.38 | 969.39 | 3973.4157 | 1617.8137 | 0 | 0 | 2355.602 | 0 | 0 | 0
1477 | 1552.097 | 986.59 | 4027.0617 | 1612.3257 | 0 | 0 | 2414.7359 | 0 | 0 | 0
1478 | 1601.467 | 904.05 | 3753.9942 | 1663.6115 | 0 | 0 | 2090.3826 | 0 | 0 | 0
1479 | 1699.22 | 754.19 | 3229.9016 | 1765.1578 | 0 | 0 | 1464.7438 | 0 | 0 | 0
1480 | 1209.033 | 409.02 | 1810.8611 | 1255.9492 | 0 | 0 | 554.9118 | 0 | 0 | 0
1481 | 1602.265 | 304.39 | 1352.3659 | 1352.3659 | 0 | 0 | 0 | 300.417 | 0 | 0
1482 | 1255.783 | 72.03 | 258.0453 | 258.0453 | 0 | 0 | 0 | 1007.377 | 0 | 0
1483 | 1313.251 | 0 | 0 | 0 | 0 | 0 | 0 | 1313.251 | 0 | 0
1484 | 1345.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1345.6 | 0 | 0
1485 | 1182.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1182.4 | 0 | 0
1486 | 1305.6 | 0 | 0 | 0 | 0 | 0 | 0 | 999.726 | 0 | 317.7434
1487 | 1395.2 | 0 | 0 | 0 | 0 | 0 | 0 | 803.2 | 0 | 614.9724
1488 | 1414.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1414.4 | 0 | 0
1489 | 1534.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1534.4 | 0 | 0
1490 | 1493.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1493.6 | 0 | 0
1491 | 1685.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1685.6 | 0 | 0
1492 | 1434.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1434.4 | 0 | 0
1493 | 1459.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1459.2 | 0 | 0
1494 | 1717.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1717.6 | 0 | 0
1495 | 1190.4 | 37.12 | 113.4011 | 113.4011 | 0 | 0 | 0 | 1081.235 | 0 | 0
1496 | 1580.043 | 237.98 | 1051.823 | 1051.823 | 0 | 0 | 0 | 567.511 | 0 | 0
1497 | 1502.036 | 441.96 | 1977.2516 | 1560.3221 | -416.9295 | 0 | 0 | 0 | 0 | 0
1498 | 1441.807 | 603.63 | 2616.4064 | 1497.756 | -614.9724 | 0 | 503.678 | 0 | 0 | 0
1499 | 1867.076 | 856.76 | 3578.727 | 1939.5285 | -6.1092 | 0 | 1633.0894 | 0 | 0 | 0
1500 | 1969.563 | 978.72 | 4015.908 | 2045.9914 | 0 | 0 | 1969.9166 | 0 | 0 | 0
1501 | 1991.36 | 600.79 | 2537.3782 | 2068.6342 | 0 | 0 | 468.744 | 0 | 0 | 0
1502 | 1801.825 | 264.04 | 1113.6891 | 1113.6891 | 0 | 0 | 0 | 137.738 | 0 | 614.9724
1503 | 1593.282 | 705.82 | 3050.5 | 1655.1089 | -614.9724 | 0 | 780.4187 | 0 | 0 | 0
1504 | 1359.178 | 556.71 | 2484.2049 | 1411.9206 | -69.4254 | 0 | 1002.859 | 0 | 0 | 0
1505 | 1889.839 | 309.29 | 1378.0919 | 1378.0919 | 0 | 0 | 0 | 563.226 | 0 | 0
1506 | 1338.014 | 73.96 | 267.325 | 267.325 | 0 | 0 | 0 | 1080.675 | 0 | 0
1507 | 1353.885 | 0 | 0 | 0 | 0 | 0 | 0 | 1353.885 | 0 | 0
1508 | 1158.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1158.4 | 0 | 0
1509 | 1659.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1659.2 | 0 | 0
1510 | 1568 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.126 | 0 | 317.7434
1511 | 1603.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1011.2 | 0 | 614.9724
1512 | 1517.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1517.6 | 0 | 0
1513 | 1664 | 0 | 0 | 0 | 0 | 0 | 0 | 1664 | 0 | 0
1514 | 1617.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1617.6 | 0 | 0
1515 | 1648 | 0 | 0 | 0 | 0 | 0 | 0 | 1648 | 0 | 0
1516 | 1176.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1176.8 | 0 | 0
1517 | 1515.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1515.2 | 0 | 0
1518 | 1512.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1512.8 | 0 | 0
1519 | 1321.6 | 39.15 | 119.581 | 119.581 | 0 | 0 | 0 | 1206.486 | 0 | 0
1520 | 1341.317 | 257.9 | 1145.3882 | 1145.3882 | 0 | 0 | 0 | 238.715 | 0 | 0
1521 | 1629.663 | 489.01 | 2215.5919 | 1692.9017 | -522.6902 | 0 | 0 | 0 | 0 | 0
1522 | 1448.199 | 607.25 | 2667.1312 | 1504.396 | -515.3219 | 0 | 647.4132 | 0 | 0 | 0
1523 | 1859.743 | 885.03 | 3764.2191 | 1931.9099 | 0 | 0 | 1832.3093 | 0 | 0 | 0
1524 | 1762.66 | 948.96 | 3972.1203 | 1831.0596 | 0 | 0 | 2141.0607 | 0 | 0 | 0
1525 | 1573.75 | 705.55 | 2980.1418 | 1634.819 | 0 | 0 | 1345.3228 | 0 | 0 | 0
1526 | 1726.047 | 666.89 | 2844.1903 | 1793.0258 | 0 | 0 | 1051.1644 | 0 | 0 | 0
1527 | 1828.904 | 516.59 | 2244.5932 | 1899.8742 | 0 | 0 | 344.719 | 0 | 0 | 0
1528 | 1697.557 | 477.19 | 2134.1257 | 1763.4303 | 0 | 0 | 370.6954 | 0 | 0 | 0
1529 | 1829.581 | 314.92 | 1405.7875 | 1405.7875 | 0 | 0 | 0 | 476.307 | 0 | 0
1530 | 1704.422 | 79.39 | 284.9244 | 284.9244 | 0 | 0 | 0 | 1430.141 | 0 | 0
1531 | 1675.433 | 0 | 0 | 0 | 0 | 0 | 0 | 1675.433 | 0 | 0
1532 | 1698.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1698.4 | 0 | 0
1533 | 1537.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1537.6 | 0 | 0
1534 | 1532 | 0 | 0 | 0 | 0 | 0 | 0 | 1226.126 | 0 | 317.7434
1535 | 1324 | 0 | 0 | 0 | 0 | 0 | 0 | 732 | 0 | 614.9724
1536 | 382.4 | 0 | 0 | 0 | 0 | 0 | 0 | 382.4 | 0 | 0
1537 | 394.4 | 0 | 0 | 0 | 0 | 0 | 0 | 394.4 | 0 | 0
1538 | 378.4 | 0 | 0 | 0 | 0 | 0 | 0 | 378.4 | 0 | 0
1539 | 357.6 | 0 | 0 | 0 | 0 | 0 | 0 | 357.6 | 0 | 0
1540 | 367.2 | 0 | 0 | 0 | 0 | 0 | 0 | 367.2 | 0 | 0
1541 | 380 | 0 | 0 | 0 | 0 | 0 | 0 | 380 | 0 | 0
1542 | 397.6 | 0 | 0 | 0 | 0 | 0 | 0 | 397.6 | 0 | 0
1543 | 354.4 | 48.5 | 150.8895 | 150.8895 | 0 | 0 | 0 | 209.147 | 0 | 0
1544 | 442.969 | 277.11 | 1231.6848 | 460.1583 | -614.9724 | 0 | 156.5541 | 0 | 0 | 0
1545 | 1680.912 | 294.74 | 1316.551 | 1316.551 | 0 | 0 | 0 | 0 | 0 | 429.5884
1546 | 1829.403 | 418.69 | 1832.2989 | 1832.2989 | 0 | 0 | 0 | 0 | 0 | 68.0937
1547 | 1851.263 | 556.09 | 2393.4789 | 1923.1008 | -470.3781 | 0 | 0 | 0 | 0 | 0
1548 | 1924.839 | 742.64 | 3140.0793 | 1999.5309 | -506.5274 | 0 | 634.021 | 0 | 0 | 0
1549 | 1677.954 | 435.71 | 1852.7789 | 1743.0666 | 0 | 0 | 109.7123 | 0 | 0 | 0
1550 | 1718.738 | 171.19 | 712.2876 | 712.2876 | 0 | 0 | 0 | 1007.762 | 0 | 26.2766
1551 | 1907.596 | 428.38 | 1857.2447 | 1857.2447 | 0 | 0 | 0 | 0 | 0 | 124.3751
1552 | 1688.519 | 432.42 | 1921.7015 | 1754.0416 | -167.66 | 0 | 0 | 0 | 0 | 0
1553 | 2091.005 | 296.29 | 1317.5088 | 1317.5088 | 0 | 0 | 0 | 822.712 | 0 | 0
1554 | 1608.296 | 63.85 | 230.8889 | 230.8889 | 0 | 0 | 0 | 1386.032 | 0 | 0
1555 | 1773.255 | 0 | 0 | 0 | 0 | 0 | 0 | 1773.255 | 0 | 0
1556 | 1601.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1601.6 | 0 | 0
1557 | 1201.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1201.6 | 0 | 0
1558 | 1380.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1074.926 | 0 | 317.7434
1559 | 1320.8 | 0 | 0 | 0 | 0 | 0 | 0 | 728.8 | 0 | 614.9724
1560 | 361.6 | 0 | 0 | 0 | 0 | 0 | 0 | 361.6 | 0 | 0
1561 | 110.4 | 0 | 0 | 0 | 0 | 0 | 0 | 110.4 | 0 | 0
1562 | 116.8 | 0 | 0 | 0 | 0 | 0 | 0 | 116.8 | 0 | 0
1563 | 111.2 | 0 | 0 | 0 | 0 | 0 | 0 | 111.2 | 0 | 0
1564 | 113.6 | 0 | 0 | 0 | 0 | 0 | 0 | 113.6 | 0 | 0
1565 | 110.4 | 0 | 0 | 0 | 0 | 0 | 0 | 110.4 | 0 | 0
1566 | 114.4 | 0 | 0 | 0 | 0 | 0 | 0 | 114.4 | 0 | 0
1567 | 98.4 | 44.29 | 138.3169 | 102.2184 | -36.0985 | 0 | 0 | 0 | 0 | 0
1568 | 220.236 | 267.1 | 1171.8175 | 228.7822 | -614.9724 | 0 | 328.0628 | 0 | 0 | 0
1569 | 1212.985 | 512.7 | 2269.3729 | 1260.0546 | -386.9402 | 0 | 622.3781 | 0 | 0 | 0
1570 | 1238.812 | 727.34 | 3080.2181 | 1286.8838 | 0 | 0 | 1793.3343 | 0 | 0 | 0
1571 | 1664.717 | 783.38 | 3219.4637 | 1729.3159 | 0 | 0 | 1490.1478 | 0 | 0 | 0
1572 | 1556.917 | 859.52 | 3434.4017 | 1617.3328 | 0 | 0 | 1817.069 | 0 | 0 | 0
1573 | 1408.483 | 853.19 | 3378.8932 | 1463.1388 | 0 | 0 | 1915.7544 | 0 | 0 | 0
1574 | 1587.586 | 741.62 | 3007.9194 | 1649.1919 | 0 | 0 | 1358.7275 | 0 | 0 | 0
1575 | 1726.378 | 628.86 | 2651.4234 | 1793.3697 | 0 | 0 | 858.0538 | 0 | 0 | 0
1576 | 1711.478 | 456.89 | 2000.7359 | 1777.8915 | 0 | 0 | 222.8444 | 0 | 0 | 0
1577 | 1544.327 | 230.59 | 1009.1417 | 1009.1417 | 0 | 0 | 0 | 572.882 | 0 | 0
1578 | 1402.659 | 57.95 | 204.388 | 204.388 | 0 | 0 | 0 | 1205.906 | 0 | 0
1579 | 1439.865 | 0 | 0 | 0 | 0 | 0 | 0 | 1439.865 | 0 | 0
1580 | 1459.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1459.2 | 0 | 0
1581 | 1510.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1510.4 | 0 | 0
1582 | 1384 | 0 | 0 | 0 | 0 | 0 | 0 | 1078.126 | 0 | 317.7434
1583 | 1400 | 0 | 0 | 0 | 0 | 0 | 0 | 808 | 0 | 614.9724
1584 | 472 | 0 | 0 | 0 | 0 | 0 | 0 | 472 | 0 | 0
1585 | 416.8 | 0 | 0 | 0 | 0 | 0 | 0 | 416.8 | 0 | 0
1586 | 390.4 | 0 | 0 | 0 | 0 | 0 | 0 | 390.4 | 0 | 0
1587 | 431.2 | 0 | 0 | 0 | 0 | 0 | 0 | 431.2 | 0 | 0
1588 | 381.6 | 0 | 0 | 0 | 0 | 0 | 0 | 381.6 | 0 | 0
1589 | 384 | 0 | 0 | 0 | 0 | 0 | 0 | 384 | 0 | 0
1590 | 484.8 | 0 | 0 | 0 | 0 | 0 | 0 | 484.8 | 0 | 0
1591 | 424 | 41.62 | 130.1674 | 130.1674 | 0 | 0 | 0 | 298.695 | 0 | 0
1592 | 433.137 | 261.43 | 1146.8903 | 449.9448 | -614.9724 | 0 | 81.9731 | 0 | 0 | 0
1593 | 1644.823 | 505.61 | 2218.4538 | 1708.6499 | -423.0387 | 0 | 86.7651 | 0 | 0 | 0
1594 | 1786.904 | 713.87 | 2962.9433 | 1856.2444 | 0 | 0 | 1106.6989 | 0 | 0 | 0
1595 | 1792.2 | 849.2 | 3400.5917 | 1861.7459 | 0 | 0 | 1538.8459 | 0 | 0 | 0
1596 | 1606.691 | 938.82 | 3694.2868 | 1669.0382 | 0 | 0 | 2025.2485 | 0 | 0 | 0
1597 | 1894.24 | 951.03 | 3731.7814 | 1967.7455 | 0 | 0 | 1764.0359 | 0 | 0 | 0
1598 | 1829.242 | 828.76 | 3334.6152 | 1900.2253 | 0 | 0 | 1434.3899 | 0 | 0 | 0
1599 | 1903.518 | 737.68 | 3046.6917 | 1977.3835 | 0 | 0 | 1069.3082 | 0 | 0 | 0
1600 | 1476.616 | 530.46 | 2281.13 | 1533.9157 | 0 | 0 | 747.2143 | 0 | 0 | 0
1601 | 1535.769 | 288.12 | 1247.6232 | 1247.6232 | 0 | 0 | 0 | 334.751 | 0 | 0
1602 | 1485.795 | 62.78 | 217.1621 | 217.1621 | 0 | 0 | 0 | 1276.745 | 0 | 0
1603 | 1357.077 | 0 | 0 | 0 | 0 | 0 | 0 | 1357.077 | 0 | 0
1604 | 1589.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1589.6 | 0 | 0
1605 | 1525.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1525.6 | 0 | 0
1606 | 1258.4 | 0 | 0 | 0 | 0 | 0 | 0 | 952.526 | 0 | 317.7434
1607 | 1140 | 0 | 0 | 0 | 0 | 0 | 0 | 548 | 0 | 614.9724
1608 | 1290.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1290.4 | 0 | 0
1609 | 1470.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1470.4 | 0 | 0
1610 | 904.8 | 0 | 0 | 0 | 0 | 0 | 0 | 904.8 | 0 | 0
1611 | 1167.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1167.2 | 0 | 0
1612 | 1140.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1140.8 | 0 | 0
1613 | 1201.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1201.6 | 0 | 0
1614 | 1211.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1211.2 | 0 | 0
1615 | 1014.4 | 38.37 | 122.7628 | 122.7628 | 0 | 0 | 0 | 896.223 | 0 | 0
1616 | 337.397 | 254.93 | 1126.1734 | 350.4896 | -614.9724 | 0 | 160.7114 | 0 | 0 | 0
1617 | 274.291 | 498.77 | 2208.8905 | 284.9348 | -423.0387 | 0 | 1500.917 | 0 | 0 | 0
1618 | 264.437 | 708.02 | 3010.0666 | 274.6984 | 0 | 0 | 2735.3682 | 0 | 0 | 0
1619 | 281.379 | 858.28 | 3521.7455 | 292.2978 | 0 | 0 | 3229.4476 | 0 | 0 | 0
1620 | 297.305 | 945.55 | 3801.0583 | 308.8418 | 0 | 0 | 3492.2164 | 0 | 0 | 0
1621 | 288.999 | 876.2 | 3546.04 | 300.2135 | 0 | 0 | 3245.8265 | 0 | 0 | 0
1622 | 276.252 | 666.32 | 2765.0261 | 286.9719 | 0 | 0 | 2478.0542 | 0 | 0 | 0
1623 | 267.096 | 316.18 | 1337.3209 | 277.4606 | 0 | 0 | 1059.8603 | 0 | 0 | 0
1624 | 204.599 | 300.06 | 1298.7023 | 212.5384 | 0 | 0 | 1086.1639 | 0 | 0 | 0
1625 | 286.349 | 213.92 | 925.9906 | 297.4607 | 0 | 0 | 628.5299 | 0 | 0 | 0
1626 | 229.93 | 52.13 | 179.5553 | 179.5553 | 0 | 0 | 0 | 57.082 | 0 | 0
1627 | 205.13 | 0 | 0 | 0 | 0 | 0 | 0 | 205.13 | 0 | 0
1628 | 299.2 | 0 | 0 | 0 | 0 | 0 | 0 | 299.2 | 0 | 0
1629 | 287.2 | 0 | 0 | 0 | 0 | 0 | 0 | 76.526 | 0 | 218.8492
1630 | 292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303.331
1631 | 230.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239.3406
1632 | 164.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 171.195
1633 | 195.2 | 0 | 0 | 0 | 0 | 0 | 0 | 195.2 | 0 | 0
1634 | 238.4 | 0 | 0 | 0 | 0 | 0 | 0 | 238.4 | 0 | 0
1635 | 187.2 | 0 | 0 | 0 | 0 | 0 | 0 | 187.2 | 0 | 0
1636 | 148.8 | 0 | 0 | 0 | 0 | 0 | 0 | 148.8 | 0 | 0
1637 | 132.8 | 0 | 0 | 0 | 0 | 0 | 0 | 132.8 | 0 | 0
1638 | 192.8 | 0 | 0 | 0 | 0 | 0 | 0 | 192.8 | 0 | 0
1639 | 120 | 42.19 | 133.3077 | 124.6566 | -8.6512 | 0 | 0 | 0 | 0 | 0
1640 | 191.45 | 262.62 | 1158.3868 | 198.8792 | -614.9724 | 0 | 344.5352 | 0 | 0 | 0
1641 | 866.164 | 508.37 | 2242.7192 | 899.7763 | -414.3875 | 0 | 928.5554 | 0 | 0 | 0
1642 | 1455.515 | 722.12 | 3037.034 | 1511.9959 | 0 | 0 | 1525.0381 | 0 | 0 | 0
1643 | 1743.462 | 881.33 | 3556.881 | 1811.1166 | 0 | 0 | 1745.7644 | 0 | 0 | 0
1644 | 1648.641 | 969.33 | 3809.4798 | 1712.6161 | 0 | 0 | 2096.8637 | 0 | 0 | 0
1645 | 1680.833 | 974.64 | 3813.8085 | 1746.0573 | 0 | 0 | 2067.7512 | 0 | 0 | 0
1646 | 1635.438 | 895.83 | 3581.0571 | 1698.9008 | 0 | 0 | 1882.1563 | 0 | 0 | 0
1647 | 1660.537 | 741.54 | 3074.8953 | 1724.9737 | 0 | 0 | 1349.9216 | 0 | 0 | 0
1648 | 1717.571 | 535.72 | 2319.3404 | 1784.2209 | 0 | 0 | 535.1195 | 0 | 0 | 0
1649 | 1588.152 | 291.88 | 1273.2786 | 1273.2786 | 0 | 0 | 0 | 362.437 | 0 | 0
1650 | 1863.569 | 64.09 | 224.868 | 224.868 | 0 | 0 | 0 | 1647.101 | 0 | 0
1651 | 1540.524 | 0 | 0 | 0 | 0 | 0 | 0 | 1540.524 | 0 | 0
1652 | 1230.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1230.4 | 0 | 0
1653 | 1436 | 0 | 0 | 0 | 0 | 0 | 0 | 1436 | 0 | 0
1654 | 1564.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1258.926 | 0 | 317.7434
1655 | 1647.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1055.2 | 0 | 614.9724
1656 | 1421.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1421.6 | 0 | 0
1657 | 1376.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1376.8 | 0 | 0
1658 | 1502.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1502.4 | 0 | 0
1659 | 1624 | 0 | 0 | 0 | 0 | 0 | 0 | 1624 | 0 | 0
1660 | 1292.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1292.8 | 0 | 0
1661 | 1245.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1245.6 | 0 | 0
1662 | 1281.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1281.6 | 0 | 0
1663 | 1044.8 | 28.68 | 85.7409 | 85.7409 | 0 | 0 | 0 | 962.262 | 0 | 0
1664 | 1268.07 | 248.83 | 1109.8039 | 1109.8039 | 0 | 0 | 0 | 199.723 | 0 | 0
1665 | 1664.469 | 434.67 | 1959.9233 | 1729.0583 | -230.865 | 0 | 0 | 0 | 0 | 0
1666 | 1354.034 | 703.1 | 3077.5328 | 1406.5769 | -614.9724 | 0 | 1055.9835 | 0 | 0 | 0
1667 | 1675.929 | 325.75 | 1405.107 | 1405.107 | 0 | 0 | 0 | 0 | 0 | 335.856
1668 | 1404.339 | 939.84 | 3972.4932 | 1458.834 | -565.945 | 0 | 1947.7142 | 0 | 0 | 0
1669 | 1405.495 | 956.67 | 4051.6107 | 1460.0349 | 0 | 0 | 2591.5758 | 0 | 0 | 0
1670 | 1385.337 | 810.84 | 3486.4334 | 1439.0947 | 0 | 0 | 2047.3387 | 0 | 0 | 0
1671 | 1426.323 | 758.6 | 3325.3885 | 1481.6711 | 0 | 0 | 1843.7174 | 0 | 0 | 0
1672 | 1546.268 | 554.91 | 2503.4613 | 1606.2705 | 0 | 0 | 897.1907 | 0 | 0 | 0
1673 | 1512.557 | 315.26 | 1409.176 | 1409.176 | 0 | 0 | 0 | 156.021 | 0 | 0
1674 | 1715.266 | 79.85 | 278.7799 | 278.7799 | 0 | 0 | 0 | 1446.9 | 0 | 0
1675 | 1546.02 | 0 | 0 | 0 | 0 | 0 | 0 | 1546.02 | 0 | 0
1676 | 1220 | 0 | 0 | 0 | 0 | 0 | 0 | 1220 | 0 | 0
1677 | 1550.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1550.4 | 0 | 0
1678 | 1778.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1472.526 | 0 | 317.7434
1679 | 1676.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1084.8 | 0 | 614.9724
1680 | 1480.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1480.8 | 0 | 0
1681 | 1334.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1334.4 | 0 | 0
1682 | 1472 | 0 | 0 | 0 | 0 | 0 | 0 | 1472 | 0 | 0
1683 | 1444.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1444.8 | 0 | 0
1684 | 230.4 | 0 | 0 | 0 | 0 | 0 | 0 | 230.4 | 0 | 0
1685 | 354.4 | 0 | 0 | 0 | 0 | 0 | 0 | 354.4 | 0 | 0
1686 | 880.8 | 0 | 0 | 0 | 0 | 0 | 0 | 880.8 | 0 | 0
1687 | 1391.249 | 57.95 | 188.4205 | 188.4205 | 0 | 0 | 0 | 1209.867 | 0 | 0
1688 | 1367.166 | 290.94 | 1291.5937 | 1291.5937 | 0 | 0 | 0 | 123.82 | 0 | 0
1689 | 1114.978 | 544.83 | 2462.684 | 1158.2444 | -614.9724 | 0 | 689.4672 | 0 | 0 | 0
1690 | 991.078 | 769.84 | 3350.2689 | 1029.5365 | -423.0387 | 0 | 1897.6937 | 0 | 0 | 0
1691 | 1722.516 | 935.81 | 3930.8756 | 1789.3578 | 0 | 0 | 2141.5178 | 0 | 0 | 0
1692 | 1259.699 | 1025.3 | 4212.8789 | 1308.5813 | 0 | 0 | 2904.2976 | 0 | 0 | 0
1693 | 1018.275 | 1030.87 | 4219.4088 | 1057.7889 | 0 | 0 | 3161.6199 | 0 | 0 | 0
1694 | 905.101 | 923.13 | 3847.4648 | 940.2232 | 0 | 0 | 2907.2416 | 0 | 0 | 0
1695 | 1153.41 | 803.51 | 3443.2368 | 1198.1678 | 0 | 0 | 2245.069 | 0 | 0 | 0
1696 | 1638.025 | 588.8 | 2617.146 | 1701.5881 | 0 | 0 | 915.5578 | 0 | 0 | 0
1697 | 1603.774 | 336.68 | 1485.8513 | 1485.8513 | 0 | 0 | 0 | 173.427 | 0 | 0
1698 | 1509.175 | 89.24 | 297.7931 | 297.7931 | 0 | 0 | 0 | 1222.506 | 0 | 0
1699 | 994.822 | 0 | 0 | 0 | 0 | 0 | 0 | 994.822 | 0 | 0
1700 | 1233.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1233.6 | 0 | 0
1701 | 1465.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1465.6 | 0 | 0
1702 | 1463.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1157.326 | 0 | 317.7434
1703 | 1261.6 | 0 | 0 | 0 | 0 | 0 | 0 | 669.6 | 0 | 614.9724
1704 | 1423.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1423.2 | 0 | 0
1705 | 1556.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1556.8 | 0 | 0
1706 | 1232.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1232.8 | 0 | 0
1707 | 1564 | 0 | 0 | 0 | 0 | 0 | 0 | 1564 | 0 | 0
1708 | 1275.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.2 | 0 | 0
1709 | 1312.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1312.8 | 0 | 0
1710 | 1168 | 0 | 0 | 0 | 0 | 0 | 0 | 1168 | 0 | 0
1711 | 1272.8 | 65.14 | 206.9195 | 206.9195 | 0 | 0 | 0 | 1073.61 | 0 | 0
1712 | 922.415 | 304.54 | 1346.2276 | 958.2091 | -388.0185 | 0 | 0 | 0 | 0 | 0
1713 | 1110.192 | 559.02 | 2516.33 | 1153.2727 | -614.9724 | 0 | 748.0849 | 0 | 0 | 0
1714 | 1567.16 | 769.48 | 3331.4094 | 1627.9732 | -35.0202 | 0 | 1668.416 | 0 | 0 | 0
1715 | 1212.443 | 916.93 | 3827.7888 | 1259.4915 | 0 | 0 | 2568.2972 | 0 | 0 | 0
1716 | 1091.61 | 1001.3 | 4087.5679 | 1133.9697 | 0 | 0 | 2953.5982 | 0 | 0 | 0
1717 | 971.536 | 1004.36 | 4108.1954 | 1009.2362 | 0 | 0 | 3098.9592 | 0 | 0 | 0
1718 | 1055.456 | 809.98 | 3401.402 | 1096.4127 | 0 | 0 | 2304.9893 | 0 | 0 | 0
1719 | 957.674 | 779.29 | 3347.407 | 994.8363 | 0 | 0 | 2352.5707 | 0 | 0 | 0
1720 | 997.558 | 568.54 | 2529.394 | 1036.268 | 0 | 0 | 1493.126 | 0 | 0 | 0
1721 | 1166.299 | 321.19 | 1421.6604 | 1211.5569 | 0 | 0 | 210.1035 | 0 | 0 | 0
1722 | 1040.947 | 82.11 | 282.4822 | 282.4822 | 0 | 0 | 0 | 769.017 | 0 | 0
1723 | 1287.915 | 0 | 0 | 0 | 0 | 0 | 0 | 1287.915 | 0 | 0
1724 | 1227.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1227.2 | 0 | 0
1725 | 1147.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1147.2 | 0 | 0
1726 | 1378.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1072.526 | 0 | 317.7434
1727 | 1175.2 | 0 | 0 | 0 | 0 | 0 | 0 | 583.2 | 0 | 614.9724
1728 | 160.8 | 0 | 0 | 0 | 0 | 0 | 0 | 160.8 | 0 | 0
1729 | 104.8 | 0 | 0 | 0 | 0 | 0 | 0 | 104.8 | 0 | 0
1730 | 106.4 | 0 | 0 | 0 | 0 | 0 | 0 | 106.4 | 0 | 0
1731 | 102.4 | 0 | 0 | 0 | 0 | 0 | 0 | 102.4 | 0 | 0
1732 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 0 | 0
1733 | 101.6 | 0 | 0 | 0 | 0 | 0 | 0 | 101.6 | 0 | 0
1734 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 0
1735 | 86.785 | 69.55 | 219.4267 | 90.1527 | -129.2741 | 0 | 0 | 0 | 0 | 0
1736 | 102.491 | 313.03 | 1387.6489 | 106.4681 | -614.9724 | 0 | 666.2083 | 0 | 0 | 0
1737 | 1053.719 | 570.49 | 2575.145 | 1094.6083 | -293.7646 | 0 | 1186.7721 | 0 | 0 | 0
1738 | 1351.25 | 792.48 | 3442.9885 | 1403.6849 | 0 | 0 | 2039.3036 | 0 | 0 | 0
1739 | 1014.359 | 951.51 | 4003.0746 | 1053.7209 | 0 | 0 | 2949.3537 | 0 | 0 | 0
1740 | 1130.671 | 584.14 | 2479.3205 | 1174.5464 | 0 | 0 | 1304.7741 | 0 | 0 | 0
1741 | 1327.615 | 711.91 | 2993.7678 | 1379.1328 | 0 | 0 | 1614.635 | 0 | 0 | 0
1742 | 1312.509 | 960.03 | 4036.6062 | 1363.4406 | 0 | 0 | 2673.1656 | 0 | 0 | 0
1743 | 1182.509 | 808.98 | 3501.5438 | 1228.396 | 0 | 0 | 2273.1479 | 0 | 0 | 0
1744 | 1270.68 | 593.39 | 2659.8575 | 1319.9884 | 0 | 0 | 1339.8691 | 0 | 0 | 0
1745 | 1403.753 | 339.53 | 1508.8213 | 1458.2253 | 0 | 0 | 50.596 | 0 | 0 | 0
1746 | 1739.825 | 90.05 | 301.029 | 301.029 | 0 | 0 | 0 | 1450.041 | 0 | 0
1747 | 1588.775 | 0 | 0 | 0 | 0 | 0 | 0 | 1588.775 | 0 | 0
1748 | 1500.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1500.8 | 0 | 0
1749 | 1536 | 0 | 0 | 0 | 0 | 0 | 0 | 1536 | 0 | 0
1750 | 1589.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1283.726 | 0 | 317.7434
1751 | 1916 | 0 | 0 | 0 | 0 | 0 | 0 | 1324 | 0 | 614.9724
1752 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 0 | 0
1753 | 107.2 | 0 | 0 | 0 | 0 | 0 | 0 | 107.2 | 0 | 0
1754 | 116 | 0 | 0 | 0 | 0 | 0 | 0 | 116 | 0 | 0
1755 | 110.4 | 0 | 0 | 0 | 0 | 0 | 0 | 110.4 | 0 | 0
1756 | 110.4 | 0 | 0 | 0 | 0 | 0 | 0 | 110.4 | 0 | 0
1757 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 108 | 0 | 0
1758 | 110.4 | 0 | 0 | 0 | 0 | 0 | 0 | 110.4 | 0 | 0
1759 | 103.221 | 74.32 | 230.2615 | 107.2265 | -123.035 | 0 | 0 | 0 | 0 | 0
1760 | 126.773 | 324.47 | 1445.6121 | 131.6924 | -614.9724 | 0 | 698.9473 | 0 | 0 | 0
1761 | 999.966 | 574.05 | 2619.4293 | 1038.7694 | -300.0037 | 0 | 1280.6562 | 0 | 0 | 0
1762 | 1972.895 | 799.4 | 3525.2525 | 2049.4527 | 0 | 0 | 1475.7998 | 0 | 0 | 0
1763 | 1497.263 | 951.9 | 4074.3023 | 1555.3639 | 0 | 0 | 2518.9384 | 0 | 0 | 0
1764 | 1447.357 | 976.32 | 4114.6474 | 1503.5213 | 0 | 0 | 2611.1261 | 0 | 0 | 0
1765 | 1492.397 | 1037.67 | 4350.1081 | 1550.3091 | 0 | 0 | 2799.799 | 0 | 0 | 0
1766 | 1665.983 | 946.85 | 4015.3221 | 1730.6311 | 0 | 0 | 2284.6911 | 0 | 0 | 0
1767 | 1335.156 | 779.82 | 3382.6838 | 1386.9664 | 0 | 0 | 1995.7174 | 0 | 0 | 0
1768 | 1587.901 | 568.67 | 2544.2738 | 1649.5191 | 0 | 0 | 894.7547 | 0 | 0 | 0
1769 | 1409.122 | 313.01 | 1388.643 | 1388.643 | 0 | 0 | 0 | 72.352 | 0 | 0
1770 | 1956.792 | 74.87 | 264.5628 | 264.5628 | 0 | 0 | 0 | 1702.112 | 0 | 0
1771 | 1705.486 | 0 | 0 | 0 | 0 | 0 | 0 | 1705.486 | 0 | 0
1772 | 1647.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1647.2 | 0 | 0
1773 | 1580.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1580.8 | 0 | 0
1774 | 1783.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1477.326 | 0 | 317.7434
1775 | 1466.4 | 0 | 0 | 0 | 0 | 0 | 0 | 874.4 | 0 | 614.9724
1776 | 1642.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1642.4 | 0 | 0
1777 | 1504 | 0 | 0 | 0 | 0 | 0 | 0 | 1504 | 0 | 0
1778 | 1396 | 0 | 0 | 0 | 0 | 0 | 0 | 1396 | 0 | 0
1779 | 1258.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1258.4 | 0 | 0
1780 | 1348.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1348.8 | 0 | 0
1781 | 1135.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1135.2 | 0 | 0
1782 | 1196.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1196.8 | 0 | 0
1783 | 1208.997 | 59.67 | 200.5319 | 200.5319 | 0 | 0 | 0 | 1015.956 | 0 | 0
1784 | 230.659 | 295.75 | 1316.3381 | 239.6097 | -614.9724 | 0 | 461.756 | 0 | 0 | 0
1785 | 288.152 | 529.96 | 2387.4933 | 299.3337 | -423.0387 | 0 | 1665.1209 | 0 | 0 | 0
1786 | 332.224 | 764.06 | 3313.0174 | 345.1159 | 0 | 0 | 2967.9015 | 0 | 0 | 0
1787 | 287.755 | 922.48 | 3885.6814 | 298.9213 | 0 | 0 | 3586.7601 | 0 | 0 | 0
1788 | 233.034 | 1008.35 | 4187.7564 | 242.0768 | 0 | 0 | 3945.6796 | 0 | 0 | 0
1789 | 257.376 | 1007.76 | 4189.7499 | 267.3634 | 0 | 0 | 3922.3865 | 0 | 0 | 0
1790 | 254.785 | 920.68 | 3891.6368 | 264.6719 | 0 | 0 | 3626.965 | 0 | 0 | 0
1791 | 276.33 | 769.08 | 3334.8219 | 287.0529 | 0 | 0 | 3047.769 | 0 | 0 | 0
1792 | 204.693 | 553.91 | 2473.4357 | 212.6361 | 0 | 0 | 2260.7996 | 0 | 0 | 0
1793 | 301.357 | 286.02 | 1266.4598 | 313.0511 | 0 | 0 | 953.4088 | 0 | 0 | 0
1794 | 228.211 | 70.33 | 249.3994 | 237.0667 | 0 | 0 | 12.3327 | 0 | 0 | 0
1795 | 216.305 | 0 | 0 | 0 | 0 | 0 | 0 | 216.305 | 0 | 0
1796 | 242.4 | 0 | 0 | 0 | 0 | 0 | 0 | 242.4 | 0 | 0
1797 | 200.8 | 0 | 0 | 0 | 0 | 0 | 0 | 158.126 | 0 | 44.33
1798 | 296 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307.4862
1799 | 268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278.3997
1800 | 291.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 302.4999
1801 | 237.6 | 0 | 0 | 0 | 0 | 0 | 0 | 237.6 | 0 | 0
1802 | 191.2 | 0 | 0 | 0 | 0 | 0 | 0 | 191.2 | 0 | 0
1803 | 243.2 | 0 | 0 | 0 | 0 | 0 | 0 | 243.2 | 0 | 0
1804 | 204 | 0 | 0 | 0 | 0 | 0 | 0 | 204 | 0 | 0
1805 | 236 | 0 | 0 | 0 | 0 | 0 | 0 | 236 | 0 | 0
1806 | 293.6 | 0 | 0 | 0 | 0 | 0 | 0 | 293.6 | 0 | 0
1807 | 169.6 | 63.27 | 208.4029 | 176.1813 | -32.2216 | 0 | 0 | 0 | 0 | 0
1808 | 205.306 | 309.06 | 1373.1004 | 213.2728 | -614.9724 | 0 | 544.8552 | 0 | 0 | 0
1809 | 1200.592 | 567.37 | 2568.9652 | 1247.1807 | -390.817 | 0 | 930.9675 | 0 | 0 | 0
1810 | 1832.064 | 637.16 | 2787.6824 | 1903.1568 | 0 | 0 | 884.5256 | 0 | 0 | 0
1811 | 1718.381 | 926.37 | 3940.1376 | 1785.0623 | 0 | 0 | 2155.0752 | 0 | 0 | 0
1812 | 1345.557 | 1010.3 | 4219.0421 | 1397.771 | 0 | 0 | 2821.2711 | 0 | 0 | 0
1813 | 1408.003 | 999.85 | 4165.981 | 1462.6402 | 0 | 0 | 2703.3408 | 0 | 0 | 0
1814 | 1247.32 | 771.27 | 3271.0808 | 1295.7219 | 0 | 0 | 1975.3589 | 0 | 0 | 0
1815 | 1222.285 | 654.14 | 2833.5747 | 1269.7155 | 0 | 0 | 1563.8593 | 0 | 0 | 0
1816 | 1327.605 | 532.35 | 2369.3911 | 1379.1224 | 0 | 0 | 990.2687 | 0 | 0 | 0
1817 | 1517.328 | 312.76 | 1382.4216 | 1382.4216 | 0 | 0 | 0 | 186.547 | 0 | 0
1818 | 1493.831 | 75.92 | 265.9704 | 265.9704 | 0 | 0 | 0 | 1237.796 | 0 | 0
1819 | 1418.435 | 0 | 0 | 0 | 0 | 0 | 0 | 1418.435 | 0 | 0
1820 | 1030.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1030.4 | 0 | 0
1821 | 1524 | 0 | 0 | 0 | 0 | 0 | 0 | 1524 | 0 | 0
1822 | 1386.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1080.526 | 0 | 317.7434
1823 | 1324 | 0 | 0 | 0 | 0 | 0 | 0 | 732 | 0 | 614.9724
1824 | 1220 | 0 | 0 | 0 | 0 | 0 | 0 | 1220 | 0 | 0
1825 | 1348.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1348.8 | 0 | 0
1826 | 1544.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1544.8 | 0 | 0
1827 | 1356 | 0 | 0 | 0 | 0 | 0 | 0 | 1356 | 0 | 0
1828 | 1223.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1223.2 | 0 | 0
1829 | 995.2 | 0 | 0 | 0 | 0 | 0 | 0 | 995.2 | 0 | 0
1830 | 1268 | 0 | 0 | 0 | 0 | 0 | 0 | 1268 | 0 | 0
1831 | 1071.282 | 59.74 | 206.6702 | 206.6702 | 0 | 0 | 0 | 872.332 | 0 | 0
1832 | 1080.559 | 282.66 | 1261.2492 | 1122.4898 | -138.7594 | 0 | 0 | 0 | 0 | 0
1833 | 1433.37 | 535.52 | 2407.9972 | 1488.9916 | -614.9724 | 0 | 304.0332 | 0 | 0 | 0
1834 | 1536.183 | 756.16 | 3263.9006 | 1595.7942 | -284.2793 | 0 | 1383.8271 | 0 | 0 | 0
1835 | 1523.623 | 904.66 | 3761.2388 | 1582.7468 | 0 | 0 | 2178.492 | 0 | 0 | 0
1836 | 1417.562 | 974.9 | 3965.7867 | 1472.5701 | 0 | 0 | 2493.2166 | 0 | 0 | 0
1837 | 1857.995 | 991.16 | 4016.0254 | 1930.094 | 0 | 0 | 2085.9314 | 0 | 0 | 0
1838 | 1821.112 | 654.07 | 2745.2015 | 1891.7798 | 0 | 0 | 853.4217 | 0 | 0 | 0
1839 | 2055.08 | 680.85 | 2911.7874 | 2134.8269 | 0 | 0 | 776.9605 | 0 | 0 | 0
1840 | 1685.353 | 531.67 | 2353.5005 | 1750.7527 | 0 | 0 | 602.7478 | 0 | 0 | 0
1841 | 1935.979 | 298.41 | 1320.0694 | 1320.0694 | 0 | 0 | 0 | 665.221 | 0 | 0
1842 | 1652.92 | 69.09 | 247.5129 | 247.5129 | 0 | 0 | 0 | 1414.653 | 0 | 0
1843 | 1211.742 | 0 | 0 | 0 | 0 | 0 | 0 | 1211.742 | 0 | 0
1844 | 1214.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1214.4 | 0 | 0
1845 | 1048 | 0 | 0 | 0 | 0 | 0 | 0 | 1048 | 0 | 0
1846 | 1320.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1014.926 | 0 | 317.7434
1847 | 1692 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 614.9724
1848 | 1456.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1456.8 | 0 | 0
1849 | 1660.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1660.8 | 0 | 0
1850 | 1558.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1558.4 | 0 | 0
1851 | 1351.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1351.2 | 0 | 0
1852 | 954.4 | 0 | 0 | 0 | 0 | 0 | 0 | 954.4 | 0 | 0
1853 | 1149.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1149.6 | 0 | 0
1854 | 950.4 | 0 | 0 | 0 | 0 | 0 | 0 | 950.4 | 0 | 0
1855 | 1003.501 | 44.82 | 157.2948 | 157.2948 | 0 | 0 | 0 | 852.082 | 0 | 0
1856 | 1142.233 | 297.05 | 1327.9062 | 1186.5571 | -141.3491 | 0 | 0 | 0 | 0 | 0
1857 | 1496.27 | 521.14 | 2356.2855 | 1554.3324 | -614.9724 | 0 | 186.9807 | 0 | 0 | 0
1858 | 1685.004 | 690.23 | 3027.7969 | 1750.3912 | -281.6896 | 0 | 995.7162 | 0 | 0 | 0
1859 | 1751.14 | 951.85 | 4048.9316 | 1819.0925 | 0 | 0 | 2229.8391 | 0 | 0 | 0
1860 | 1623.245 | 1036.65 | 4344.2233 | 1686.2346 | 0 | 0 | 2657.9887 | 0 | 0 | 0
1861 | 1835.131 | 1042.22 | 4362.6984 | 1906.3428 | 0 | 0 | 2456.3556 | 0 | 0 | 0
1862 | 1759.08 | 874.6 | 3721.3019 | 1827.3407 | 0 | 0 | 1893.9613 | 0 | 0 | 0
1863 | 1738.997 | 809.89 | 3521.9886 | 1806.4783 | 0 | 0 | 1715.5102 | 0 | 0 | 0
1864 | 1558.583 | 592.86 | 2662.3465 | 1619.0634 | 0 | 0 | 1043.283 | 0 | 0 | 0
1865 | 1589.517 | 336.2 | 1491.8483 | 1491.8483 | 0 | 0 | 0 | 153.397 | 0 | 0
1866 | 1636.574 | 87.84 | 294.5707 | 294.5707 | 0 | 0 | 0 | 1353.007 | 0 | 0
1867 | 1446.081 | 0 | 0 | 0 | 0 | 0 | 0 | 1446.081 | 0 | 0
1868 | 1508 | 0 | 0 | 0 | 0 | 0 | 0 | 1508 | 0 | 0
1869 | 1304 | 0 | 0 | 0 | 0 | 0 | 0 | 1304 | 0 | 0
1870 | 1274.4 | 0 | 0 | 0 | 0 | 0 | 0 | 968.526 | 0 | 317.7434
1871 | 1512.8 | 0 | 0 | 0 | 0 | 0 | 0 | 920.8 | 0 | 614.9724
1872 | 1444 | 0 | 0 | 0 | 0 | 0 | 0 | 1444 | 0 | 0
1873 | 1532 | 0 | 0 | 0 | 0 | 0 | 0 | 1532 | 0 | 0
1874 | 1208.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1208.8 | 0 | 0
1875 | 1256.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1256.8 | 0 | 0
1876 | 1124 | 0 | 0 | 0 | 0 | 0 | 0 | 1124 | 0 | 0
1877 | 1070.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1070.4 | 0 | 0
1878 | 1064 | 0 | 0 | 0 | 0 | 0 | 0 | 1064 | 0 | 0
1879 | 1158.633 | 74.71 | 250.381 | 250.381 | 0 | 0 | 0 | 917.605 | 0 | 0
1880 | 1337.607 | 290 | 1294.6811 | 1294.6811 | 0 | 0 | 0 | 91.289 | 0 | 0
1881 | 1602.436 | 478.16 | 2159.4382 | 1664.6181 | -494.8201 | 0 | 0 | 0 | 0 | 0
1882 | 1659.929 | 693.22 | 3046.0176 | 1724.3421 | -543.191 | 0 | 778.4844 | 0 | 0 | 0
1883 | 0 | 814.36 | 3498.1958 | 0 | 0 | 0 | 3498.1958 | 0 | 0 | 0
1884 | 1537.528 | 1054.68 | 4458.6061 | 1597.1914 | 0 | 0 | 2861.4147 | 0 | 0 | 0
1885 | 1283.8 | 1042.49 | 4404.5342 | 1333.6175 | 0 | 0 | 3070.9167 | 0 | 0 | 0
1886 | 1608.326 | 926.54 | 3969.5482 | 1670.7367 | 0 | 0 | 2298.8115 | 0 | 0 | 0
1887 | 1597.92 | 716.22 | 3135.9936 | 1659.9269 | 0 | 0 | 1476.0668 | 0 | 0 | 0
1888 | 1735.168 | 604.39 | 2725.9639 | 1802.5008 | 0 | 0 | 923.4631 | 0 | 0 | 0
1889 | 1535.971 | 346.09 | 1535.529 | 1535.529 | 0 | 0 | 0 | 57.802 | 0 | 0
1890 | 1401.399 | 91.51 | 295.5171 | 295.5171 | 0 | 0 | 0 | 1116.921 | 0 | 0
1891 | 1316.835 | 0 | 0 | 0 | 0 | 0 | 0 | 1316.835 | 0 | 0
1892 | 1148 | 0 | 0 | 0 | 0 | 0 | 0 | 1148 | 0 | 0
1893 | 1382.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1382.4 | 0 | 0
1894 | 1640.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1334.926 | 0 | 317.7434
1895 | 1377.6 | 0 | 0 | 0 | 0 | 0 | 0 | 785.6 | 0 | 614.9724
1896 | 1239.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1239.2 | 0 | 0
1897 | 950.4 | 0 | 0 | 0 | 0 | 0 | 0 | 950.4 | 0 | 0
1898 | 1244.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1244.8 | 0 | 0
1899 | 963.2 | 0 | 0 | 0 | 0 | 0 | 0 | 963.2 | 0 | 0
1900 | 860.8 | 0 | 0 | 0 | 0 | 0 | 0 | 860.8 | 0 | 0
1901 | 976.8 | 0 | 0 | 0 | 0 | 0 | 0 | 976.8 | 0 | 0
1902 | 1053.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1053.6 | 0 | 0
1903 | 880.938 | 81.18 | 269.3413 | 269.3413 | 0 | 0 | 0 | 621.658 | 0 | 0
1904 | 756.271 | 326.87 | 1457.0504 | 785.6179 | -614.9724 | 0 | 56.4601 | 0 | 0 | 0
1905 | 1395.164 | 586.1 | 2648.065 | 1449.304 | -423.0387 | 0 | 775.7223 | 0 | 0 | 0
1906 | 1631.193 | 807.84 | 3514.7377 | 1694.491 | 0 | 0 | 1820.2467 | 0 | 0 | 0
1907 | 1633.019 | 968.24 | 4088.1704 | 1696.3879 | 0 | 0 | 2391.7825 | 0 | 0 | 0
1908 | 1231.998 | 1052.76 | 4367.5715 | 1279.8054 | 0 | 0 | 3087.7661 | 0 | 0 | 0
1909 | 1467.239 | 1052.83 | 4374.4619 | 1524.1748 | 0 | 0 | 2850.287 | 0 | 0 | 0
1910 | 1286.247 | 893.98 | 3791.0037 | 1336.1595 | 0 | 0 | 2454.8442 | 0 | 0 | 0
1911 | 1439.505 | 812.47 | 3535.6852 | 1495.3646 | 0 | 0 | 2040.3206 | 0 | 0 | 0
1912 | 1449.081 | 597.24 | 2686.1922 | 1505.3122 | 0 | 0 | 1180.88 | 0 | 0 | 0
1913 | 1125.488 | 340.5 | 1508.2063 | 1169.1623 | 0 | 0 | 339.0441 | 0 | 0 | 0
1914 | 1313.406 | 89.91 | 290.3355 | 290.3355 | 0 | 0 | 0 | 1033.916 | 0 | 0
1915 | 1105.904 | 0 | 0 | 0 | 0 | 0 | 0 | 1105.904 | 0 | 0
1916 | 1031.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1031.2 | 0 | 0
1917 | 1051.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1051.2 | 0 | 0
1918 | 1335.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1029.326 | 0 | 317.7434
1919 | 1077.6 | 0 | 0 | 0 | 0 | 0 | 0 | 485.6 | 0 | 614.9724
1920 | 1121.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1121.6 | 0 | 0
1921 | 1212 | 0 | 0 | 0 | 0 | 0 | 0 | 1212 | 0 | 0
1922 | 1262.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.4 | 0 | 0
1923 | 1207.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1207.2 | 0 | 0
1924 | 970.4 | 0 | 0 | 0 | 0 | 0 | 0 | 970.4 | 0 | 0
1925 | 967.2 | 0 | 0 | 0 | 0 | 0 | 0 | 967.2 | 0 | 0
1926 | 1076.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1076.8 | 0 | 0
1927 | 691.327 | 80.93 | 268.9216 | 268.9216 | 0 | 0 | 0 | 432.451 | 0 | 0
1928 | 897.95 | 325.77 | 1450.0946 | 932.7947 | -517.2998 | 0 | 0 | 0 | 0 | 0
1929 | 500.197 | 579.74 | 2613.4146 | 519.607 | -520.7113 | 0 | 1573.0963 | 0 | 0 | 0
1930 | 375.337 | 789.08 | 3416.3286 | 389.9019 | 0 | 0 | 3026.4267 | 0 | 0 | 0
1931 | 375.588 | 928.97 | 3889.7265 | 390.1626 | 0 | 0 | 3499.5639 | 0 | 0 | 0
1932 | 389.912 | 1005.69 | 4127.593 | 405.0424 | 0 | 0 | 3722.5506 | 0 | 0 | 0
1933 | 750.082 | 790.41 | 3295.0326 | 779.1887 | 0 | 0 | 2515.8438 | 0 | 0 | 0
1934 | 1316.533 | 919.67 | 3839.948 | 1367.6207 | 0 | 0 | 2472.3273 | 0 | 0 | 0
1935 | 1499.779 | 766.3 | 3289.3368 | 1557.9775 | 0 | 0 | 1731.3593 | 0 | 0 | 0
1936 | 1507.149 | 554.55 | 2465.2031 | 1565.6335 | 0 | 0 | 899.5696 | 0 | 0 | 0
1937 | 1397.369 | 309.13 | 1362.9108 | 1362.9108 | 0 | 0 | 0 | 85.37 | 0 | 0
1938 | 997.74 | 75.26 | 258.8972 | 258.8972 | 0 | 0 | 0 | 748.514 | 0 | 0
1939 | 884.928 | 0 | 0 | 0 | 0 | 0 | 0 | 884.928 | 0 | 0
1940 | 686.4 | 0 | 0 | 0 | 0 | 0 | 0 | 686.4 | 0 | 0
1941 | 1051.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1051.2 | 0 | 0
1942 | 1072.8 | 0 | 0 | 0 | 0 | 0 | 0 | 766.926 | 0 | 317.7434
1943 | 1167.2 | 0 | 0 | 0 | 0 | 0 | 0 | 575.2 | 0 | 614.9724
1944 | 1155.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1155.2 | 0 | 0
1945 | 943.2 | 0 | 0 | 0 | 0 | 0 | 0 | 943.2 | 0 | 0
1946 | 1432.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1432.8 | 0 | 0
1947 | 1044 | 0 | 0 | 0 | 0 | 0 | 0 | 1044 | 0 | 0
1948 | 1157.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1157.6 | 0 | 0
1949 | 960.8 | 0 | 0 | 0 | 0 | 0 | 0 | 960.8 | 0 | 0
1950 | 852.8 | 0 | 0 | 0 | 0 | 0 | 0 | 852.8 | 0 | 0
1951 | 1154.806 | 75.41 | 264.5212 | 264.5212 | 0 | 0 | 0 | 900.166 | 0 | 0
1952 | 248.715 | 309.7 | 1376.7435 | 258.3663 | -614.9724 | 0 | 503.4048 | 0 | 0 | 0
1953 | 294.906 | 559.94 | 2504.4668 | 306.3498 | -423.0387 | 0 | 1775.0784 | 0 | 0 | 0
1954 | 233.76 | 767.08 | 3302.9981 | 242.831 | 0 | 0 | 3060.1671 | 0 | 0 | 0
1955 | 233.438 | 904.7 | 3770.8083 | 242.4965 | 0 | 0 | 3528.3118 | 0 | 0 | 0
1956 | 273.494 | 991.08 | 4051.031 | 284.1069 | 0 | 0 | 3766.9242 | 0 | 0 | 0
1957 | 185.868 | 988.46 | 4039.2853 | 193.0806 | 0 | 0 | 3846.2047 | 0 | 0 | 0
1958 | 251.672 | 900.77 | 3748.743 | 261.4381 | 0 | 0 | 3487.3049 | 0 | 0 | 0
1959 | 290.153 | 750.96 | 3218.8425 | 301.4123 | 0 | 0 | 2917.4302 | 0 | 0 | 0
1960 | 251.848 | 541.75 | 2404.1183 | 261.6209 | 0 | 0 | 2142.4974 | 0 | 0 | 0
1961 | 267.282 | 303.04 | 1333.7671 | 277.6538 | 0 | 0 | 1056.1133 | 0 | 0 | 0
1962 | 269.159 | 73.43 | 251.4572 | 251.4572 | 0 | 0 | 0 | 27.095 | 0 | 0
1963 | 186.389 | 0 | 0 | 0 | 0 | 0 | 0 | 186.389 | 0 | 0
1964 | 352 | 0 | 0 | 0 | 0 | 0 | 0 | 352 | 0 | 0
1965 | 209.6 | 0 | 0 | 0 | 0 | 0 | 0 | 116.526 | 0 | 96.6857
1966 | 269.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 280.0618
1967 | 288.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 300.0068
1968 | 246.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 255.9615
1969 | 255.2 | 0 | 0 | 0 | 0 | 0 | 0 | 255.2 | 0 | 0
1970 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | 220 | 0 | 0
1971 | 287.2 | 0 | 0 | 0 | 0 | 0 | 0 | 287.2 | 0 | 0
1972 | 292.8 | 0 | 0 | 0 | 0 | 0 | 0 | 292.8 | 0 | 0
1973 | 234.4 | 0 | 0 | 0 | 0 | 0 | 0 | 234.4 | 0 | 0
1974 | 231.2 | 0 | 0 | 0 | 0 | 0 | 0 | 231.2 | 0 | 0
1975 | 217.414 | 67.14 | 244.1004 | 225.8507 | -18.2497 | 0 | 0 | 0 | 0 | 0
1976 | 235.207 | 292.68 | 1312.2514 | 244.3341 | -614.9724 | 0 | 452.9448 | 0 | 0 | 0
1977 | 822.233 | 536.68 | 2422.4864 | 854.1395 | -404.789 | 0 | 1163.5579 | 0 | 0 | 0
1978 | 1224.436 | 431.7 | 1886.5006 | 1271.9499 | 0 | 0 | 614.5507 | 0 | 0 | 0
1979 | 1183.914 | 893.29 | 3806.8122 | 1229.8555 | 0 | 0 | 2576.9567 | 0 | 0 | 0
1980 | 1080.396 | 983.15 | 4119.1309 | 1122.3205 | 0 | 0 | 2996.8104 | 0 | 0 | 0
1981 | 1034.163 | 989.98 | 4132.8514 | 1074.2934 | 0 | 0 | 3058.558 | 0 | 0 | 0
1982 | 1287.314 | 912.1 | 3856.3185 | 1337.2679 | 0 | 0 | 2519.0506 | 0 | 0 | 0
1983 | 930.64 | 765.57 | 3316.4174 | 966.7533 | 0 | 0 | 2349.6641 | 0 | 0 | 0
1984 | 1303.577 | 554.14 | 2477.9004 | 1354.162 | 0 | 0 | 1123.7385 | 0 | 0 | 0
1985 | 1377.861 | 309.69 | 1367.494 | 1367.494 | 0 | 0 | 0 | 61.45 | 0 | 0
1986 | 1489.129 | 75.07 | 254.3555 | 254.3555 | 0 | 0 | 0 | 1244.275 | 0 | 0
1987 | 1582.537 | 0 | 0 | 0 | 0 | 0 | 0 | 1582.537 | 0 | 0
1988 | 1236.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1236.8 | 0 | 0
1989 | 1488.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1488.8 | 0 | 0
1990 | 1436.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1130.926 | 0 | 317.7434
1991 | 1529.6 | 0 | 0 | 0 | 0 | 0 | 0 | 937.6 | 0 | 614.9724
1992 | 1294.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1294.4 | 0 | 0
1993 | 1304 | 0 | 0 | 0 | 0 | 0 | 0 | 1304 | 0 | 0
1994 | 1234.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1234.4 | 0 | 0
1995 | 1701.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1701.6 | 0 | 0
1996 | 1300 | 0 | 0 | 0 | 0 | 0 | 0 | 1300 | 0 | 0
1997 | 1364.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1364.8 | 0 | 0
1998 | 1507.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1507.2 | 0 | 0
1999 | 1696 | 72.9 | 258.9501 | 258.9501 | 0 | 0 | 0 | 1446.723 | 0 | 0
2000 | 1387.644 | 304.37 | 1359.3155 | 1359.3155 | 0 | 0 | 0 | 79.106 | 0 | 0
2001 | 1583.009 | 551.4 | 2485.4588 | 1644.4373 | -614.9724 | 0 | 226.0491 | 0 | 0 | 0
2002 | 2116.262 | 758.88 | 3309.3265 | 2198.383 | -423.0387 | 0 | 687.9048 | 0 | 0 | 0
2003 | 2008.054 | 900.35 | 3828.0557 | 2085.976 | 0 | 0 | 1742.0797 | 0 | 0 | 0
2004 | 1681.412 | 980.96 | 4116.3095 | 1746.6588 | 0 | 0 | 2369.6508 | 0 | 0 | 0
2005 | 1625.792 | 662.02 | 2816.2828 | 1688.8804 | 0 | 0 | 1127.4023 | 0 | 0 | 0
2006 | 1544.619 | 875.81 | 3740.6112 | 1604.5576 | 0 | 0 | 2136.0537 | 0 | 0 | 0
2007 | 1606.752 | 750.07 | 3280.0229 | 1669.1016 | 0 | 0 | 1610.9213 | 0 | 0 | 0
2008 | 1395.182 | 543.7 | 2446.7166 | 1449.3217 | 0 | 0 | 997.3949 | 0 | 0 | 0
2009 | 1443.602 | 305.47 | 1355.7669 | 1355.7669 | 0 | 0 | 0 | 138.48 | 0 | 0
2010 | 1556.4 | 74.49 | 256.2711 | 256.2711 | 0 | 0 | 0 | 1309.702 | 0 | 0
2011 | 1556.11 | 0 | 0 | 0 | 0 | 0 | 0 | 1556.11 | 0 | 0
2012 | 1073.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1073.6 | 0 | 0
2013 | 1459.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1459.2 | 0 | 0
2014 | 1785.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1479.726 | 0 | 317.7434
2015 | 1840 | 0 | 0 | 0 | 0 | 0 | 0 | 1248 | 0 | 614.9724
2016 | 1543.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1543.2 | 0 | 0
2017 | 1344.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1344.8 | 0 | 0
2018 | 1585.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1585.6 | 0 | 0
2019 | 1395.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1395.2 | 0 | 0
2020 | 1634.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1634.4 | 0 | 0
2021 | 1428 | 0 | 0 | 0 | 0 | 0 | 0 | 1428 | 0 | 0
2022 | 1732.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1732.8 | 0 | 0
2023 | 1353.618 | 72.27 | 259.8726 | 259.8726 | 0 | 0 | 0 | 1103.453 | 0 | 0
2024 | 1535.856 | 299.43 | 1337.5099 | 1337.5099 | 0 | 0 | 0 | 248.309 | 0 | 0
2025 | 1275.614 | 538.51 | 2414.3432 | 1325.1139 | -614.9724 | 0 | 474.257 | 0 | 0 | 0
2026 | 1988.333 | 753.92 | 3262.8722 | 2065.4898 | -423.0387 | 0 | 774.3438 | 0 | 0 | 0
2027 | 1904.751 | 922.08 | 3878.7681 | 1978.6644 | 0 | 0 | 1900.1037 | 0 | 0 | 0
2028 | 1672.28 | 997.28 | 4134.7203 | 1737.1724 | 0 | 0 | 2397.5479 | 0 | 0 | 0
2029 | 1859.284 | 647.48 | 2753.8714 | 1931.433 | 0 | 0 | 822.4383 | 0 | 0 | 0
2030 | 1626.32 | 531.34 | 2284.9154 | 1689.4289 | 0 | 0 | 595.4865 | 0 | 0 | 0
2031 | 1494.969 | 759.29 | 3316.299 | 1552.9809 | 0 | 0 | 1763.3181 | 0 | 0 | 0
2032 | 1162.25 | 549.81 | 2472.8207 | 1207.3508 | 0 | 0 | 1265.4699 | 0 | 0 | 0
2033 | 1264.538 | 306.07 | 1355.7908 | 1313.6081 | 0 | 0 | 42.1827 | 0 | 0 | 0
2034 | 1476.872 | 75.51 | 261.6178 | 261.6178 | 0 | 0 | 0 | 1225.027 | 0 | 0
2035 | 1536.546 | 0 | 0 | 0 | 0 | 0 | 0 | 1536.546 | 0 | 0
2036 | 1277.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1277.6 | 0 | 0
2037 | 1460.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1460.8 | 0 | 0
2038 | 1661.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1355.726 | 0 | 317.7434
2039 | 1407.2 | 0 | 0 | 0 | 0 | 0 | 0 | 815.2 | 0 | 614.9724
2040 | 1428 | 0 | 0 | 0 | 0 | 0 | 0 | 1428 | 0 | 0
2041 | 1554.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1554.4 | 0 | 0
2042 | 1313.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1313.6 | 0 | 0
2043 | 1546.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1546.4 | 0 | 0
2044 | 1344.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1344.8 | 0 | 0
2045 | 1362.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1362.4 | 0 | 0
2046 | 1128.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1128.8 | 0 | 0
2047 | 1486.419 | 75.78 | 269.3766 | 269.3766 | 0 | 0 | 0 | 1227.105 | 0 | 0
2048 | 1323.308 | 187.22 | 825.1153 | 825.1153 | 0 | 0 | 0 | 529.015 | 0 | 0
2049 | 1226.957 | 470.56 | 2088.2448 | 1274.5688 | -614.9724 | 0 | 198.7036 | 0 | 0 | 0
2050 | 1796.019 | 757.77 | 3228.7599 | 1865.7131 | -423.0387 | 0 | 940.0082 | 0 | 0 | 0
2051 | 1668.541 | 882.73 | 3638.7783 | 1733.2883 | 0 | 0 | 1905.4899 | 0 | 0 | 0
2052 | 1931.97 | 963.57 | 3883.4521 | 2006.9396 | 0 | 0 | 1876.5125 | 0 | 0 | 0
2053 | 1668.96 | 764.32 | 3139.429 | 1733.7236 | 0 | 0 | 1405.7054 | 0 | 0 | 0
2054 | 1763.69 | 584.26 | 2453.955 | 1832.1295 | 0 | 0 | 621.8254 | 0 | 0 | 0
2055 | 1579.999 | 668.07 | 2856.604 | 1641.3105 | 0 | 0 | 1215.2935 | 0 | 0 | 0
2056 | 1714.12 | 504.59 | 2231.5178 | 1780.636 | 0 | 0 | 450.8818 | 0 | 0 | 0
2057 | 1622.297 | 271.09 | 1198.2831 | 1198.2831 | 0 | 0 | 0 | 468.776 | 0 | 0
2058 | 1842.205 | 54.54 | 192.2578 | 192.2578 | 0 | 0 | 0 | 1657.129 | 0 | 0
2059 | 1704.336 | 0 | 0 | 0 | 0 | 0 | 0 | 1704.336 | 0 | 0
2060 | 1539.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1539.2 | 0 | 0
2061 | 1760 | 0 | 0 | 0 | 0 | 0 | 0 | 1760 | 0 | 0
2062 | 1748 | 0 | 0 | 0 | 0 | 0 | 0 | 1442.126 | 0 | 317.7434
2063 | 1951.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1359.2 | 0 | 614.9724
2064 | 1534.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1534.4 | 0 | 0
2065 | 1479.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1479.2 | 0 | 0
2066 | 1765.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1765.6 | 0 | 0
2067 | 1462.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1462.4 | 0 | 0
2068 | 1915.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1915.2 | 0 | 0
2069 | 1624.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1624.8 | 0 | 0
2070 | 1568 | 0 | 0 | 0 | 0 | 0 | 0 | 1568 | 0 | 0
2071 | 1421.665 | 60.78 | 221.2602 | 221.2602 | 0 | 0 | 0 | 1208.67 | 0 | 0
2072 | 1488.271 | 282.88 | 1265.2704 | 1265.2704 | 0 | 0 | 0 | 270.265 | 0 | 0
2073 | 1486.483 | 515.37 | 2291.4682 | 1544.1656 | -614.9724 | 0 | 132.3302 | 0 | 0 | 0
2074 | 1803.338 | 724.33 | 3092.7794 | 1873.3161 | -423.0387 | 0 | 796.4246 | 0 | 0 | 0
2075 | 2033.628 | 885.45 | 3650.3755 | 2112.5424 | 0 | 0 | 1537.833 | 0 | 0 | 0
2076 | 1696.775 | 878.64 | 3589.3488 | 1762.6179 | 0 | 0 | 1826.7309 | 0 | 0 | 0
2077 | 1592.548 | 922.45 | 3761.8423 | 1654.3464 | 0 | 0 | 2107.4959 | 0 | 0 | 0
2078 | 1457.42 | 709.01 | 2974.8896 | 1513.9748 | 0 | 0 | 1460.9147 | 0 | 0 | 0
2079 | 1641.988 | 727.04 | 3105.9618 | 1705.7049 | 0 | 0 | 1400.2569 | 0 | 0 | 0
2080 | 1955.911 | 521.94 | 2308.4236 | 2031.8096 | 0 | 0 | 276.614 | 0 | 0 | 0
2081 | 1702.841 | 283.66 | 1246.3694 | 1246.3694 | 0 | 0 | 0 | 503.03 | 0 | 0
2082 | 1466.806 | 62.55 | 219.1556 | 219.1556 | 0 | 0 | 0 | 1255.837 | 0 | 0
2083 | 1663.509 | 0 | 0 | 0 | 0 | 0 | 0 | 1663.509 | 0 | 0
2084 | 1294.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1294.4 | 0 | 0
2085 | 1368 | 0 | 0 | 0 | 0 | 0 | 0 | 1368 | 0 | 0
2086 | 1146.4 | 0 | 0 | 0 | 0 | 0 | 0 | 840.526 | 0 | 317.7434
2087 | 1459.2 | 0 | 0 | 0 | 0 | 0 | 0 | 867.2 | 0 | 614.9724
2088 | 1268.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1268.8 | 0 | 0
2089 | 923.2 | 0 | 0 | 0 | 0 | 0 | 0 | 923.2 | 0 | 0
2090 | 1351.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1351.2 | 0 | 0
2091 | 1026.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1026.4 | 0 | 0
2092 | 1252.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1252.8 | 0 | 0
2093 | 1265.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1265.6 | 0 | 0
2094 | 918.4 | 0 | 0 | 0 | 0 | 0 | 0 | 918.4 | 0 | 0
2095 | 1050.829 | 67.97 | 249.8668 | 249.8668 | 0 | 0 | 0 | 810.296 | 0 | 0
2096 | 806.027 | 303.92 | 1357.4228 | 837.3047 | -520.1181 | 0 | 0 | 0 | 0 | 0
2097 | 1095.822 | 457.81 | 2054.2696 | 1138.3461 | -517.893 | 0 | 398.0305 | 0 | 0 | 0
2098 | 1270.332 | 776.77 | 3371.9384 | 1319.6269 | 0 | 0 | 2052.3115 | 0 | 0 | 0
2099 | 1318.43 | 938.77 | 3969.8962 | 1369.5913 | 0 | 0 | 2600.3049 | 0 | 0 | 0
2100 | 1137.052 | 1023.34 | 4270.4224 | 1181.175 | 0 | 0 | 3089.2474 | 0 | 0 | 0
2101 | 1338.908 | 1024.82 | 4287.4962 | 1390.864 | 0 | 0 | 2896.6322 | 0 | 0 | 0
2102 | 1124.637 | 933.59 | 3967.8976 | 1168.2783 | 0 | 0 | 2799.6193 | 0 | 0 | 0
2103 | 1168.045 | 782.7 | 3412.7624 | 1213.3707 | 0 | 0 | 2199.3917 | 0 | 0 | 0
2104 | 1479.406 | 568.7 | 2553.5888 | 1536.814 | 0 | 0 | 1016.7748 | 0 | 0 | 0
2105 | 1301.431 | 318.95 | 1404.7289 | 1351.9327 | 0 | 0 | 52.7962 | 0 | 0 | 0
2106 | 1478.389 | 78.07 | 254.6391 | 254.6391 | 0 | 0 | 0 | 1233.262 | 0 | 0
2107 | 1147.38 | 0 | 0 | 0 | 0 | 0 | 0 | 1147.38 | 0 | 0
2108 | 1016 | 0 | 0 | 0 | 0 | 0 | 0 | 1016 | 0 | 0
2109 | 1436 | 0 | 0 | 0 | 0 | 0 | 0 | 1436 | 0 | 0
2110 | 1550.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1244.526 | 0 | 317.7434
2111 | 1441.6 | 0 | 0 | 0 | 0 | 0 | 0 | 849.6 | 0 | 614.9724
2112 | 1428 | 0 | 0 | 0 | 0 | 0 | 0 | 1428 | 0 | 0
2113 | 1300 | 0 | 0 | 0 | 0 | 0 | 0 | 1300 | 0 | 0
2114 | 1284 | 0 | 0 | 0 | 0 | 0 | 0 | 1284 | 0 | 0
2115 | 1629.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1629.6 | 0 | 0
2116 | 1440 | 0 | 0 | 0 | 0 | 0 | 0 | 1440 | 0 | 0
2117 | 1583.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1583.2 | 0 | 0
2118 | 1600 | 0 | 0 | 0 | 0 | 0 | 0 | 1600 | 0 | 0
2119 | 1140.384 | 85.2 | 305.3338 | 305.3338 | 0 | 0 | 0 | 846.456 | 0 | 0
2120 | 204.826 | 321.34 | 1428.2838 | 212.7742 | -614.9724 | 0 | 600.5372 | 0 | 0 | 0
2121 | 307.065 | 567.78 | 2530.0858 | 318.9806 | -423.0387 | 0 | 1788.0666 | 0 | 0 | 0
2122 | 313.222 | 773.7 | 3320.368 | 325.3765 | 0 | 0 | 2994.9915 | 0 | 0 | 0
2123 | 355.547 | 917.13 | 3827.4699 | 369.3439 | 0 | 0 | 3458.126 | 0 | 0 | 0
2124 | 311.517 | 997.11 | 4099.5785 | 323.6053 | 0 | 0 | 3775.9732 | 0 | 0 | 0
2125 | 299.716 | 668.68 | 2807.2992 | 311.3464 | 0 | 0 | 2495.9528 | 0 | 0 | 0
2126 | 315.351 | 915.01 | 3824.8562 | 327.5881 | 0 | 0 | 3497.2681 | 0 | 0 | 0
2127 | 283.379 | 761.48 | 3271.6719 | 294.3755 | 0 | 0 | 2977.2965 | 0 | 0 | 0
2128 | 230.684 | 549.51 | 2435.4736 | 239.6356 | 0 | 0 | 2195.8379 | 0 | 0 | 0
2129 | 250.683 | 304.05 | 1326.4394 | 260.4107 | 0 | 0 | 1066.0287 | 0 | 0 | 0
2130 | 298.518 | 72.87 | 242.8403 | 242.8403 | 0 | 0 | 0 | 64.749 | 0 | 0
2131 | 256.165 | 0 | 0 | 0 | 0 | 0 | 0 | 256.165 | 0 | 0
2132 | 318.4 | 0 | 0 | 0 | 0 | 0 | 0 | 318.4 | 0 | 0
2133 | 298.4 | 0 | 0 | 0 | 0 | 0 | 0 | 111.726 | 0 | 193.9178
2134 | 237.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246.82
2135 | 305.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 317.4587
2136 | 168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 174.5192
2137 | 228.8 | 0 | 0 | 0 | 0 | 0 | 0 | 228.8 | 0 | 0
2138 | 226.4 | 0 | 0 | 0 | 0 | 0 | 0 | 226.4 | 0 | 0
2139 | 221.6 | 0 | 0 | 0 | 0 | 0 | 0 | 221.6 | 0 | 0
2140 | 135.2 | 0 | 0 | 0 | 0 | 0 | 0 | 135.2 | 0 | 0
2141 | 148.8 | 0 | 0 | 0 | 0 | 0 | 0 | 148.8 | 0 | 0
2142 | 203.2 | 0 | 0 | 0 | 0 | 0 | 0 | 203.2 | 0 | 0
2143 | 139.948 | 84.65 | 309.0714 | 145.3786 | -163.6928 | 0 | 0 | 0 | 0 | 0
2144 | 168.345 | 315.71 | 1396.3426 | 174.8776 | -614.9724 | 0 | 606.4926 | 0 | 0 | 0
2145 | 999.188 | 559.15 | 2460.4371 | 1037.9612 | -259.3459 | 0 | 1163.1299 | 0 | 0 | 0
2146 | 1188.218 | 687.78 | 2926.2704 | 1234.3265 | 0 | 0 | 1691.9439 | 0 | 0 | 0
2147 | 1369.757 | 525.43 | 2214.6746 | 1422.9101 | 0 | 0 | 791.7645 | 0 | 0 | 0
2148 | 1382.264 | 599.82 | 2495.0158 | 1435.9024 | 0 | 0 | 1059.1134 | 0 | 0 | 0
2149 | 1401.945 | 780.61 | 3210.8998 | 1456.3471 | 0 | 0 | 1754.5526 | 0 | 0 | 0
2150 | 1395.96 | 638.1 | 2668.4972 | 1450.1299 | 0 | 0 | 1218.3673 | 0 | 0 | 0
2151 | 1436.28 | 550.68 | 2357.504 | 1492.0145 | 0 | 0 | 865.4895 | 0 | 0 | 0
2152 | 1584.287 | 433.63 | 1913.0784 | 1645.7649 | 0 | 0 | 267.3135 | 0 | 0 | 0
2153 | 1458.461 | 289.6 | 1266.9387 | 1266.9387 | 0 | 0 | 0 | 238.849 | 0 | 0
2154 | 1392.377 | 67.8 | 233.0288 | 233.0288 | 0 | 0 | 0 | 1168.053 | 0 | 0
2155 | 1600.335 | 0 | 0 | 0 | 0 | 0 | 0 | 1600.335 | 0 | 0
2156 | 1251.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1251.2 | 0 | 0
2157 | 921.6 | 0 | 0 | 0 | 0 | 0 | 0 | 921.6 | 0 | 0
2158 | 1216 | 0 | 0 | 0 | 0 | 0 | 0 | 910.126 | 0 | 317.7434
2159 | 1305.6 | 0 | 0 | 0 | 0 | 0 | 0 | 713.6 | 0 | 614.9724
2160 | 875.2 | 0 | 0 | 0 | 0 | 0 | 0 | 875.2 | 0 | 0
2161 | 1137.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1137.6 | 0 | 0
2162 | 760 | 0 | 0 | 0 | 0 | 0 | 0 | 760 | 0 | 0
2163 | 1196.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1196.8 | 0 | 0
2164 | 1156 | 0 | 0 | 0 | 0 | 0 | 0 | 1156 | 0 | 0
2165 | 1220 | 0 | 0 | 0 | 0 | 0 | 0 | 1220 | 0 | 0
2166 | 1054.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1054.4 | 0 | 0
2167 | 1293.304 | 75.61 | 283.5168 | 283.5168 | 0 | 0 | 0 | 1020.378 | 0 | 0
2168 | 1393.785 | 243.93 | 1085.9343 | 1085.9343 | 0 | 0 | 0 | 348.416 | 0 | 0
2169 | 1579.901 | 551.03 | 2432.7592 | 1641.2087 | -614.9724 | 0 | 176.5781 | 0 | 0 | 0
2170 | 1649.699 | 753.44 | 3182.477 | 1713.7152 | -423.0387 | 0 | 1045.7232 | 0 | 0 | 0
2171 | 1676.943 | 911.3 | 3726.3048 | 1742.0164 | 0 | 0 | 1984.2885 | 0 | 0 | 0
2172 | 1684.745 | 991.31 | 3992.0747 | 1750.1211 | 0 | 0 | 2241.9536 | 0 | 0 | 0
2173 | 1931.871 | 988.55 | 4008.2136 | 2006.8368 | 0 | 0 | 2001.3768 | 0 | 0 | 0
2174 | 1728.951 | 432.11 | 1820.8263 | 1796.0425 | 0 | 0 | 24.7838 | 0 | 0 | 0
2175 | 1653.202 | 722.21 | 3081.7618 | 1717.3541 | 0 | 0 | 1364.4077 | 0 | 0 | 0
2176 | 1470.106 | 438.37 | 1914.0487 | 1527.1531 | 0 | 0 | 386.8956 | 0 | 0 | 0
2177 | 1634.306 | 276.88 | 1213.6356 | 1213.6356 | 0 | 0 | 0 | 466.006 | 0 | 0
2178 | 1538.105 | 60.12 | 206.9133 | 206.9133 | 0 | 0 | 0 | 1338.921 | 0 | 0
2179 | 1470.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1470.4 | 0 | 0
2180 | 1250.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1250.4 | 0 | 0
2181 | 1324.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1324.8 | 0 | 0
2182 | 1529.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1223.726 | 0 | 317.7434
2183 | 1635.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1043.2 | 0 | 614.9724
2184 | 1508 | 0 | 0 | 0 | 0 | 0 | 0 | 1508 | 0 | 0
2185 | 972 | 0 | 0 | 0 | 0 | 0 | 0 | 972 | 0 | 0
2186 | 1086.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1086.4 | 0 | 0
2187 | 1562.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1562.4 | 0 | 0
2188 | 1220 | 0 | 0 | 0 | 0 | 0 | 0 | 1220 | 0 | 0
2189 | 1601.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1601.6 | 0 | 0
2190 | 1461.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1461.6 | 0 | 0
2191 | 1554.491 | 52.85 | 203.7377 | 203.7377 | 0 | 0 | 0 | 1358.364 | 0 | 0
2192 | 1258.89 | 195.35 | 859.7532 | 859.7532 | 0 | 0 | 0 | 431.253 | 0 | 0
2193 | 1130.656 | 420.19 | 1828.875 | 1174.5308 | -614.9724 | 0 | 39.3717 | 0 | 0 | 0
2194 | 1493.053 | 605.43 | 2553.1037 | 1550.9905 | -423.0387 | 0 | 579.0744 | 0 | 0 | 0
2195 | 1407.71 | 720.63 | 2974.1686 | 1462.3358 | 0 | 0 | 1511.8328 | 0 | 0 | 0
2196 | 1593.023 | 791.25 | 3228.736 | 1654.8399 | 0 | 0 | 1573.8962 | 0 | 0 | 0
2197 | 1931.914 | 755.94 | 3098.0908 | 2006.8814 | 0 | 0 | 1091.2093 | 0 | 0 | 0
2198 | 1327.845 | 629.47 | 2622.2444 | 1379.3717 | 0 | 0 | 1242.8727 | 0 | 0 | 0
2199 | 1348.658 | 773.75 | 3307.7413 | 1400.9923 | 0 | 0 | 1906.749 | 0 | 0 | 0
2200 | 1472.454 | 485.18 | 2115.5269 | 1529.5922 | 0 | 0 | 585.9347 | 0 | 0 | 0
2201 | 1419.53 | 312.83 | 1353.6436 | 1353.6436 | 0 | 0 | 0 | 116.452 | 0 | 0
2202 | 938.571 | 40.11 | 141.0842 | 141.0842 | 0 | 0 | 0 | 802.757 | 0 | 0
2203 | 1347.852 | 0 | 0 | 0 | 0 | 0 | 0 | 1347.852 | 0 | 0
2204 | 1007.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1007.2 | 0 | 0
2205 | 1144 | 0 | 0 | 0 | 0 | 0 | 0 | 1144 | 0 | 0
2206 | 1352 | 0 | 0 | 0 | 0 | 0 | 0 | 1046.126 | 0 | 317.7434
2207 | 1520.8 | 0 | 0 | 0 | 0 | 0 | 0 | 928.8 | 0 | 614.9724
2208 | 1532.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1532.8 | 0 | 0
2209 | 1087.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1087.2 | 0 | 0
2210 | 1328.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1328.8 | 0 | 0
2211 | 1067.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1067.2 | 0 | 0
2212 | 1069.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1069.6 | 0 | 0
2213 | 964.8 | 0 | 0 | 0 | 0 | 0 | 0 | 964.8 | 0 | 0
2214 | 1233.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1233.6 | 0 | 0
2215 | 1241.187 | 94.83 | 331.0484 | 331.0484 | 0 | 0 | 0 | 922.505 | 0 | 0
2216 | 1139.749 | 332.6 | 1477.0391 | 1183.9767 | -293.0624 | 0 | 0 | 0 | 0 | 0
2217 | 1485.342 | 576.05 | 2571.5196 | 1542.9803 | -614.9724 | 0 | 413.5669 | 0 | 0 | 0
2218 | 1788.565 | 784.99 | 3386.6822 | 1857.9698 | -129.9763 | 0 | 1398.7361 | 0 | 0 | 0
2219 | 1486.331 | 935.09 | 3938.5108 | 1544.0077 | 0 | 0 | 2394.5031 | 0 | 0 | 0
2220 | 1635.414 | 1012.44 | 4215.0147 | 1698.8758 | 0 | 0 | 2516.1388 | 0 | 0 | 0
2221 | 1839.255 | 719.66 | 3012.941 | 1910.6268 | 0 | 0 | 1102.3142 | 0 | 0 | 0
2222 | 1431.431 | 920.7 | 3898.0888 | 1486.9773 | 0 | 0 | 2411.1115 | 0 | 0 | 0
2223 | 1727.174 | 768.04 | 3332.3319 | 1794.1966 | 0 | 0 | 1538.1353 | 0 | 0 | 0
2224 | 1726.438 | 559.03 | 2497.9317 | 1793.432 | 0 | 0 | 704.4997 | 0 | 0 | 0
2225 | 1599.501 | 312.42 | 1359.6105 | 1359.6105 | 0 | 0 | 0 | 290.679 | 0 | 0
2226 | 1633.042 | 77.24 | 240.9601 | 240.9601 | 0 | 0 | 0 | 1401.083 | 0 | 0
2227 | 1619.476 | 0 | 0 | 0 | 0 | 0 | 0 | 1619.476 | 0 | 0
2228 | 1533.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1533.6 | 0 | 0
2229 | 1748.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1748.8 | 0 | 0
2230 | 1145.6 | 0 | 0 | 0 | 0 | 0 | 0 | 839.726 | 0 | 317.7434
2231 | 1203.2 | 0 | 0 | 0 | 0 | 0 | 0 | 611.2 | 0 | 614.9724
2232 | 382.4 | 0 | 0 | 0 | 0 | 0 | 0 | 382.4 | 0 | 0
2233 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 120 | 0 | 0
2234 | 126.4 | 0 | 0 | 0 | 0 | 0 | 0 | 126.4 | 0 | 0
2235 | 118.4 | 0 | 0 | 0 | 0 | 0 | 0 | 118.4 | 0 | 0
2236 | 124.8 | 0 | 0 | 0 | 0 | 0 | 0 | 124.8 | 0 | 0
2237 | 127.2 | 0 | 0 | 0 | 0 | 0 | 0 | 127.2 | 0 | 0
2238 | 104.8 | 0 | 0 | 0 | 0 | 0 | 0 | 104.8 | 0 | 0
2239 | 90.455 | 50.03 | 192.5539 | 93.9651 | -98.5888 | 0 | 0 | 0 | 0 | 0
2240 | 181.636 | 194.46 | 859.2276 | 188.6843 | -614.9724 | 0 | 55.5709 | 0 | 0 | 0
2241 | 1303.888 | 212.59 | 923.3883 | 923.3883 | 0 | 0 | 0 | 0 | 0 | 431.0967
2242 | 1593.999 | 518.73 | 2226.8992 | 1655.8537 | -571.0455 | 0 | 0 | 0 | 0 | 0
2243 | 1722.687 | 611.28 | 2574.1873 | 1789.5354 | -233.1691 | 0 | 551.4827 | 0 | 0 | 0
2244 | 1824.597 | 610.08 | 2545.8237 | 1895.4 | 0 | 0 | 650.4237 | 0 | 0 | 0
2245 | 1538.349 | 766.06 | 3152.7236 | 1598.0442 | 0 | 0 | 1554.6793 | 0 | 0 | 0
2246 | 1462.819 | 716.29 | 2975.0319 | 1519.5833 | 0 | 0 | 1455.4486 | 0 | 0 | 0
2247 | 1763.062 | 529.02 | 2252.5536 | 1831.4772 | 0 | 0 | 421.0764 | 0 | 0 | 0
2248 | 1727.078 | 450.78 | 1967.0734 | 1794.0968 | 0 | 0 | 172.9766 | 0 | 0 | 0
2249 | 1726.744 | 70.39 | 282.9496 | 282.9496 | 0 | 0 | 0 | 1454.364 | 0 | 0
2250 | 1440.062 | 19.59 | 54.6567 | 54.6567 | 0 | 0 | 0 | 1387.447 | 0 | 0
2251 | 1485.876 | 0 | 0 | 0 | 0 | 0 | 0 | 1485.876 | 0 | 0
2252 | 1420 | 0 | 0 | 0 | 0 | 0 | 0 | 1420 | 0 | 0
2253 | 1555.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1555.2 | 0 | 0
2254 | 1828.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1522.926 | 0 | 317.7434
2255 | 1337.6 | 0 | 0 | 0 | 0 | 0 | 0 | 745.6 | 0 | 614.9724
2256 | 1448.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1448.8 | 0 | 0
2257 | 1088.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1088.8 | 0 | 0
2258 | 1398.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1398.4 | 0 | 0
2259 | 1239.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1239.2 | 0 | 0
2260 | 1181.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1181.6 | 0 | 0
2261 | 1463.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1463.2 | 0 | 0
2262 | 1187.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1187.2 | 0 | 0
2263 | 1184.8 | 83.53 | 321.9349 | 321.9349 | 0 | 0 | 0 | 874.891 | 0 | 0
2264 | 1603.456 | 280.9 | 1257.121 | 1257.121 | 0 | 0 | 0 | 393.295 | 0 | 0
2265 | 1609.349 | 445.01 | 1965.0924 | 1671.7994 | -293.293 | 0 | 0 | 0 | 0 | 0
2266 | 1528.207 | 610.18 | 2621.1734 | 1587.5087 | -614.9724 | 0 | 418.6923 | 0 | 0 | 0
2267 | 1584.409 | 710.29 | 2977.6933 | 1645.8926 | -129.7457 | 0 | 1202.055 | 0 | 0 | 0
2268 | 1411.614 | 748.29 | 3089.2017 | 1466.3913 | 0 | 0 | 1622.8104 | 0 | 0 | 0
2269 | 1807.633 | 779.54 | 3200.065 | 1877.7777 | 0 | 0 | 1322.2873 | 0 | 0 | 0
2270 | 1580.825 | 752.37 | 3118.6591 | 1642.1685 | 0 | 0 | 1476.4906 | 0 | 0 | 0
2271 | 1109.428 | 584.53 | 2487.2684 | 1152.4791 | 0 | 0 | 1334.7893 | 0 | 0 | 0
2272 | 1562.899 | 440.64 | 1929.6318 | 1623.5469 | 0 | 0 | 306.0849 | 0 | 0 | 0
2273 | 1288.141 | 243.19 | 1069.1742 | 1069.1742 | 0 | 0 | 0 | 258.906 | 0 | 0
2274 | 1690.754 | 60.78 | 217.186 | 217.186 | 0 | 0 | 0 | 1481.681 | 0 | 0
2275 | 1651.22 | 0 | 0 | 0 | 0 | 0 | 0 | 1651.22 | 0 | 0
2276 | 1392.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1392.8 | 0 | 0
2277 | 1446.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1446.4 | 0 | 0
2278 | 1270.4 | 0 | 0 | 0 | 0 | 0 | 0 | 964.526 | 0 | 317.7434
2279 | 1509.6 | 0 | 0 | 0 | 0 | 0 | 0 | 917.6 | 0 | 614.9724
2280 | 1620 | 0 | 0 | 0 | 0 | 0 | 0 | 1620 | 0 | 0
2281 | 1519.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1519.2 | 0 | 0
2282 | 1356.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1356.8 | 0 | 0
2283 | 1847.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1847.2 | 0 | 0
2284 | 1688 | 0 | 0 | 0 | 0 | 0 | 0 | 1688 | 0 | 0
2285 | 1469.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1469.6 | 0 | 0
2286 | 1407.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1407.2 | 0 | 0
2287 | 1298.407 | 34.3 | 122.9519 | 122.9519 | 0 | 0 | 0 | 1180.048 | 0 | 0
2288 | 341.456 | 118.01 | 509.0299 | 354.7061 | -154.3238 | 0 | 0 | 0 | 0 | 0
2289 | 276.424 | 344.97 | 1519.4431 | 287.1506 | -614.9724 | 0 | 617.3201 | 0 | 0 | 0
2290 | 284.243 | 599.75 | 2555.0317 | 295.274 | -268.7149 | 0 | 1991.0428 | 0 | 0 | 0
2291 | 269.004 | 912.23 | 3756.9454 | 279.4426 | 0 | 0 | 3477.5028 | 0 | 0 | 0
2292 | 333.853 | 858.81 | 3461.0741 | 346.8081 | 0 | 0 | 3114.266 | 0 | 0 | 0
2293 | 211.973 | 746.35 | 3034.6156 | 220.1986 | 0 | 0 | 2814.4171 | 0 | 0 | 0
2294 | 211.252 | 821.02 | 3303.8447 | 219.4496 | 0 | 0 | 3084.3952 | 0 | 0 | 0
2295 | 343.658 | 607.31 | 2545.457 | 356.9936 | 0 | 0 | 2188.4635 | 0 | 0 | 0
2296 | 393.167 | 313.99 | 1354.3708 | 408.4237 | 0 | 0 | 945.947 | 0 | 0 | 0
2297 | 317.159 | 253.68 | 1105.9479 | 329.4663 | 0 | 0 | 776.4816 | 0 | 0 | 0
2298 | 348.83 | 62.6 | 220.1248 | 220.1248 | 0 | 0 | 0 | 136.928 | 0 | 0
2299 | 281.691 | 0 | 0 | 0 | 0 | 0 | 0 | 281.691 | 0 | 0
2300 | 266.4 | 0 | 0 | 0 | 0 | 0 | 0 | 266.4 | 0 | 0
2301 | 309.6 | 0 | 0 | 0 | 0 | 0 | 0 | 86.126 | 0 | 232.1459
2302 | 292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 303.331
2303 | 243.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 252.6373
2304 | 139.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 144.6016
2305 | 142.4 | 0 | 0 | 0 | 0 | 0 | 0 | 142.4 | 0 | 0
2306 | 124 | 0 | 0 | 0 | 0 | 0 | 0 | 124 | 0 | 0
2307 | 118.4 | 0 | 0 | 0 | 0 | 0 | 0 | 118.4 | 0 | 0
2308 | 115.2 | 0 | 0 | 0 | 0 | 0 | 0 | 115.2 | 0 | 0
2309 | 101.6 | 0 | 0 | 0 | 0 | 0 | 0 | 101.6 | 0 | 0
2310 | 99.2 | 0 | 0 | 0 | 0 | 0 | 0 | 99.2 | 0 | 0
2311 | 81.795 | 79.16 | 309.355 | 84.969 | -224.386 | 0 | 0 | 0 | 0 | 0
2312 | 89.489 | 265.15 | 1185.5505 | 92.9616 | -614.9724 | 0 | 477.6165 | 0 | 0 | 0
2313 | 89.121 | 559 | 2492.2661 | 92.5793 | -198.6527 | 0 | 2201.034 | 0 | 0 | 0
2314 | 88.082 | 761.4 | 3286.049 | 91.5 | 0 | 0 | 3194.549 | 0 | 0 | 0
2315 | 84.446 | 900.54 | 3791.8731 | 87.7229 | 0 | 0 | 3704.1502 | 0 | 0 | 0
2316 | 92.13 | 590.69 | 2498.5643 | 95.7051 | 0 | 0 | 2402.8593 | 0 | 0 | 0
2317 | 88.264 | 194.27 | 816.0196 | 91.6891 | 0 | 0 | 724.3305 | 0 | 0 | 0
2318 | 92.708 | 236.6 | 1005.5214 | 96.3055 | 0 | 0 | 909.2159 | 0 | 0 | 0
2319 | 86.801 | 226.85 | 971.404 | 90.1693 | 0 | 0 | 881.2347 | 0 | 0 | 0
2320 | 98.247 | 46.09 | 170.7431 | 102.0595 | 0 | 0 | 68.6837 | 0 | 0 | 0
2321 | 88.18 | 112.12 | 475.2251 | 91.6018 | 0 | 0 | 383.6233 | 0 | 0 | 0
2322 | 94.896 | 28.42 | 92.329 | 92.329 | 0 | 0 | 0 | 0 | 0 | 6.2494
2323 | 102.069 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.0298
2324 | 104.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.8667
2325 | 103.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 107.2047
2326 | 111.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 115.5151
2327 | 101.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.5426
2328 | 107.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 111.3599
2329 | 96.8 | 0 | 0 | 0 | 0 | 0 | 0 | 96.8 | 0 | 0
2330 | 103.2 | 0 | 0 | 0 | 0 | 0 | 0 | 103.2 | 0 | 0
2331 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0
2332 | 101.6 | 0 | 0 | 0 | 0 | 0 | 0 | 37.411 | 0 | 66.6798
2333 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.7253
2334 | 101.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.5426
2335 | 90.638 | 79.4 | 312.3302 | 94.1552 | -218.175 | 0 | 0 | 0 | 0 | 0
2336 | 142.371 | 270.3 | 1208.4073 | 147.8957 | -614.9724 | 0 | 445.5392 | 0 | 0 | 0
2337 | 876.805 | 489.22 | 2160.4791 | 910.8292 | -204.8637 | 0 | 1044.7862 | 0 | 0 | 0
2338 | 1186.13 | 558.68 | 2404.5671 | 1232.1575 | 0 | 0 | 1172.4096 | 0 | 0 | 0
2339 | 1409.196 | 607.38 | 2576.5111 | 1463.8795 | 0 | 0 | 1112.6316 | 0 | 0 | 0
2340 | 1645.065 | 985.6 | 4101.9678 | 1708.9013 | 0 | 0 | 2393.0665 | 0 | 0 | 0
2341 | 1551.507 | 508.85 | 2157.4157 | 1611.7128 | 0 | 0 | 545.7028 | 0 | 0 | 0
2342 | 1454.836 | 642.64 | 2727.4598 | 1511.2905 | 0 | 0 | 1216.1692 | 0 | 0 | 0
2343 | 1456.702 | 402.07 | 1742.0101 | 1513.229 | 0 | 0 | 228.7812 | 0 | 0 | 0
2344 | 1631.387 | 192.85 | 834.0574 | 834.0574 | 0 | 0 | 0 | 828.486 | 0 | 0
2345 | 1631.553 | 217.44 | 959.2801 | 959.2801 | 0 | 0 | 0 | 708.107 | 0 | 0
2346 | 1765.931 | 52.23 | 188.9285 | 188.9285 | 0 | 0 | 0 | 1584.06 | 0 | 0
2347 | 1730.86 | 0 | 0 | 0 | 0 | 0 | 0 | 1730.86 | 0 | 0
2348 | 1846.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1846.4 | 0 | 0
2349 | 1725.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1725.6 | 0 | 0
2350 | 1554.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1248.526 | 0 | 317.7434
2351 | 1998.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1406.4 | 0 | 614.9724
2352 | 1700.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1700.8 | 0 | 0
2353 | 1940.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1940.8 | 0 | 0
2354 | 1621.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1621.6 | 0 | 0
2355 | 1272.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1272.8 | 0 | 0
2356 | 1277.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1277.6 | 0 | 0
2357 | 1742.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1742.4 | 0 | 0
2358 | 1696 | 0 | 0 | 0 | 0 | 0 | 0 | 1696 | 0 | 0
2359 | 1093.028 | 97.44 | 370.8969 | 370.8969 | 0 | 0 | 0 | 735.986 | 0 | 0
2360 | 1153.367 | 332.82 | 1470.0427 | 1198.1231 | -271.9196 | 0 | 0 | 0 | 0 | 0
2361 | 1724.16 | 579.52 | 2503.8633 | 1791.0656 | -614.9724 | 0 | 97.8253 | 0 | 0 | 0
2362 | 2138.256 | 789.18 | 3218.588 | 2221.2305 | -151.1191 | 0 | 846.2384 | 0 | 0 | 0
2363 | 1900.048 | 943.98 | 3708.9828 | 1973.7789 | 0 | 0 | 1735.2039 | 0 | 0 | 0
2364 | 2133.191 | 1016.44 | 3955.2709 | 2215.9689 | 0 | 0 | 1739.302 | 0 | 0 | 0
2365 | 1700.026 | 1008.05 | 3973.9008 | 1765.9951 | 0 | 0 | 2207.9057 | 0 | 0 | 0
2366 | 1540.681 | 917.65 | 3740.5697 | 1600.4667 | 0 | 0 | 2140.103 | 0 | 0 | 0
2367 | 1354.534 | 758.21 | 3214.2593 | 1407.0964 | 0 | 0 | 1807.1629 | 0 | 0 | 0
2368 | 1652.807 | 544.14 | 2400.1791 | 1716.9438 | 0 | 0 | 683.2354 | 0 | 0 | 0
2369 | 1811.042 | 298.25 | 1291.0317 | 1291.0317 | 0 | 0 | 0 | 568.237 | 0 | 0
2370 | 1517.038 | 71.12 | 233.0236 | 233.0236 | 0 | 0 | 0 | 1292.719 | 0 | 0
2371 | 1866.297 | 0 | 0 | 0 | 0 | 0 | 0 | 1866.297 | 0 | 0
2372 | 1745.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1745.6 | 0 | 0
2373 | 2057.6 | 0 | 0 | 0 | 0 | 0 | 0 | 2057.6 | 0 | 0
2374 | 1675.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1369.326 | 0 | 317.7434
2375 | 1663.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1071.2 | 0 | 614.9724
2376 | 1429.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1429.6 | 0 | 0
2377 | 1479.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1479.2 | 0 | 0
2378 | 1613.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1613.6 | 0 | 0
2379 | 1020.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1020.8 | 0 | 0
2380 | 1254.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1254.4 | 0 | 0
2381 | 1267.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1267.2 | 0 | 0
2382 | 1392 | 0 | 0 | 0 | 0 | 0 | 0 | 1392 | 0 | 0
2383 | 1293.522 | 104.26 | 382.9429 | 382.9429 | 0 | 0 | 0 | 924.884 | 0 | 0
2384 | 650.269 | 340.09 | 1518.6972 | 675.5025 | -614.9724 | 0 | 228.2223 | 0 | 0 | 0
2385 | 1468.701 | 582.57 | 2603.4255 | 1525.6936 | -423.0387 | 0 | 654.6932 | 0 | 0 | 0
2386 | 1476.864 | 785.28 | 3394.7246 | 1534.1733 | 0 | 0 | 1860.5512 | 0 | 0 | 0
2387 | 1368.496 | 906.82 | 3833.23 | 1421.6001 | 0 | 0 | 2411.6299 | 0 | 0 | 0
2388 | 1103.419 | 980.41 | 4101.1108 | 1146.2369 | 0 | 0 | 2954.8739 | 0 | 0 | 0
2389 | 1738.664 | 975.3 | 4088.6908 | 1806.1324 | 0 | 0 | 2282.5584 | 0 | 0 | 0
2390 | 1353.651 | 882.48 | 3756.0292 | 1406.1791 | 0 | 0 | 2349.8501 | 0 | 0 | 0
2391 | 1671.773 | 734.34 | 3198.3323 | 1736.6457 | 0 | 0 | 1461.6866 | 0 | 0 | 0
2392 | 1643.7 | 527.6 | 2360.9757 | 1707.4834 | 0 | 0 | 653.4923 | 0 | 0 | 0
2393 | 1554.145 | 290.62 | 1269.5108 | 1269.5108 | 0 | 0 | 0 | 332.057 | 0 | 0
2394 | 1624.376 | 67.8 | 230.7996 | 230.7996 | 0 | 0 | 0 | 1402.198 | 0 | 0
2395 | 1597.412 | 0 | 0 | 0 | 0 | 0 | 0 | 1597.412 | 0 | 0
2396 | 1305.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1305.6 | 0 | 0
2397 | 1634.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1634.4 | 0 | 0
2398 | 1851.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1545.326 | 0 | 317.7434
2399 | 1613.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1021.6 | 0 | 614.9724
2400 | 1363.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1363.2 | 0 | 0
2401 | 1245.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1245.6 | 0 | 0
2402 | 1235.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1235.2 | 0 | 0
2403 | 1324 | 0 | 0 | 0 | 0 | 0 | 0 | 1324 | 0 | 0
2404 | 1393.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1393.6 | 0 | 0
2405 | 1192 | 0 | 0 | 0 | 0 | 0 | 0 | 1192 | 0 | 0
2406 | 1108 | 0 | 0 | 0 | 0 | 0 | 0 | 1108 | 0 | 0
2407 | 1071.458 | 97.02 | 377.8517 | 377.8517 | 0 | 0 | 0 | 707.721 | 0 | 0
2408 | 700.377 | 328.02 | 1467.3636 | 727.555 | -614.9724 | 0 | 124.8363 | 0 | 0 | 0
2409 | 1179.725 | 386.24 | 1697.0693 | 1225.5039 | -423.0387 | 0 | 48.5267 | 0 | 0 | 0
2410 | 1627.857 | 368.74 | 1576.1161 | 1576.1161 | 0 | 0 | 0 | 0 | 0 | 114.9095
2411 | 1504.309 | 581.29 | 2409.6354 | 1562.6833 | -127.881 | 0 | 719.071 | 0 | 0 | 0
2412 | 1607.655 | 621.67 | 2530.5055 | 1670.0396 | 0 | 0 | 860.4659 | 0 | 0 | 0
2413 | 1708.11 | 987.25 | 3920.7213 | 1774.3928 | 0 | 0 | 2146.3285 | 0 | 0 | 0
2414 | 1747.615 | 685.98 | 2808.8719 | 1815.4308 | 0 | 0 | 993.4412 | 0 | 0 | 0
2415 | 1656.806 | 468.88 | 1979.4217 | 1721.0979 | 0 | 0 | 258.3237 | 0 | 0 | 0
2416 | 1940.668 | 274.14 | 1178.9852 | 1178.9852 | 0 | 0 | 0 | 805.724 | 0 | 0
2417 | 1471.768 | 282.34 | 1218.946 | 1218.946 | 0 | 0 | 0 | 298.356 | 0 | 0
2418 | 1831.384 | 62.93 | 215.311 | 215.311 | 0 | 0 | 0 | 1624.116 | 0 | 0
2419 | 1741.725 | 0 | 0 | 0 | 0 | 0 | 0 | 1741.725 | 0 | 0
2420 | 1332.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1332.8 | 0 | 0
2421 | 1913.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1913.6 | 0 | 0
2422 | 1916 | 0 | 0 | 0 | 0 | 0 | 0 | 1610.126 | 0 | 317.7434
2423 | 1797.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1205.6 | 0 | 614.9724
2424 | 1308 | 0 | 0 | 0 | 0 | 0 | 0 | 1308 | 0 | 0
2425 | 1379.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1379.2 | 0 | 0
2426 | 1590.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1590.4 | 0 | 0
2427 | 1549.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1549.6 | 0 | 0
2428 | 934.4 | 0 | 0 | 0 | 0 | 0 | 0 | 934.4 | 0 | 0
2429 | 1459.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1459.2 | 0 | 0
2430 | 1591.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1591.2 | 0 | 0
2431 | 966.93 | 95.97 | 369.2525 | 369.2525 | 0 | 0 | 0 | 611.471 | 0 | 0
2432 | 1477.577 | 321.15 | 1418.7393 | 1418.7393 | 0 | 0 | 0 | 111.835 | 0 | 0
2433 | 1354.983 | 553.21 | 2401.2439 | 1407.5628 | -614.9724 | 0 | 378.7087 | 0 | 0 | 0
2434 | 1698.036 | 751.57 | 3126.3826 | 1763.9279 | -423.0387 | 0 | 939.4161 | 0 | 0 | 0
2435 | 1687.35 | 905.08 | 3638.1041 | 1752.8272 | 0 | 0 | 1885.2769 | 0 | 0 | 0
2436 | 1799.841 | 973.93 | 3853.8399 | 1869.6834 | 0 | 0 | 1984.1565 | 0 | 0 | 0
2437 | 1492.56 | 966.45 | 3854.5089 | 1550.4784 | 0 | 0 | 2304.0305 | 0 | 0 | 0
2438 | 1614.825 | 872.66 | 3583.5585 | 1677.4879 | 0 | 0 | 1906.0706 | 0 | 0 | 0
2439 | 1802.673 | 721.65 | 3072.3939 | 1872.6253 | 0 | 0 | 1199.7686 | 0 | 0 | 0
2440 | 1703.159 | 399.91 | 1743.5953 | 1743.5953 | 0 | 0 | 0 | 24.696 | 0 | 0
2441 | 1953.342 | 159.24 | 685.9238 | 685.9238 | 0 | 0 | 0 | 1293.041 | 0 | 0
2442 | 1610.257 | 35.22 | 120.5626 | 120.5626 | 0 | 0 | 0 | 1494.198 | 0 | 0
2443 | 1843.247 | 0 | 0 | 0 | 0 | 0 | 0 | 1843.247 | 0 | 0
2444 | 1636 | 0 | 0 | 0 | 0 | 0 | 0 | 1636 | 0 | 0
2445 | 1706.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1706.4 | 0 | 0
2446 | 2003.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1697.326 | 0 | 317.7434
2447 | 1822.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1230.4 | 0 | 614.9724
2448 | 1698.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1698.4 | 0 | 0
2449 | 1377.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1377.6 | 0 | 0
2450 | 1225.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1225.6 | 0 | 0
2451 | 1188 | 0 | 0 | 0 | 0 | 0 | 0 | 1188 | 0 | 0
2452 | 1199.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1199.2 | 0 | 0
2453 | 1212 | 0 | 0 | 0 | 0 | 0 | 0 | 1212 | 0 | 0
2454 | 1070.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1070.4 | 0 | 0
2455 | 974.019 | 58.68 | 231.8758 | 231.8758 | 0 | 0 | 0 | 750.805 | 0 | 0
2456 | 196.406 | 205.62 | 905.605 | 204.0275 | -614.9724 | 0 | 86.6052 | 0 | 0 | 0
2457 | 173.54 | 542.78 | 2349.0055 | 180.2742 | -423.0387 | 0 | 1745.6927 | 0 | 0 | 0
2458 | 0 | 745.51 | 3086.9485 | 0 | 0 | 0 | 3086.9485 | 0 | 0 | 0
2459 | 0 | 891.18 | 3586.2438 | 0 | 0 | 0 | 3586.2438 | 0 | 0 | 0
2460 | 0 | 721.5 | 2932.1438 | 0 | 0 | 0 | 2932.1438 | 0 | 0 | 0
2461 | 0 | 795.66 | 3239.5064 | 0 | 0 | 0 | 3239.5064 | 0 | 0 | 0
2462 | 267.984 | 534.78 | 2245.3983 | 278.3831 | 0 | 0 | 1967.0152 | 0 | 0 | 0
2463 | 256.129 | 721.8 | 3105.4123 | 266.068 | 0 | 0 | 2839.3442 | 0 | 0 | 0
2464 | 126.647 | 513.79 | 2279.6581 | 131.5615 | 0 | 0 | 2148.0966 | 0 | 0 | 0
2465 | 227.812 | 278.45 | 1214.2568 | 236.6522 | 0 | 0 | 977.6046 | 0 | 0 | 0
2466 | 353.747 | 61.88 | 215.1396 | 215.1396 | 0 | 0 | 0 | 146.644 | 0 | 0
2467 | 216.663 | 0 | 0 | 0 | 0 | 0 | 0 | 26.789 | 0 | 197.242
2468 | 193.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 201.1126
2469 | 127.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132.136
2470 | 117.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 122.1634
2471 | 128.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133.7981
2472 | 140.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 146.2637
2473 | 108.8 | 0 | 0 | 0 | 0 | 0 | 0 | 108.8 | 0 | 0
2474 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0
2475 | 89.6 | 0 | 0 | 0 | 0 | 0 | 0 | 89.6 | 0 | 0
2476 | 99.2 | 0 | 0 | 0 | 0 | 0 | 0 | 99.2 | 0 | 0
2477 | 91.2 | 0 | 0 | 0 | 0 | 0 | 0 | 91.2 | 0 | 0
2478 | 98.4 | 0 | 0 | 0 | 0 | 0 | 0 | 98.4 | 0 | 0
2479 | 64.271 | 92.42 | 363.699 | 66.765 | -296.934 | 0 | 0 | 0 | 0 | 0
2480 | 44.716 | 317.64 | 1414.4397 | 46.4512 | -614.9724 | 0 | 753.0161 | 0 | 0 | 0
2481 | 503.248 | 463.77 | 2036.2256 | 522.7764 | -126.1047 | 0 | 1387.3445 | 0 | 0 | 0
2482 | 593.572 | 619.03 | 2634.4151 | 616.6054 | 0 | 0 | 2017.8097 | 0 | 0 | 0
2483 | 451.248 | 468.83 | 1982.3376 | 468.7586 | 0 | 0 | 1513.579 | 0 | 0 | 0
2484 | 445.515 | 977.16 | 4043.5496 | 462.8031 | 0 | 0 | 3580.7465 | 0 | 0 | 0
2485 | 1718.709 | 653.08 | 2748.5673 | 1785.4031 | 0 | 0 | 963.1642 | 0 | 0 | 0
2486 | 1825.482 | 674.33 | 2865.9896 | 1896.3194 | 0 | 0 | 969.6702 | 0 | 0 | 0
2487 | 1311.2 | 499.71 | 2167.6998 | 1362.0808 | 0 | 0 | 805.6191 | 0 | 0 | 0
2488 | 1571.2 | 442.18 | 1961.0057 | 1632.17 | 0 | 0 | 328.8357 | 0 | 0 | 0
2489 | 1255.2 | 273.76 | 1200.69 | 1200.69 | 0 | 0 | 0 | 99.362 | 0 | 0
2490 | 1663.487 | 59.72 | 207.1377 | 207.1377 | 0 | 0 | 0 | 1464.087 | 0 | 0
2491 | 1610.935 | 0 | 0 | 0 | 0 | 0 | 0 | 1610.935 | 0 | 0
2492 | 1180.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1180.8 | 0 | 0
2493 | 1295.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1295.2 | 0 | 0
2494 | 1408 | 0 | 0 | 0 | 0 | 0 | 0 | 1102.126 | 0 | 317.7434
2495 | 1508 | 0 | 0 | 0 | 0 | 0 | 0 | 916 | 0 | 614.9724
2496 | 1367.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1367.2 | 0 | 0
2497 | 1770.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1770.4 | 0 | 0
2498 | 1622.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1622.4 | 0 | 0
2499 | 1314.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1314.4 | 0 | 0
2500 | 1200.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1200.8 | 0 | 0
2501 | 1348 | 0 | 0 | 0 | 0 | 0 | 0 | 1348 | 0 | 0
2502 | 1156 | 0 | 0 | 0 | 0 | 0 | 0 | 1156 | 0 | 0
2503 | 1375.182 | 102.64 | 397.6337 | 397.6337 | 0 | 0 | 0 | 992.402 | 0 | 0
2504 | 1228.928 | 331.06 | 1475.4954 | 1276.6162 | -198.8792 | 0 | 0 | 0 | 0 | 0
2505 | 1763.437 | 565.97 | 2512.0833 | 1831.8667 | -614.9724 | 0 | 65.2442 | 0 | 0 | 0
2506 | 1786.454 | 111.22 | 455.5855 | 455.5855 | 0 | 0 | 0 | 755.887 | 0 | 614.9724
2507 | 1601.327 | 903.17 | 3775.0248 | 1663.4661 | -614.9724 | 0 | 1496.5863 | 0 | 0 | 0
2508 | 1886.909 | 975.44 | 4009.4965 | 1960.129 | -293.5849 | 0 | 1755.7826 | 0 | 0 | 0
2509 | 1830.371 | 452.51 | 1902.1024 | 1901.3981 | 0 | 0 | 0.70431 | 0 | 0 | 0
2510 | 1393.734 | 892.15 | 3723.6081 | 1447.8175 | 0 | 0 | 2275.7906 | 0 | 0 | 0
2511 | 1534.199 | 504.69 | 2160.502 | 1593.7332 | 0 | 0 | 566.7688 | 0 | 0 | 0
2512 | 1641.378 | 404.03 | 1771.7282 | 1705.0713 | 0 | 0 | 66.657 | 0 | 0 | 0
2513 | 1522.665 | 231.4 | 1014.8426 | 1014.8426 | 0 | 0 | 0 | 545.732 | 0 | 0
2514 | 1554.326 | 64.93 | 223.638 | 223.638 | 0 | 0 | 0 | 1339.042 | 0 | 0
2515 | 1267.674 | 0 | 0 | 0 | 0 | 0 | 0 | 1267.674 | 0 | 0
2516 | 1214.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1214.4 | 0 | 0
2517 | 1422.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1422.4 | 0 | 0
2518 | 1226.4 | 0 | 0 | 0 | 0 | 0 | 0 | 920.526 | 0 | 317.7434
2519 | 1222.4 | 0 | 0 | 0 | 0 | 0 | 0 | 630.4 | 0 | 614.9724
2520 | 1440.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1440.8 | 0 | 0
2521 | 1159.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1159.2 | 0 | 0
2522 | 1145.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1145.6 | 0 | 0
2523 | 1368.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1368.8 | 0 | 0
2524 | 864.8 | 0 | 0 | 0 | 0 | 0 | 0 | 864.8 | 0 | 0
2525 | 943.2 | 0 | 0 | 0 | 0 | 0 | 0 | 943.2 | 0 | 0
2526 | 1092 | 0 | 0 | 0 | 0 | 0 | 0 | 1092 | 0 | 0
2527 | 1156.517 | 91.39 | 365.5086 | 365.5086 | 0 | 0 | 0 | 804.662 | 0 | 0
2528 | 715.847 | 332.81 | 1477.518 | 743.6253 | -614.9724 | 0 | 118.9203 | 0 | 0 | 0
2529 | 1374.694 | 473.93 | 2066.1265 | 1428.0387 | -423.0387 | 0 | 215.0492 | 0 | 0 | 0
2530 | 1474.584 | 654.37 | 2755.4504 | 1531.8049 | 0 | 0 | 1223.6455 | 0 | 0 | 0
2531 | 1171.084 | 907.03 | 3723.5842 | 1216.5276 | 0 | 0 | 2507.0566 | 0 | 0 | 0
2532 | 1452.682 | 972.61 | 3941.113 | 1509.053 | 0 | 0 | 2432.0601 | 0 | 0 | 0
2533 | 1536.423 | 804.98 | 3286.7055 | 1596.0435 | 0 | 0 | 1690.662 | 0 | 0 | 0
2534 | 1489.362 | 723.63 | 3019.1271 | 1547.1563 | 0 | 0 | 1471.9707 | 0 | 0 | 0
2535 | 1094.152 | 590.88 | 2537.0406 | 1136.6103 | 0 | 0 | 1400.4303 | 0 | 0 | 0
2536 | 1400.201 | 416.34 | 1836.5517 | 1454.5354 | 0 | 0 | 382.0163 | 0 | 0 | 0
2537 | 1681.075 | 221.86 | 976.3539 | 976.3539 | 0 | 0 | 0 | 741.193 | 0 | 0
2538 | 1647.588 | 53.62 | 192.5061 | 192.5061 | 0 | 0 | 0 | 1462.273 | 0 | 0
2539 | 1122.777 | 0 | 0 | 0 | 0 | 0 | 0 | 1122.777 | 0 | 0
2540 | 1656 | 0 | 0 | 0 | 0 | 0 | 0 | 1656 | 0 | 0
2541 | 1400.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1400.8 | 0 | 0
2542 | 1624.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1318.926 | 0 | 317.7434
2543 | 1046.4 | 0 | 0 | 0 | 0 | 0 | 0 | 454.4 | 0 | 614.9724
2544 | 1645.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1645.6 | 0 | 0
2545 | 1430.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1430.4 | 0 | 0
2546 | 1149.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1149.6 | 0 | 0
2547 | 1410.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1410.4 | 0 | 0
2548 | 1274.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.4 | 0 | 0
2549 | 1276.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1276.8 | 0 | 0
2550 | 1566.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1566.4 | 0 | 0
2551 | 1491.966 | 36.26 | 132.5681 | 132.5681 | 0 | 0 | 0 | 1364.35 | 0 | 0
2552 | 1493.014 | 124.33 | 534.9273 | 534.9273 | 0 | 0 | 0 | 978.069 | 0 | 0
2553 | 1539.824 | 426.25 | 1872.8933 | 1599.5765 | -273.3168 | 0 | 0 | 0 | 0 | 0
2554 | 1782.499 | 755.01 | 3230.9601 | 1851.6684 | -614.9724 | 0 | 764.3193 | 0 | 0 | 0
2555 | 1835.337 | 904.09 | 3761.2918 | 1906.5558 | -149.7229 | 0 | 1705.0131 | 0 | 0 | 0
2556 | 1632.697 | 974.69 | 3993.7067 | 1696.0534 | 0 | 0 | 2297.6533 | 0 | 0 | 0
2557 | 1766.248 | 966.17 | 3954.3786 | 1834.7868 | 0 | 0 | 2119.5918 | 0 | 0 | 0
2558 | 1904.871 | 878.42 | 3652.8883 | 1978.789 | 0 | 0 | 1674.0993 | 0 | 0 | 0
2559 | 1996.523 | 725.12 | 3096.8546 | 2073.9976 | 0 | 0 | 1022.857 | 0 | 0 | 0
2560 | 1909.872 | 447.53 | 1952.8148 | 1952.8148 | 0 | 0 | 0 | 30.005 | 0 | 0
2561 | 1550.773 | 64.95 | 256.7385 | 256.7385 | 0 | 0 | 0 | 1303.625 | 0 | 0
2562 | 1749.963 | 17.63 | 46.0637 | 46.0637 | 0 | 0 | 0 | 1705.62 | 0 | 0
2563 | 2041.861 | 0 | 0 | 0 | 0 | 0 | 0 | 2041.861 | 0 | 0
2564 | 1636 | 0 | 0 | 0 | 0 | 0 | 0 | 1636 | 0 | 0
2565 | 1492.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1492.8 | 0 | 0
2566 | 1684 | 0 | 0 | 0 | 0 | 0 | 0 | 1378.126 | 0 | 317.7434
2567 | 1725.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1133.6 | 0 | 614.9724
2568 | 1603.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1603.2 | 0 | 0
2569 | 792 | 0 | 0 | 0 | 0 | 0 | 0 | 792 | 0 | 0
2570 | 863.2 | 0 | 0 | 0 | 0 | 0 | 0 | 863.2 | 0 | 0
2571 | 843.2 | 0 | 0 | 0 | 0 | 0 | 0 | 843.2 | 0 | 0
2572 | 594.4 | 0 | 0 | 0 | 0 | 0 | 0 | 594.4 | 0 | 0
2573 | 836 | 0 | 0 | 0 | 0 | 0 | 0 | 836 | 0 | 0
2574 | 635.2 | 0 | 0 | 0 | 0 | 0 | 0 | 635.2 | 0 | 0
2575 | 612.699 | 36.26 | 132.7156 | 132.7156 | 0 | 0 | 0 | 484.941 | 0 | 0
2576 | 532.414 | 123.36 | 528.7942 | 528.7942 | 0 | 0 | 0 | 23.373 | 0 | 0
2577 | 903.735 | 497.07 | 2166.0855 | 938.8042 | -614.9724 | 0 | 612.3089 | 0 | 0 | 0
2578 | 888.082 | 491.79 | 2094.4132 | 922.5438 | -423.0387 | 0 | 748.8307 | 0 | 0 | 0
2579 | 1104.242 | 917.69 | 3799.7151 | 1147.0918 | 0 | 0 | 2652.6232 | 0 | 0 | 0
2580 | 873.013 | 984.98 | 4034.2938 | 906.89 | 0 | 0 | 3127.4038 | 0 | 0 | 0
2581 | 777.272 | 977.02 | 4010.6859 | 807.4338 | 0 | 0 | 3203.2521 | 0 | 0 | 0
2582 | 991.14 | 895.3 | 3739.186 | 1029.6009 | 0 | 0 | 2709.5851 | 0 | 0 | 0
2583 | 976.907 | 738.94 | 3171.1167 | 1014.8156 | 0 | 0 | 2156.301 | 0 | 0 | 0
2584 | 874.205 | 525.47 | 2326.8104 | 908.1283 | 0 | 0 | 1418.6821 | 0 | 0 | 0
2585 | 861.226 | 285.86 | 1232.5304 | 894.6457 | 0 | 0 | 337.8847 | 0 | 0 | 0
2586 | 364.693 | 66.53 | 222.9576 | 222.9576 | 0 | 0 | 0 | 150.064 | 0 | 0
2587 | 407.546 | 0 | 0 | 0 | 0 | 0 | 0 | 407.546 | 0 | 0
2588 | 380.8 | 0 | 0 | 0 | 0 | 0 | 0 | 380.8 | 0 | 0
2589 | 503.2 | 0 | 0 | 0 | 0 | 0 | 0 | 503.2 | 0 | 0
2590 | 686.4 | 0 | 0 | 0 | 0 | 0 | 0 | 380.526 | 0 | 317.7434
2591 | 699.2 | 0 | 0 | 0 | 0 | 0 | 0 | 107.2 | 0 | 614.9724
2592 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2593 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2594 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2595 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2596 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2597 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2598 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2599 | 1576.944 | 111.5 | 417.3751 | 417.3751 | 0 | 0 | 0 | 1175.16 | 0 | 0
2600 | 1498.248 | 343.51 | 1518.4375 | 1518.4375 | 0 | 0 | 0 | 36.532 | 0 | 0
2601 | 1510.044 | 579.45 | 2547.1534 | 1568.6409 | -614.9724 | 0 | 363.5401 | 0 | 0 | 0
2602 | 1902.362 | 776.59 | 3308.9775 | 1976.1827 | -423.0387 | 0 | 909.7561 | 0 | 0 | 0
2603 | 1884.636 | 928.47 | 3870.6187 | 1957.7688 | 0 | 0 | 1912.8499 | 0 | 0 | 0
2604 | 1594.663 | 994.81 | 4116.5755 | 1656.5435 | 0 | 0 | 2460.032 | 0 | 0 | 0
2605 | 1945.081 | 983.44 | 4093.3696 | 2020.5594 | 0 | 0 | 2072.8102 | 0 | 0 | 0
2606 | 1916.271 | 883.7 | 3735.7143 | 1990.6314 | 0 | 0 | 1745.0829 | 0 | 0 | 0
2607 | 2098.686 | 729.05 | 3156.5028 | 2180.125 | 0 | 0 | 976.3778 | 0 | 0 | 0
2608 | 1693.969 | 457.6 | 2013.2379 | 1759.703 | 0 | 0 | 253.5348 | 0 | 0 | 0
2609 | 2117.631 | 188.13 | 818.6571 | 818.6571 | 0 | 0 | 0 | 1329.555 | 0 | 0
2610 | 2089.833 | 45.69 | 163.8351 | 163.8351 | 0 | 0 | 0 | 1932.118 | 0 | 0
2611 | 1694.447 | 0 | 0 | 0 | 0 | 0 | 0 | 1694.447 | 0 | 0
2612 | 1517.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1517.6 | 0 | 0
2613 | 1688.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1688.8 | 0 | 0
2614 | 1653.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1347.726 | 0 | 317.7434
2615 | 1461.6 | 0 | 0 | 0 | 0 | 0 | 0 | 869.6 | 0 | 614.9724
2616 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2617 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2618 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2620 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2621 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2623 | 601.179 | 114.55 | 429.9 | 429.9 | 0 | 0 | 0 | 187.338 | 0 | 0
2624 | 322.859 | 344.71 | 1527.3847 | 335.3875 | -614.9724 | 0 | 577.0249 | 0 | 0 | 0
2625 | 345.786 | 580.41 | 2561.2946 | 359.2052 | -423.0387 | 0 | 1779.0508 | 0 | 0 | 0
2626 | 329.02 | 777.06 | 3315.1812 | 341.7875 | 0 | 0 | 2973.3937 | 0 | 0 | 0
2627 | 281.969 | 913.22 | 3801.3772 | 292.9107 | 0 | 0 | 3508.4664 | 0 | 0 | 0
2628 | 315.114 | 982.14 | 4047.1095 | 327.3419 | 0 | 0 | 3719.7676 | 0 | 0 | 0
2629 | 313.792 | 972.7 | 4029.989 | 325.9686 | 0 | 0 | 3704.0204 | 0 | 0 | 0
2630 | 298.368 | 859.73 | 3623.3427 | 309.9461 | 0 | 0 | 3313.3966 | 0 | 0 | 0
2631 | 287.073 | 709.76 | 3073.5594 | 298.2128 | 0 | 0 | 2775.3466 | 0 | 0 | 0
2632 | 258.151 | 508.01 | 2263.9264 | 268.1685 | 0 | 0 | 1995.7579 | 0 | 0 | 0
2633 | 315.607 | 276.11 | 1197.5912 | 327.8541 | 0 | 0 | 869.7372 | 0 | 0 | 0
2634 | 311.492 | 62.49 | 209.9591 | 209.9591 | 0 | 0 | 0 | 109.376 | 0 | 0
2635 | 272.738 | 0 | 0 | 0 | 0 | 0 | 0 | 272.738 | 0 | 0
2636 | 274.4 | 0 | 0 | 0 | 0 | 0 | 0 | 130.926 | 0 | 149.0415
2637 | 260.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270.9203
2638 | 225.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 234.3544
2639 | 268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 278.3997
2640 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2641 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2643 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2646 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2647 | 39.491 | 99.63 | 395.8947 | 41.0234 | -354.8713 | 0 | 0 | 0 | 0 | 0
2648 | 37.99 | 326.79 | 1439.077 | 39.4642 | -614.9724 | 0 | 784.6404 | 0 | 0 | 0
2649 | 302.112 | 563.69 | 2435.1962 | 313.8354 | -68.1674 | 0 | 2053.1934 | 0 | 0 | 0
2650 | 565.025 | 763.87 | 3151.4105 | 586.9507 | 0 | 0 | 2564.4599 | 0 | 0 | 0
2651 | 324.56 | 469.1 | 1942.6542 | 337.1545 | 0 | 0 | 1605.4997 | 0 | 0 | 0
2652 | 314.692 | 982.14 | 3928.8125 | 326.9035 | 0 | 0 | 3601.909 | 0 | 0 | 0
2653 | 593.521 | 434.09 | 1801.0558 | 616.5524 | 0 | 0 | 1184.5033 | 0 | 0 | 0
2654 | 606.677 | 866.61 | 3590.5081 | 630.2189 | 0 | 0 | 2960.2892 | 0 | 0 | 0
2655 | 413.157 | 384.17 | 1631.2112 | 429.1895 | 0 | 0 | 1202.0218 | 0 | 0 | 0
2656 | 615.896 | 502.17 | 2210.8134 | 639.7957 | 0 | 0 | 1571.0177 | 0 | 0 | 0
2657 | 592.271 | 269.87 | 1164.3183 | 615.2539 | 0 | 0 | 549.0644 | 0 | 0 | 0
2658 | 583.145 | 57.22 | 196.8535 | 196.8535 | 0 | 0 | 0 | 393.645 | 0 | 0
2659 | 752.979 | 0 | 0 | 0 | 0 | 0 | 0 | 752.979 | 0 | 0
2660 | 606.4 | 0 | 0 | 0 | 0 | 0 | 0 | 606.4 | 0 | 0
2661 | 505.6 | 0 | 0 | 0 | 0 | 0 | 0 | 505.6 | 0 | 0
2662 | 594.4 | 0 | 0 | 0 | 0 | 0 | 0 | 288.526 | 0 | 317.7434
2663 | 668.8 | 0 | 0 | 0 | 0 | 0 | 0 | 76.8 | 0 | 614.9724
2664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2665 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2666 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2668 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2669 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2670 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2671 | 1652.413 | 114.55 | 430.2023 | 430.2023 | 0 | 0 | 0 | 1238.281 | 0 | 0
2672 | 1082.942 | 348.14 | 1526.4862 | 1124.9653 | -401.5209 | 0 | 0 | 0 | 0 | 0
2673 | 1038.061 | 588.11 | 2562.1994 | 1078.3427 | -614.9724 | 0 | 868.8843 | 0 | 0 | 0
2674 | 1455.5 | 789.28 | 3311.1662 | 1511.9813 | -21.5178 | 0 | 1777.6671 | 0 | 0 | 0
2675 | 1822.657 | 917.6 | 3743.3256 | 1893.3847 | 0 | 0 | 1849.9409 | 0 | 0 | 0
2676 | 1569.698 | 984.07 | 3977.815 | 1630.6097 | 0 | 0 | 2347.2053 | 0 | 0 | 0
2677 | 1627.187 | 974.24 | 3961.3157 | 1690.3296 | 0 | 0 | 2270.9861 | 0 | 0 | 0
2678 | 1849.064 | 884.51 | 3670.843 | 1920.8165 | 0 | 0 | 1750.0266 | 0 | 0 | 0
2679 | 1544.646 | 729.17 | 3110.385 | 1604.5856 | 0 | 0 | 1505.7994 | 0 | 0 | 0
2680 | 1277.5 | 520.66 | 2291.8702 | 1327.0731 | 0 | 0 | 964.7972 | 0 | 0 | 0
2681 | 1415.472 | 281.88 | 1204.4806 | 1204.4806 | 0 | 0 | 0 | 255.985 | 0 | 0
2682 | 1528.819 | 45.52 | 161.5466 | 161.5466 | 0 | 0 | 0 | 1373.307 | 0 | 0
2683 | 1597.596 | 0 | 0 | 0 | 0 | 0 | 0 | 1597.596 | 0 | 0
2684 | 1565.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1565.6 | 0 | 0
2685 | 1574.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.4 | 0 | 0
2686 | 2055.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1749.326 | 0 | 317.7434
2687 | 2027.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1435.2 | 0 | 614.9724
2688 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2690 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2691 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2693 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2694 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2695 | 1539.86 | 78.14 | 315.6834 | 315.6834 | 0 | 0 | 0 | 1235.969 | 0 | 0
2696 | 753.773 | 350.76 | 1539.8338 | 783.023 | -614.9724 | 0 | 141.8384 | 0 | 0 | 0
2697 | 1086.631 | 586.52 | 2548.6742 | 1128.7985 | -423.0387 | 0 | 996.837 | 0 | 0 | 0
2698 | 1522.957 | 786.68 | 3286.7169 | 1582.055 | 0 | 0 | 1704.662 | 0 | 0 | 0
2699 | 1186.075 | 930.62 | 3775.5982 | 1232.1003 | 0 | 0 | 2543.4978 | 0 | 0 | 0
2700 | 1273.679 | 998.5 | 4001.1933 | 1323.1038 | 0 | 0 | 2678.0895 | 0 | 0 | 0
2701 | 1087.344 | 990.03 | 3997.0423 | 1129.5381 | 0 | 0 | 2867.5042 | 0 | 0 | 0
2702 | 1231.626 | 898.87 | 3710.9762 | 1279.4189 | 0 | 0 | 2431.5573 | 0 | 0 | 0
2703 | 1034.934 | 742.55 | 3166.7464 | 1075.0944 | 0 | 0 | 2091.6521 | 0 | 0 | 0
2704 | 806.512 | 532.68 | 2350.437 | 837.8085 | 0 | 0 | 1512.6285 | 0 | 0 | 0
2705 | 1209.862 | 196.76 | 849.3455 | 849.3455 | 0 | 0 | 0 | 392.244 | 0 | 0
2706 | 1026.622 | 54.7 | 193.092 | 193.092 | 0 | 0 | 0 | 840.743 | 0 | 0
2707 | 1116.444 | 0 | 0 | 0 | 0 | 0 | 0 | 1116.444 | 0 | 0
2708 | 1189.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1189.6 | 0 | 0
2709 | 1585.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1585.6 | 0 | 0
2710 | 1313.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1007.726 | 0 | 317.7434
2711 | 1244.8 | 0 | 0 | 0 | 0 | 0 | 0 | 652.8 | 0 | 614.9724
2712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2713 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2714 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2715 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2717 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2719 | 726.714 | 123.18 | 445.9329 | 445.9329 | 0 | 0 | 0 | 297.439 | 0 | 0
2720 | 674.256 | 29.4 | 100.0888 | 100.0888 | 0 | 0 | 0 | 577.906 | 0 | 0
2721 | 632.529 | 593.95 | 2632.351 | 657.0741 | -614.9724 | 0 | 1360.3044 | 0 | 0 | 0
2722 | 561.581 | 791.32 | 3401.9578 | 583.373 | -423.0387 | 0 | 2395.5461 | 0 | 0 | 0
2723 | 451.698 | 913.68 | 3845.3124 | 469.226 | 0 | 0 | 3376.0863 | 0 | 0 | 0
2724 | 423.123 | 980.08 | 4082.9369 | 439.5422 | 0 | 0 | 3643.3947 | 0 | 0 | 0
2725 | 1088.675 | 971.88 | 4050.2675 | 1130.9208 | 0 | 0 | 2919.3468 | 0 | 0 | 0
2726 | 1337.162 | 889.65 | 3765.2309 | 1389.0502 | 0 | 0 | 2376.1807 | 0 | 0 | 0
2727 | 1171.09 | 735.59 | 3188.5156 | 1216.5339 | 0 | 0 | 1971.9818 | 0 | 0 | 0
2728 | 1325.832 | 526.33 | 2348.2722 | 1377.2806 | 0 | 0 | 970.9916 | 0 | 0 | 0
2729 | 1450.922 | 288.5 | 1239.1549 | 1239.1549 | 0 | 0 | 0 | 258.056 | 0 | 0
2730 | 1693.945 | 67.16 | 211.4082 | 211.4082 | 0 | 0 | 0 | 1490.434 | 0 | 0
2731 | 1224.801 | 0 | 0 | 0 | 0 | 0 | 0 | 1224.801 | 0 | 0
2732 | 1521.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1521.6 | 0 | 0
2733 | 1564 | 0 | 0 | 0 | 0 | 0 | 0 | 1564 | 0 | 0
2734 | 1750.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1444.526 | 0 | 317.7434
2735 | 1775.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1183.2 | 0 | 614.9724
2736 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2737 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2740 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2741 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2742 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2743 | 1263.257 | 114.17 | 444.839 | 444.839 | 0 | 0 | 0 | 835.035 | 0 | 0
2744 | 953.993 | 341.64 | 1509.9391 | 991.0125 | -518.9266 | 0 | 0 | 0 | 0 | 0
2745 | 1386.66 | 572.9 | 2508.459 | 1440.47 | -519.0845 | 0 | 548.9044 | 0 | 0 | 0
2746 | 1396.16 | 771.71 | 3249.3885 | 1450.3376 | 0 | 0 | 1799.0509 | 0 | 0 | 0
2747 | 1632.597 | 923.27 | 3789.0642 | 1695.9495 | 0 | 0 | 2093.1147 | 0 | 0 | 0
2748 | 1604.417 | 991.5 | 4039.3029 | 1666.676 | 0 | 0 | 2372.6269 | 0 | 0 | 0
2749 | 1737.845 | 979.89 | 4024.5425 | 1805.2816 | 0 | 0 | 2219.2609 | 0 | 0 | 0
2750 | 1592.395 | 881.65 | 3690.0817 | 1654.1875 | 0 | 0 | 2035.8942 | 0 | 0 | 0
2751 | 1657.388 | 728.22 | 3132.6871 | 1721.7025 | 0 | 0 | 1410.9846 | 0 | 0 | 0
2752 | 1478.101 | 519.37 | 2300.3749 | 1535.4583 | 0 | 0 | 764.9166 | 0 | 0 | 0
2753 | 1658.613 | 225.3 | 977.9921 | 977.9921 | 0 | 0 | 0 | 717.154 | 0 | 0
2754 | 1608.759 | 54.45 | 192.5954 | 192.5954 | 0 | 0 | 0 | 1423.358 | 0 | 0
2755 | 1122.711 | 0 | 0 | 0 | 0 | 0 | 0 | 1122.711 | 0 | 0
2756 | 1280.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1280.8 | 0 | 0
2757 | 1492 | 0 | 0 | 0 | 0 | 0 | 0 | 1492 | 0 | 0
2758 | 1771.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1465.326 | 0 | 317.7434
2759 | 1771.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1179.2 | 0 | 614.9724
2760 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2761 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2763 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2765 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2767 | 1162.556 | 96.1 | 390.2883 | 390.2883 | 0 | 0 | 0 | 786.847 | 0 | 0
2768 | 970.887 | 317.45 | 1400.0564 | 1008.562 | -391.4943 | 0 | 0 | 0 | 0 | 0
2769 | 1196.422 | 541.59 | 2353.0153 | 1242.8489 | -614.9724 | 0 | 495.1941 | 0 | 0 | 0
2770 | 1332.16 | 736.83 | 3098.8003 | 1383.8541 | -31.5443 | 0 | 1683.4018 | 0 | 0 | 0
2771 | 1301.099 | 896.59 | 3669.6256 | 1351.5878 | 0 | 0 | 2318.0377 | 0 | 0 | 0
2772 | 1262.025 | 964.82 | 3904.3934 | 1310.9976 | 0 | 0 | 2593.3958 | 0 | 0 | 0
2773 | 1431.18 | 956.75 | 3895.4981 | 1486.7166 | 0 | 0 | 2408.7815 | 0 | 0 | 0
2774 | 1472.893 | 727.5 | 3014.9926 | 1530.0482 | 0 | 0 | 1484.9444 | 0 | 0 | 0
2775 | 1483.656 | 542.76 | 2309.8312 | 1541.2289 | 0 | 0 | 768.6023 | 0 | 0 | 0
2776 | 1473.083 | 335.35 | 1456.2038 | 1456.2038 | 0 | 0 | 0 | 71.276 | 0 | 0
2777 | 1294.28 | 101.42 | 420.6567 | 420.6567 | 0 | 0 | 0 | 889.337 | 0 | 0
2778 | 1058.51 | 26.46 | 82.8374 | 82.8374 | 0 | 0 | 0 | 978.767 | 0 | 0
2779 | 1464.006 | 0 | 0 | 0 | 0 | 0 | 0 | 1464.006 | 0 | 0
2780 | 1241.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1241.6 | 0 | 0
2781 | 1408.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1408.8 | 0 | 0
2782 | 1203.2 | 0 | 0 | 0 | 0 | 0 | 0 | 897.326 | 0 | 317.7434
2783 | 1300 | 0 | 0 | 0 | 0 | 0 | 0 | 708 | 0 | 614.9724
2784 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2785 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2786 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2788 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2790 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2791 | 1083.813 | 123.83 | 457.2767 | 457.2767 | 0 | 0 | 0 | 643.618 | 0 | 0
2792 | 1008.77 | 354.17 | 1567.145 | 1047.9151 | -519.2299 | 0 | 0 | 0 | 0 | 0
2793 | 934.389 | 585.77 | 2584.8911 | 970.6477 | -518.7812 | 0 | 1095.4622 | 0 | 0 | 0
2794 | 1123.825 | 777.96 | 3318.0442 | 1167.4347 | 0 | 0 | 2150.6094 | 0 | 0 | 0
2795 | 930.985 | 916.76 | 3819.8648 | 967.1116 | 0 | 0 | 2852.7531 | 0 | 0 | 0
2796 | 972.383 | 981.56 | 4048.3104 | 1010.1161 | 0 | 0 | 3038.1943 | 0 | 0 | 0
2797 | 958.182 | 970.67 | 4020.5681 | 995.364 | 0 | 0 | 3025.2041 | 0 | 0 | 0
2798 | 1202.344 | 877.37 | 3693.275 | 1249.0007 | 0 | 0 | 2444.2743 | 0 | 0 | 0
2799 | 871.996 | 724.54 | 3124.6738 | 905.8336 | 0 | 0 | 2218.8402 | 0 | 0 | 0
2800 | 905.877 | 517.97 | 2297.6242 | 941.0293 | 0 | 0 | 1356.5949 | 0 | 0 | 0
2801 | 1065.211 | 282.14 | 1203.7597 | 1106.5462 | 0 | 0 | 97.2134 | 0 | 0 | 0
2802 | 1003.197 | 66.28 | 211.3843 | 211.3843 | 0 | 0 | 0 | 799.709 | 0 | 0
2803 | 1253.158 | 0 | 0 | 0 | 0 | 0 | 0 | 1253.158 | 0 | 0
2804 | 1226.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1226.4 | 0 | 0
2805 | 1049.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1049.6 | 0 | 0
2806 | 1300 | 0 | 0 | 0 | 0 | 0 | 0 | 1300 | 0 | 0
2807 | 1016.8 | 0 | 0 | 0 | 0 | 0 | 0 | 710.926 | 0 | 317.7434
2808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2809 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2810 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2812 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2813 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2814 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2815 | 976.828 | 76.03 | 308.7993 | 308.7993 | 0 | 0 | 0 | 87.564 | 0 | 614.9724
2816 | 949.208 | 321.53 | 1434.5707 | 986.0418 | -448.5289 | 0 | 0 | 0 | 0 | 0
2817 | 1320.769 | 541.02 | 2398.328 | 1372.0211 | -589.4822 | 0 | 436.8247 | 0 | 0 | 0
2818 | 1344.335 | 733.31 | 3163.47 | 1396.5016 | 0 | 0 | 1766.9684 | 0 | 0 | 0
2819 | 1328.345 | 872.21 | 3678.177 | 1379.8911 | 0 | 0 | 2298.2859 | 0 | 0 | 0
2820 | 1413.067 | 811.5 | 3382.4116 | 1467.9007 | 0 | 0 | 1914.5109 | 0 | 0 | 0
2821 | 1334.168 | 655.27 | 2754.771 | 1385.9401 | 0 | 0 | 1368.8309 | 0 | 0 | 0
2822 | 1503.829 | 644.3 | 2724.8337 | 1562.1847 | 0 | 0 | 1162.649 | 0 | 0 | 0
2823 | 1371.782 | 308.43 | 1325.2801 | 1325.2801 | 0 | 0 | 0 | 96.008 | 0 | 0
2824 | 1502.032 | 176.62 | 756.3122 | 756.3122 | 0 | 0 | 0 | 773.972 | 0 | 0
2825 | 1377.423 | 158.02 | 682.3036 | 682.3036 | 0 | 0 | 0 | 720.607 | 0 | 0
2826 | 1514.373 | 38.94 | 136.9155 | 136.9155 | 0 | 0 | 0 | 1382.572 | 0 | 0
2827 | 1132.464 | 0 | 0 | 0 | 0 | 0 | 0 | 1132.464 | 0 | 0
2828 | 1019.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1019.2 | 0 | 0
2829 | 1064.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1064.8 | 0 | 0
2830 | 1386.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1080.526 | 0 | 317.7434
2831 | 1148 | 0 | 0 | 0 | 0 | 0 | 0 | 556 | 0 | 614.9724
2832 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2834 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2835 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2836 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2837 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2838 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2839 | 989.561 | 98.34 | 406.02 | 406.02 | 0 | 0 | 0 | 598.708 | 0 | 0
2840 | 970.741 | 283.07 | 1271.4804 | 1008.4104 | -263.07 | 0 | 0 | 0 | 0 | 0
2841 | 1081.276 | 588.58 | 2627.0936 | 1123.2346 | -614.9724 | 0 | 888.8865 | 0 | 0 | 0
2842 | 1571.813 | 374.37 | 1616.8695 | 1616.8695 | 0 | 0 | 0 | 0 | 0 | 15.9373
2843 | 1519.172 | 703.24 | 2956.1838 | 1578.1231 | -177.7052 | 0 | 1200.3555 | 0 | 0 | 0
2844 | 1461.244 | 855.84 | 3525.2525 | 1517.9472 | 0 | 0 | 2007.3053 | 0 | 0 | 0
2845 | 1711.452 | 961.54 | 4014.997 | 1777.8645 | 0 | 0 | 2237.1325 | 0 | 0 | 0
2846 | 1173.122 | 877.33 | 3720.876 | 1218.6447 | 0 | 0 | 2502.2313 | 0 | 0 | 0
2847 | 1493.09 | 53.01 | 198.7815 | 198.7815 | 0 | 0 | 0 | 1301.734 | 0 | 0
2848 | 1648.072 | 166.78 | 718.9588 | 718.9588 | 0 | 0 | 0 | 955.97 | 0 | 0
2849 | 1134.203 | 26.45 | 88.2901 | 88.2901 | 0 | 0 | 0 | 1049.211 | 0 | 0
2850 | 1182.912 | 8.81 | 10.7101 | 10.7101 | 0 | 0 | 0 | 1172.602 | 0 | 0
2851 | 1420.356 | 0 | 0 | 0 | 0 | 0 | 0 | 1420.356 | 0 | 0
2852 | 1311.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1311.2 | 0 | 0
2853 | 1405.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1405.6 | 0 | 0
2854 | 1212 | 0 | 0 | 0 | 0 | 0 | 0 | 906.126 | 0 | 317.7434
2855 | 1395.2 | 0 | 0 | 0 | 0 | 0 | 0 | 803.2 | 0 | 614.9724
2856 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2858 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2859 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2860 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2862 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2863 | 1384.773 | 125.89 | 455.0526 | 455.0526 | 0 | 0 | 0 | 946.719 | 0 | 0
2864 | 330.448 | 103.18 | 436.7021 | 343.271 | -93.4311 | 0 | 0 | 0 | 0 | 0
2865 | 66.072 | 463.43 | 2022.6297 | 68.6359 | -614.9724 | 0 | 1339.0214 | 0 | 0 | 0
2866 | 69.845 | 504.21 | 2149.7212 | 72.5553 | -329.6086 | 0 | 1747.5573 | 0 | 0 | 0
2867 | 66.865 | 416.15 | 1761.8752 | 69.4597 | 0 | 0 | 1692.4155 | 0 | 0 | 0
2868 | 69.874 | 187.15 | 778.5956 | 72.5854 | 0 | 0 | 706.0101 | 0 | 0 | 0
2869 | 62.387 | 84.7 | 330.9653 | 64.8079 | 0 | 0 | 266.1574 | 0 | 0 | 0
2870 | 65.31 | 151.41 | 624.9023 | 67.8443 | 0 | 0 | 557.058 | 0 | 0 | 0
2871 | 60.338 | 248.74 | 1057.1272 | 62.6794 | 0 | 0 | 994.4478 | 0 | 0 | 0
2872 | 69.75 | 256.24 | 1106.5327 | 72.4566 | 0 | 0 | 1034.0761 | 0 | 0 | 0
2873 | 62.252 | 140.12 | 598.9997 | 64.6677 | 0 | 0 | 534.3321 | 0 | 0 | 0
2874 | 69.556 | 35.17 | 121.0831 | 72.2551 | 0 | 0 | 48.828 | 0 | 0 | 0
2875 | 70.538 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 73.2752
2876 | 76.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 79.7802
2877 | 72.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.625
2878 | 78.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4423
2879 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.7939
2880 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2881 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2882 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2883 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2884 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2887 | 59.935 | 90.56 | 372.0375 | 62.2608 | -309.7768 | 0 | 0 | 0 | 0 | 0
2888 | 60.615 | 363.45 | 1599.8144 | 62.9682 | -118.5931 | 0 | 1418.2531 | 0 | 0 | 0
2889 | 57.444 | 594.9 | 2592.2832 | 59.6731 | 0 | 0 | 2532.6101 | 0 | 0 | 0
2890 | 63.569 | 786.27 | 3275.4511 | 66.0358 | 0 | 0 | 3209.4153 | 0 | 0 | 0
2891 | 57.64 | 922.68 | 3716.9722 | 59.8767 | 0 | 0 | 3657.0955 | 0 | 0 | 0
2892 | 64.133 | 983.94 | 3935.1347 | 66.6217 | 0 | 0 | 3868.513 | 0 | 0 | 0
2893 | 56.963 | 234.04 | 973.545 | 59.1734 | 0 | 0 | 914.3715 | 0 | 0 | 0
2894 | 68.404 | 359.06 | 1509.3532 | 71.0584 | 0 | 0 | 1438.2948 | 0 | 0 | 0
2895 | 60.106 | 171.8 | 716.6111 | 62.4384 | 0 | 0 | 654.1727 | 0 | 0 | 0
2896 | 68.887 | 62.78 | 242.1838 | 71.5601 | 0 | 0 | 170.6237 | 0 | 0 | 0
2897 | 59.771 | 32.34 | 111.9759 | 62.0904 | 0 | 0 | 49.8855 | 0 | 0 | 0
2898 | 69.059 | 10.77 | 18.0201 | 18.0201 | 0 | 0 | 0 | 0 | 0 | 53.7187
2899 | 74.479 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.3691
2900 | 85.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.9217
2901 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.9492
2902 | 78.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.4423
2903 | 72.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.625
2904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2905 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2906 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2907 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2908 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2909 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2910 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2911 | 59.139 | 126.72 | 461.0911 | 61.4339 | -399.6573 | 0 | 0 | 0 | 0 | 0
2912 | 159.508 | 356.06 | 1574.934 | 165.6977 | -107.8508 | 0 | 1301.3855 | 0 | 0 | 0
2913 | 1257.452 | 584.33 | 2571.1415 | 1306.2471 | 0 | 0 | 1264.8944 | 0 | 0 | 0
2914 | 1452.636 | 775.12 | 3286.3502 | 1509.0052 | 0 | 0 | 1777.3451 | 0 | 0 | 0
2915 | 1793.298 | 903.67 | 3715.1803 | 1862.8865 | 0 | 0 | 1852.2938 | 0 | 0 | 0
2916 | 1328.98 | 964.37 | 3916.0197 | 1380.5507 | 0 | 0 | 2535.4689 | 0 | 0 | 0
2917 | 1338.234 | 951.21 | 3874.2618 | 1390.1638 | 0 | 0 | 2484.0979 | 0 | 0 | 0
2918 | 1057.156 | 651.13 | 2721.8471 | 1098.1787 | 0 | 0 | 1623.6684 | 0 | 0 | 0
2919 | 1280.998 | 292.48 | 1253.9807 | 1253.9807 | 0 | 0 | 0 | 0 | 0 | 76.7261
2920 | 1089.986 | 453.37 | 1987.9856 | 1132.2826 | -85.3877 | 0 | 770.3153 | 0 | 0 | 0
2921 | 1851.164 | 219.29 | 957.2523 | 957.2523 | 0 | 0 | 0 | 929.67 | 0 | 0
2922 | 1796.006 | 55.03 | 197.8113 | 197.8113 | 0 | 0 | 0 | 1605.584 | 0 | 0
2923 | 1783.629 | 0 | 0 | 0 | 0 | 0 | 0 | 1783.629 | 0 | 0
2924 | 1345.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1345.6 | 0 | 0
2925 | 1422.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1422.4 | 0 | 0
2926 | 1416.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1110.926 | 0 | 317.7434
2927 | 1570.4 | 0 | 0 | 0 | 0 | 0 | 0 | 978.4 | 0 | 614.9724
2928 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2929 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2930 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2931 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2932 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2933 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2934 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2935 | 1555.098 | 127.12 | 462.1673 | 462.1673 | 0 | 0 | 0 | 1110.195 | 0 | 0
2936 | 1292.903 | 358.07 | 1588.9734 | 1343.0738 | -245.8996 | 0 | 0 | 0 | 0 | 0
2937 | 1616.041 | 585.45 | 2588.5996 | 1678.7511 | -614.9724 | 0 | 294.8762 | 0 | 0 | 0
2938 | 1859.685 | 775.99 | 3307.0256 | 1931.8496 | -177.1391 | 0 | 1198.0369 | 0 | 0 | 0
2939 | 1608.786 | 732.37 | 3053.8533 | 1671.2145 | 0 | 0 | 1382.6387 | 0 | 0 | 0
2940 | 1823.532 | 968.12 | 3987.4905 | 1894.2937 | 0 | 0 | 2093.1968 | 0 | 0 | 0
2941 | 1798.158 | 498.71 | 2114.5328 | 1867.9351 | 0 | 0 | 246.5977 | 0 | 0 | 0
2942 | 1525.044 | 281.78 | 1204.6053 | 1204.6053 | 0 | 0 | 0 | 76.63 | 0 | 300.0151
2943 | 1520.027 | 443.07 | 1912.8956 | 1579.0113 | -333.8843 | 0 | 0 | 0 | 0 | 0
2944 | 1553.305 | 118.9 | 500.1533 | 500.1533 | 0 | 0 | 0 | 1071.835 | 0 | 0
2945 | 1531.346 | 13.71 | 32.3255 | 32.3255 | 0 | 0 | 0 | 1500.228 | 0 | 0
2946 | 1537.263 | 5.87 | 0 | 0 | 0 | 0 | 0 | 1537.263 | 0 | 0
2947 | 1394.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1394.4 | 0 | 0
2948 | 1347.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1347.2 | 0 | 0
2949 | 1466.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1466.4 | 0 | 0
2950 | 1319.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1013.326 | 0 | 317.7434
2951 | 1240 | 0 | 0 | 0 | 0 | 0 | 0 | 648 | 0 | 614.9724
2952 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2954 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2955 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2956 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2957 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2958 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2959 | 1206.214 | 130.55 | 465.7865 | 465.7865 | 0 | 0 | 0 | 757.827 | 0 | 0
2960 | 1033.754 | 294.32 | 1314.221 | 1073.8686 | -240.3524 | 0 | 0 | 0 | 0 | 0
2961 | 1422.494 | 589.65 | 2631.0857 | 1477.6935 | -614.9724 | 0 | 538.4198 | 0 | 0 | 0
2962 | 1530.86 | 653.53 | 2809.3217 | 1590.2646 | -182.6863 | 0 | 1036.3708 | 0 | 0 | 0
2963 | 1656.662 | 908.3 | 3856.2946 | 1720.9484 | 0 | 0 | 2135.3463 | 0 | 0 | 0
2964 | 1345.486 | 813.12 | 3409.8766 | 1397.6972 | 0 | 0 | 2012.1793 | 0 | 0 | 0
2965 | 1497.656 | 216.08 | 914.3871 | 914.3871 | 0 | 0 | 0 | 617.426 | 0 | 0
2966 | 1691.038 | 74.3 | 289.6801 | 289.6801 | 0 | 0 | 0 | 1412.179 | 0 | 0
2967 | 1889.882 | 132.3 | 552.2193 | 552.2193 | 0 | 0 | 0 | 1358.291 | 0 | 0
2968 | 1787.216 | 255.4 | 1118.1009 | 1118.1009 | 0 | 0 | 0 | 710.882 | 0 | 0
2969 | 1100.388 | 151.86 | 658.0859 | 658.0859 | 0 | 0 | 0 | 466.885 | 0 | 0
2970 | 1874.444 | 38.93 | 138.3813 | 138.3813 | 0 | 0 | 0 | 1741.232 | 0 | 0
2971 | 1314.638 | 0 | 0 | 0 | 0 | 0 | 0 | 1314.638 | 0 | 0
2972 | 1416 | 0 | 0 | 0 | 0 | 0 | 0 | 1416 | 0 | 0
2973 | 988.8 | 0 | 0 | 0 | 0 | 0 | 0 | 988.8 | 0 | 0
2974 | 963.2 | 0 | 0 | 0 | 0 | 0 | 0 | 963.2 | 0 | 0
2975 | 1384 | 0 | 0 | 0 | 0 | 0 | 0 | 1078.126 | 0 | 317.7434
2976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2977 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2978 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2979 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2980 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2981 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2982 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2983 | 1212.52 | 132.77 | 466.9105 | 466.9105 | 0 | 0 | 0 | 171.051 | 0 | 614.9724
2984 | 1002.061 | 367.38 | 1641.4071 | 1040.9457 | -600.4613 | 0 | 0 | 0 | 0 | 0
2985 | 965.107 | 262.56 | 1149.3086 | 1002.5577 | -146.7509 | 0 | 0 | 0 | 0 | 0
2986 | 1411.917 | 787.42 | 3433.4138 | 1466.7061 | -290.7988 | 0 | 1675.9089 | 0 | 0 | 0
2987 | 1427.898 | 504.63 | 2154.4821 | 1483.3072 | 0 | 0 | 671.1749 | 0 | 0 | 0
2988 | 1337.421 | 398.64 | 1693.4148 | 1389.3193 | 0 | 0 | 304.0955 | 0 | 0 | 0
2989 | 1072.122 | 540.58 | 2291.5326 | 1113.7254 | 0 | 0 | 1177.8072 | 0 | 0 | 0
2990 | 1193.708 | 684.42 | 2910.9418 | 1240.0295 | 0 | 0 | 1670.9122 | 0 | 0 | 0
2991 | 980.197 | 646.88 | 2796.5891 | 1018.2333 | 0 | 0 | 1778.3558 | 0 | 0 | 0
2992 | 1206.253 | 474.81 | 2106.5901 | 1253.0613 | 0 | 0 | 853.5287 | 0 | 0 | 0
2993 | 1386.057 | 158.75 | 687.4675 | 687.4675 | 0 | 0 | 0 | 724.27 | 0 | 0
2994 | 1219.223 | 40.79 | 145.8513 | 145.8513 | 0 | 0 | 0 | 1078.82 | 0 | 0
2995 | 1409.584 | 0 | 0 | 0 | 0 | 0 | 0 | 1409.584 | 0 | 0
2996 | 1578.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1578.4 | 0 | 0
2997 | 1444.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1444.8 | 0 | 0
2998 | 1684 | 0 | 0 | 0 | 0 | 0 | 0 | 1378.126 | 0 | 317.7434
2999 | 1376.8 | 0 | 0 | 0 | 0 | 0 | 0 | 784.8 | 0 | 614.9724
3000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3001 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3003 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3004 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3005 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3007 | 781.83 | 72.02 | 294.15 | 294.15 | 0 | 0 | 0 | 498.668 | 0 | 0
3008 | 709.607 | 362.62 | 1611.127 | 737.1431 | -614.9724 | 0 | 259.0114 | 0 | 0 | 0
3009 | 1534.229 | 590.3 | 2625.1417 | 1593.7644 | -423.0387 | 0 | 608.3386 | 0 | 0 | 0
3010 | 1020.516 | 780.43 | 3356.8747 | 1060.1169 | 0 | 0 | 2296.7578 | 0 | 0 | 0
3011 | 1287.992 | 628.49 | 2648.0525 | 1337.9722 | 0 | 0 | 1310.0803 | 0 | 0 | 0
3012 | 1475.707 | 972.31 | 4024.2403 | 1532.9714 | 0 | 0 | 2491.2688 | 0 | 0 | 0
3013 | 1238.1 | 958.47 | 3985.6809 | 1286.1442 | 0 | 0 | 2699.5367 | 0 | 0 | 0
3014 | 1241.662 | 598.85 | 2538.3475 | 1289.8444 | 0 | 0 | 1248.5031 | 0 | 0 | 0
3015 | 1191.082 | 440.55 | 1904.314 | 1237.3016 | 0 | 0 | 667.0124 | 0 | 0 | 0
3016 | 1159.838 | 365.2 | 1608.6556 | 1204.8452 | 0 | 0 | 403.8104 | 0 | 0 | 0
3017 | 1030.094 | 179.51 | 783.3502 | 783.3502 | 0 | 0 | 0 | 276.006 | 0 | 0
3018 | 1147.534 | 46.15 | 168.0225 | 168.0225 | 0 | 0 | 0 | 985.788 | 0 | 0
3019 | 1455.483 | 0 | 0 | 0 | 0 | 0 | 0 | 1455.483 | 0 | 0
3020 | 1283.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1283.2 | 0 | 0
3021 | 1238.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1238.4 | 0 | 0
3022 | 1134.4 | 0 | 0 | 0 | 0 | 0 | 0 | 828.526 | 0 | 317.7434
3023 | 1165.6 | 0 | 0 | 0 | 0 | 0 | 0 | 573.6 | 0 | 614.9724
3024 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3025 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3026 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3027 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3028 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3029 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3030 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3031 | 1273.643 | 128.72 | 474.8647 | 474.8647 | 0 | 0 | 0 | 816.517 | 0 | 0
3032 | 802.242 | 356.92 | 1586.8916 | 833.3728 | -614.9724 | 0 | 138.5464 | 0 | 0 | 0
3033 | 1200.115 | 415.4 | 1821.0621 | 1246.6852 | -423.0387 | 0 | 151.3383 | 0 | 0 | 0
3034 | 1471.92 | 774.65 | 3300.8873 | 1529.0375 | 0 | 0 | 1771.8498 | 0 | 0 | 0
3035 | 1380.935 | 895.25 | 3680.7138 | 1434.5218 | 0 | 0 | 2246.1919 | 0 | 0 | 0
3036 | 1423.39 | 957.41 | 3850.2509 | 1478.6243 | 0 | 0 | 2371.6266 | 0 | 0 | 0
3037 | 1393.065 | 758.23 | 3070.4191 | 1447.1225 | 0 | 0 | 1623.2966 | 0 | 0 | 0
3038 | 1542.057 | 767.84 | 3128.2691 | 1601.8961 | 0 | 0 | 1526.373 | 0 | 0 | 0
3039 | 1458.87 | 611.72 | 2575.3756 | 1515.4811 | 0 | 0 | 1059.8946 | 0 | 0 | 0
3040 | 2088.377 | 79.04 | 316.1748 | 316.1748 | 0 | 0 | 0 | 1784.013 | 0 | 0
3041 | 1746.298 | 78.5 | 318.8944 | 318.8944 | 0 | 0 | 0 | 1439.316 | 0 | 0
3042 | 1528.475 | 21.55 | 63.1853 | 63.1853 | 0 | 0 | 0 | 1467.65 | 0 | 0
3043 | 1628.348 | 0 | 0 | 0 | 0 | 0 | 0 | 1628.348 | 0 | 0
3044 | 1763.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1763.2 | 0 | 0
3045 | 1925.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1925.6 | 0 | 0
3046 | 2003.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1697.326 | 0 | 317.7434
3047 | 1744 | 0 | 0 | 0 | 0 | 0 | 0 | 1152 | 0 | 614.9724
3048 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3049 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3050 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3051 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3052 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3053 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3055 | 1371.414 | 75.2 | 307.7168 | 307.7168 | 0 | 0 | 0 | 1075.192 | 0 | 0
3056 | 1360.451 | 212.16 | 935.4769 | 935.4769 | 0 | 0 | 0 | 459.919 | 0 | 0
3057 | 1498.823 | 338.6 | 1475.2534 | 1475.2534 | 0 | 0 | 0 | 78.678 | 0 | 0
3058 | 2067.103 | 592.58 | 2501.2258 | 2147.3164 | -353.9094 | 0 | 0 | 0 | 0 | 0
3059 | 1900.996 | 880.73 | 3624.8853 | 1974.7637 | -614.9724 | 0 | 1035.1492 | 0 | 0 | 0
3060 | 2047.677 | 941.6 | 3857.3355 | 2127.1366 | -69.1293 | 0 | 1661.0696 | 0 | 0 | 0
3061 | 1737.954 | 817.86 | 3367.4134 | 1805.3949 | 0 | 0 | 1562.0185 | 0 | 0 | 0
3062 | 1834.925 | 712.11 | 2992.6905 | 1906.1288 | 0 | 0 | 1086.5617 | 0 | 0 | 0
3063 | 1799.821 | 245.16 | 1052.8515 | 1052.8515 | 0 | 0 | 0 | 786.299 | 0 | 0
3064 | 1674.824 | 50.57 | 191.2294 | 191.2294 | 0 | 0 | 0 | 1490.738 | 0 | 0
3065 | 1838.59 | 80.77 | 331.172 | 331.172 | 0 | 0 | 0 | 1519.789 | 0 | 0
3066 | 1892.738 | 22.53 | 67.7332 | 67.7332 | 0 | 0 | 0 | 1827.535 | 0 | 0
3067 | 1857.119 | 0 | 0 | 0 | 0 | 0 | 0 | 1857.119 | 0 | 0
3068 | 1924 | 0 | 0 | 0 | 0 | 0 | 0 | 1924 | 0 | 0
3069 | 1824.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1824.8 | 0 | 0
3070 | 2112.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1806.926 | 0 | 317.7434
3071 | 1693.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1101.6 | 0 | 614.9724
3072 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3073 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3074 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3075 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3079 | 1151.437 | 128.43 | 478.2532 | 478.2532 | 0 | 0 | 0 | 691.049 | 0 | 0
3080 | 1016.173 | 352.73 | 1575.1407 | 1055.6053 | -519.5353 | 0 | 0 | 0 | 0 | 0
3081 | 1393.713 | 577.1 | 2584.3416 | 1447.7967 | -518.4758 | 0 | 618.0691 | 0 | 0 | 0
3082 | 1742.288 | 764.97 | 3318.8004 | 1809.897 | 0 | 0 | 1508.9034 | 0 | 0 | 0
3083 | 1918.198 | 561.06 | 2393.5557 | 1992.6332 | 0 | 0 | 400.9225 | 0 | 0 | 0
3084 | 1389.518 | 955.99 | 3991.3288 | 1443.4379 | 0 | 0 | 2547.8909 | 0 | 0 | 0
3085 | 1454.847 | 941.51 | 3935.2822 | 1511.302 | 0 | 0 | 2423.9802 | 0 | 0 | 0
3086 | 1572.945 | 852.24 | 3616.9488 | 1633.9827 | 0 | 0 | 1982.9661 | 0 | 0 | 0
3087 | 1407.007 | 278.82 | 1203.4698 | 1203.4698 | 0 | 0 | 0 | 248.493 | 0 | 0
3088 | 1270.866 | 67.96 | 269.4244 | 269.4244 | 0 | 0 | 0 | 1011.506 | 0 | 0
3089 | 1921.03 | 34.3 | 122.42 | 122.42 | 0 | 0 | 0 | 1803.183 | 0 | 0
3090 | 1338.785 | 10.77 | 18.5281 | 18.5281 | 0 | 0 | 0 | 1320.949 | 0 | 0
3091 | 1455.323 | 0 | 0 | 0 | 0 | 0 | 0 | 1455.323 | 0 | 0
3092 | 1472 | 0 | 0 | 0 | 0 | 0 | 0 | 1472 | 0 | 0
3093 | 1682.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1682.4 | 0 | 0
3094 | 1751.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1445.326 | 0 | 317.7434
3095 | 1388 | 0 | 0 | 0 | 0 | 0 | 0 | 796 | 0 | 614.9724
3096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3099 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3101 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3102 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3103 | 596.8 | 128.37 | 474.9831 | 474.9831 | 0 | 0 | 0 | 139.56 | 0 | 0
3104 | 559.198 | 212.02 | 935.7605 | 580.8975 | -354.863 | 0 | 0 | 0 | 0 | 0
3105 | 533.643 | 436.27 | 1905.8816 | 554.3509 | -614.9724 | 0 | 736.5583 | 0 | 0 | 0
3106 | 918.03 | 503 | 2152.1282 | 953.6539 | -68.1757 | 0 | 1130.2985 | 0 | 0 | 0
3107 | 967.693 | 594.24 | 2508.2398 | 1005.2441 | 0 | 0 | 1502.9957 | 0 | 0 | 0
3108 | 627.109 | 796.48 | 3306.8251 | 651.4438 | 0 | 0 | 2655.3813 | 0 | 0 | 0
3109 | 812.063 | 777.83 | 3246.3189 | 843.5749 | 0 | 0 | 2402.744 | 0 | 0 | 0
3110 | 905.477 | 699.2 | 2960.3588 | 940.6138 | 0 | 0 | 2019.745 | 0 | 0 | 0
3111 | 596.201 | 514.38 | 2225.3078 | 619.3364 | 0 | 0 | 1605.9714 | 0 | 0 | 0
3112 | 817.356 | 31.38 | 106.5471 | 106.5471 | 0 | 0 | 0 | 714.789 | 0 | 0
3113 | 855.171 | 14.69 | 36.3239 | 36.3239 | 0 | 0 | 0 | 820.204 | 0 | 0
3114 | 864.861 | 5.87 | 0 | 0 | 0 | 0 | 0 | 864.861 | 0 | 0
3115 | 824.194 | 0 | 0 | 0 | 0 | 0 | 0 | 824.194 | 0 | 0
3116 | 626.4 | 0 | 0 | 0 | 0 | 0 | 0 | 626.4 | 0 | 0
3117 | 780 | 0 | 0 | 0 | 0 | 0 | 0 | 780 | 0 | 0
3118 | 831.2 | 0 | 0 | 0 | 0 | 0 | 0 | 525.326 | 0 | 317.7434
3119 | 764 | 0 | 0 | 0 | 0 | 0 | 0 | 172 | 0 | 614.9724
3120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3122 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3123 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3124 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3125 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3127 | 1606.824 | 85.52 | 354.0589 | 354.0589 | 0 | 0 | 0 | 1265.991 | 0 | 0
3128 | 1031.203 | 292.88 | 1309.3656 | 1071.2186 | -238.147 | 0 | 0 | 0 | 0 | 0
3129 | 1251.649 | 427.28 | 1886.1578 | 1300.2189 | -585.9389 | 0 | 0 | 0 | 0 | 0
3130 | 1182.361 | 623.89 | 2695.9736 | 1228.2422 | -213.9252 | 0 | 1253.8062 | 0 | 0 | 0
3131 | 1327.158 | 739.57 | 3145.0655 | 1378.658 | 0 | 0 | 1766.4075 | 0 | 0 | 0
3132 | 662.126 | 776.07 | 3278.2361 | 687.8196 | 0 | 0 | 2590.4165 | 0 | 0 | 0
3133 | 803.013 | 795.79 | 3367.5858 | 834.1737 | 0 | 0 | 2533.4121 | 0 | 0 | 0
3134 | 839.44 | 679.3 | 2908.1973 | 872.0143 | 0 | 0 | 2036.183 | 0 | 0 | 0
3135 | 881.612 | 614.63 | 2673.7899 | 915.8227 | 0 | 0 | 1757.9672 | 0 | 0 | 0
3136 | 723.729 | 394.34 | 1746.6172 | 751.8131 | 0 | 0 | 994.8041 | 0 | 0 | 0
3137 | 1037.81 | 177.47 | 774.2316 | 774.2316 | 0 | 0 | 0 | 292.5 | 0 | 0
3138 | 1280.783 | 46.03 | 167.8927 | 167.8927 | 0 | 0 | 0 | 1119.162 | 0 | 0
3139 | 1299.258 | 0 | 0 | 0 | 0 | 0 | 0 | 1299.258 | 0 | 0
3140 | 1091.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1091.2 | 0 | 0
3141 | 1475.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1475.2 | 0 | 0
3142 | 901.6 | 0 | 0 | 0 | 0 | 0 | 0 | 901.6 | 0 | 0
3143 | 1424.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1118.926 | 0 | 317.7434
3144 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3146 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3151 | 1360.959 | 108.71 | 447.0746 | 447.0746 | 0 | 0 | 0 | 338.585 | 0 | 614.9724
3152 | 1089.279 | 295.6 | 1324.9664 | 1131.5482 | -193.4182 | 0 | 0 | 0 | 0 | 0
3153 | 1352.296 | 576.63 | 2587.7769 | 1404.7715 | -614.9724 | 0 | 568.033 | 0 | 0 | 0
3154 | 1592.847 | 761.21 | 3325.1174 | 1654.657 | -229.6205 | 0 | 1440.8398 | 0 | 0 | 0
3155 | 1626.609 | 673.47 | 2885.5534 | 1689.7292 | 0 | 0 | 1195.8242 | 0 | 0 | 0
3156 | 1541.713 | 638.31 | 2734.3315 | 1601.5388 | 0 | 0 | 1132.7927 | 0 | 0 | 0
3157 | 1622.298 | 706.56 | 3023.006 | 1685.2509 | 0 | 0 | 1337.7551 | 0 | 0 | 0
3158 | 1448.694 | 496.42 | 2157.9953 | 1504.9102 | 0 | 0 | 653.0851 | 0 | 0 | 0
3159 | 1620.387 | 385.68 | 1695.2244 | 1683.2657 | 0 | 0 | 11.9587 | 0 | 0 | 0
3160 | 1509.994 | 251.99 | 1115.8944 | 1115.8944 | 0 | 0 | 0 | 435.784 | 0 | 0
3161 | 1315.27 | 190.5 | 842.3605 | 842.3605 | 0 | 0 | 0 | 504.376 | 0 | 0
3162 | 1693.54 | 49.29 | 182.8431 | 182.8431 | 0 | 0 | 0 | 1517.527 | 0 | 0
3163 | 1887.87 | 0 | 0 | 0 | 0 | 0 | 0 | 1887.87 | 0 | 0
3164 | 1574.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.4 | 0 | 0
3165 | 1738.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1738.4 | 0 | 0
3166 | 1488 | 0 | 0 | 0 | 0 | 0 | 0 | 1182.126 | 0 | 317.7434
3167 | 1567.2 | 0 | 0 | 0 | 0 | 0 | 0 | 975.2 | 0 | 614.9724
3168 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3170 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3171 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3172 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3173 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3174 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3175 | 1222.398 | 109.4 | 451.2682 | 451.2682 | 0 | 0 | 0 | 787.987 | 0 | 0
3176 | 1224.246 | 289.21 | 1291.9365 | 1271.7526 | -20.184 | 0 | 0 | 0 | 0 | 0
3177 | 1405.356 | 582.37 | 2602.9705 | 1459.8905 | -614.9724 | 0 | 528.1076 | 0 | 0 | 0
3178 | 1702.904 | 768.03 | 3338.2105 | 1768.9848 | -402.8547 | 0 | 1166.371 | 0 | 0 | 0
3179 | 1163.639 | 754.55 | 3200.2489 | 1208.7937 | 0 | 0 | 1991.4552 | 0 | 0 | 0
3180 | 1654.093 | 744.09 | 3139.3344 | 1718.2797 | 0 | 0 | 1421.0548 | 0 | 0 | 0
3181 | 1527.881 | 817.98 | 3425.0099 | 1587.17 | 0 | 0 | 1837.8399 | 0 | 0 | 0
3182 | 1582.693 | 846.62 | 3610.1831 | 1644.109 | 0 | 0 | 1966.0741 | 0 | 0 | 0
3183 | 1693.198 | 607.43 | 2615.8215 | 1758.9021 | 0 | 0 | 856.9194 | 0 | 0 | 0
3184 | 1547.887 | 312.74 | 1368.3635 | 1368.3635 | 0 | 0 | 0 | 230.639 | 0 | 0
3185 | 1494.49 | 197.75 | 860.1792 | 860.1792 | 0 | 0 | 0 | 666.443 | 0 | 0
3186 | 1557.6 | 51.69 | 189.2661 | 189.2661 | 0 | 0 | 0 | 1375.404 | 0 | 0
3187 | 1736.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1736.8 | 0 | 0
3188 | 1518.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1518.4 | 0 | 0
3189 | 1556 | 0 | 0 | 0 | 0 | 0 | 0 | 1556 | 0 | 0
3190 | 1313.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1007.726 | 0 | 317.7434
3191 | 1468.8 | 0 | 0 | 0 | 0 | 0 | 0 | 876.8 | 0 | 614.9724
3192 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3193 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3194 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3196 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3197 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3198 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3199 | 1067.464 | 120.17 | 490.4893 | 490.4893 | 0 | 0 | 0 | 595.297 | 0 | 0
3200 | 1283.562 | 309.03 | 1381.4753 | 1333.3703 | -48.105 | 0 | 0 | 0 | 0 | 0
3201 | 1599.831 | 447.34 | 1972.0825 | 1661.912 | -310.1705 | 0 | 0 | 0 | 0 | 0
3202 | 1734.369 | 748.59 | 3247.1115 | 1801.6708 | -614.9724 | 0 | 830.4683 | 0 | 0 | 0
3203 | 1623.038 | 889.39 | 3788.0649 | 1686.0196 | -64.7643 | 0 | 2037.281 | 0 | 0 | 0
3204 | 1636.443 | 949.59 | 4014.1213 | 1699.9448 | 0 | 0 | 2314.1765 | 0 | 0 | 0
3205 | 1725.917 | 939.27 | 3972.032 | 1792.8908 | 0 | 0 | 2179.1412 | 0 | 0 | 0
3206 | 2012.075 | 853.26 | 3651.2803 | 2090.1531 | 0 | 0 | 1561.1272 | 0 | 0 | 0
3207 | 1948.007 | 704.95 | 3074.7717 | 2023.5989 | 0 | 0 | 1051.1728 | 0 | 0 | 0
3208 | 1556.628 | 505.8 | 2258.6981 | 1617.0326 | 0 | 0 | 641.6655 | 0 | 0 | 0
3209 | 1721.903 | 277.05 | 1166.6671 | 1166.6671 | 0 | 0 | 0 | 598.817 | 0 | 0
3210 | 1737.852 | 66.48 | 193.6654 | 193.6654 | 0 | 0 | 0 | 1551.421 | 0 | 0
3211 | 1568.995 | 0 | 0 | 0 | 0 | 0 | 0 | 1568.995 | 0 | 0
3212 | 1459.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1459.2 | 0 | 0
3213 | 1577.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1577.6 | 0 | 0
3214 | 1764.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1458.926 | 0 | 317.7434
3215 | 1724 | 0 | 0 | 0 | 0 | 0 | 0 | 1132 | 0 | 614.9724
3216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3217 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3219 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3220 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3222 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3223 | 1482.886 | 43.13 | 165.0889 | 165.0889 | 0 | 0 | 0 | 1323.964 | 0 | 0
3224 | 905.259 | 120.25 | 517.6759 | 517.6759 | 0 | 0 | 0 | 406.921 | 0 | 0
3225 | 1293.998 | 288.91 | 1272.1785 | 1272.1785 | 0 | 0 | 0 | 69.342 | 0 | 0
3226 | 1538.464 | 435.37 | 1892.9942 | 1598.1637 | -294.8304 | 0 | 0 | 0 | 0 | 0
3227 | 1566.084 | 603.42 | 2579.3023 | 1626.8555 | -614.9724 | 0 | 337.4744 | 0 | 0 | 0
3228 | 1519.876 | 682.88 | 2896.3455 | 1578.8534 | -128.2082 | 0 | 1189.2839 | 0 | 0 | 0
3229 | 2001.861 | 508.1 | 2177.7004 | 2079.5427 | 0 | 0 | 98.1577 | 0 | 0 | 0
3230 | 1474.906 | 121.78 | 503.2521 | 503.2521 | 0 | 0 | 0 | 856.607 | 0 | 139.0399
3231 | 1790.369 | 462.77 | 2014.58 | 1859.8438 | -154.7362 | 0 | 0 | 0 | 0 | 0
3232 | 1829.06 | 229.02 | 1001.5657 | 1001.5657 | 0 | 0 | 0 | 864.908 | 0 | 0
3233 | 1677.484 | 27.43 | 92.7019 | 92.7019 | 0 | 0 | 0 | 1588.245 | 0 | 0
3234 | 2026.099 | 9.79 | 14.8559 | 14.8559 | 0 | 0 | 0 | 2011.798 | 0 | 0
3235 | 1587.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1587.2 | 0 | 0
3236 | 1344 | 0 | 0 | 0 | 0 | 0 | 0 | 1344 | 0 | 0
3237 | 1775.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1775.2 | 0 | 0
3238 | 1706.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1400.526 | 0 | 317.7434
3239 | 1422.4 | 0 | 0 | 0 | 0 | 0 | 0 | 830.4 | 0 | 614.9724
3240 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3242 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3243 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3245 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3246 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3247 | 1055.099 | 79.42 | 327.9787 | 327.9787 | 0 | 0 | 0 | 739.372 | 0 | 0
3248 | 1425.043 | 222.58 | 989.7254 | 989.7254 | 0 | 0 | 0 | 472.289 | 0 | 0
3249 | 1508.333 | 449.72 | 1987.944 | 1566.8635 | -421.0805 | 0 | 0 | 0 | 0 | 0
3250 | 1700.252 | 643.82 | 2780.5323 | 1766.2299 | -614.9724 | 0 | 399.33 | 0 | 0 | 0
3251 | 1839.549 | 724.3 | 3080.8861 | 1910.9322 | -1.9581 | 0 | 1167.9957 | 0 | 0 | 0
3252 | 1816.85 | 742.05 | 3141.5232 | 1887.3524 | 0 | 0 | 1254.1708 | 0 | 0 | 0
3253 | 1707.886 | 803.24 | 3389.2958 | 1774.1601 | 0 | 0 | 1615.1357 | 0 | 0 | 0
3254 | 1728.169 | 673.76 | 2876.3569 | 1795.2302 | 0 | 0 | 1081.1267 | 0 | 0 | 0
3255 | 1703.789 | 550.6 | 2384.4537 | 1769.9041 | 0 | 0 | 614.5496 | 0 | 0 | 0
3256 | 1569.14 | 458.58 | 2026.0058 | 1630.0301 | 0 | 0 | 395.9757 | 0 | 0 | 0
3257 | 1690.426 | 219.28 | 958.4345 | 958.4345 | 0 | 0 | 0 | 767.794 | 0 | 0
3258 | 1602.301 | 57.19 | 207.5345 | 207.5345 | 0 | 0 | 0 | 1402.519 | 0 | 0
3259 | 1476.806 | 0 | 0 | 0 | 0 | 0 | 0 | 1476.806 | 0 | 0
3260 | 1332.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1332.8 | 0 | 0
3261 | 1378.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1378.4 | 0 | 0
3262 | 1814.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1508.526 | 0 | 317.7434
3263 | 1490.4 | 0 | 0 | 0 | 0 | 0 | 0 | 898.4 | 0 | 614.9724
3264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3269 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3271 | 1106.227 | 89.01 | 369.1819 | 369.1819 | 0 | 0 | 0 | 750.836 | 0 | 0
3272 | 998.236 | 244.02 | 1087.265 | 1036.9723 | -50.2927 | 0 | 0 | 0 | 0 | 0
3273 | 1435.791 | 572.73 | 2558.1595 | 1491.5065 | -614.9724 | 0 | 451.6806 | 0 | 0 | 0
3274 | 1831.647 | 591.11 | 2558.7153 | 1902.7226 | -372.746 | 0 | 283.2467 | 0 | 0 | 0
3275 | 1511.408 | 745.36 | 3173.884 | 1570.0578 | 0 | 0 | 1603.8262 | 0 | 0 | 0
3276 | 1131.45 | 690.92 | 2949.229 | 1175.3556 | 0 | 0 | 1773.8734 | 0 | 0 | 0
3277 | 1343.015 | 295.76 | 1279.5239 | 1279.5239 | 0 | 0 | 0 | 0 | 0 | 115.6065
3278 | 1463.195 | 653.73 | 2827.8561 | 1519.9739 | -128.658 | 0 | 1179.2241 | 0 | 0 | 0
3279 | 1538.188 | 583.09 | 2560.5197 | 1597.877 | 0 | 0 | 962.6427 | 0 | 0 | 0
3280 | 1937.529 | 132.69 | 569.7491 | 569.7491 | 0 | 0 | 0 | 1389.063 | 0 | 0
3281 | 1784.662 | 130.28 | 565.2365 | 565.2365 | 0 | 0 | 0 | 1240.54 | 0 | 0
3282 | 1641.186 | 42.66 | 157.2418 | 157.2418 | 0 | 0 | 0 | 1489.818 | 0 | 0
3283 | 1082.752 | 0 | 0 | 0 | 0 | 0 | 0 | 1082.752 | 0 | 0
3284 | 1290.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1290.4 | 0 | 0
3285 | 1324.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1324.8 | 0 | 0
3286 | 1139.2 | 0 | 0 | 0 | 0 | 0 | 0 | 833.326 | 0 | 317.7434
3287 | 1259.2 | 0 | 0 | 0 | 0 | 0 | 0 | 667.2 | 0 | 614.9724
3288 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3289 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3290 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3292 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3293 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3294 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3295 | 1182.657 | 120.9 | 493.6888 | 493.6888 | 0 | 0 | 0 | 707.41 | 0 | 0
3296 | 936.672 | 307.86 | 1383.9767 | 973.0193 | -410.9574 | 0 | 0 | 0 | 0 | 0
3297 | 1006.925 | 330.42 | 1462.4792 | 1045.9985 | -416.4807 | 0 | 0 | 0 | 0 | 0
3298 | 980.994 | 346.88 | 1509.5246 | 1019.0602 | -210.574 | 0 | 279.8904 | 0 | 0 | 0
3299 | 1100.227 | 438.16 | 1881.4738 | 1142.921 | 0 | 0 | 738.5528 | 0 | 0 | 0
3300 | 1192.407 | 783.26 | 3239.1272 | 1238.6781 | 0 | 0 | 2000.4492 | 0 | 0 | 0
3301 | 1178.5 | 782.88 | 3246.5079 | 1224.2314 | 0 | 0 | 2022.2765 | 0 | 0 | 0
3302 | 1218.473 | 846.41 | 3559.5008 | 1265.7555 | 0 | 0 | 2293.7453 | 0 | 0 | 0
3303 | 1017.622 | 701.04 | 3030.7419 | 1057.1106 | 0 | 0 | 1973.6314 | 0 | 0 | 0
3304 | 339.258 | 502.96 | 2243.1212 | 352.4228 | 0 | 0 | 1890.6984 | 0 | 0 | 0
3305 | 224.739 | 275.97 | 1168.1515 | 233.4599 | 0 | 0 | 934.6916 | 0 | 0 | 0
3306 | 209.471 | 68.88 | 239.6533 | 217.5995 | 0 | 0 | 22.0538 | 0 | 0 | 0
3307 | 115.054 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.5186
3308 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3309 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3310 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3313 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3314 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3315 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3316 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3317 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3318 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3319 | 79.923 | 79.57 | 329.3863 | 83.0244 | -133.0117 | 0 | 113.3502 | 0 | 0 | 0
3320 | 156.96 | 353.68 | 1576.0039 | 163.0508 | 0 | 0 | 1412.9531 | 0 | 0 | 0
3321 | 637.627 | 573.54 | 2581.8277 | 662.37 | 0 | 0 | 1919.4577 | 0 | 0 | 0
3322 | 1024.991 | 755.9 | 3316.8672 | 1064.7655 | 0 | 0 | 2252.1017 | 0 | 0 | 0
3323 | 1410.943 | 644.42 | 2774.34 | 1465.6943 | 0 | 0 | 1308.6457 | 0 | 0 | 0
3324 | 1071.439 | 687.46 | 2938.1107 | 1113.0159 | 0 | 0 | 1825.0948 | 0 | 0 | 0
3325 | 1560.347 | 929.12 | 3964.858 | 1620.8959 | 0 | 0 | 2343.9622 | 0 | 0 | 0
3326 | 1408.139 | 676.19 | 2908.8891 | 1462.7815 | 0 | 0 | 1446.1076 | 0 | 0 | 0
3327 | 996.949 | 59.37 | 230.5336 | 230.5336 | 0 | 0 | 0 | 775.027 | 0 | 0
3328 | 1328.349 | 130.69 | 560.5879 | 560.5879 | 0 | 0 | 0 | 788.702 | 0 | 0
3329 | 1340.192 | 252.92 | 1115.6285 | 1115.6285 | 0 | 0 | 0 | 266.238 | 0 | 0
3330 | 1479.054 | 67.49 | 201.8917 | 201.8917 | 0 | 0 | 0 | 1284.704 | 0 | 0
3331 | 1458.236 | 0 | 0 | 0 | 0 | 0 | 0 | 1458.236 | 0 | 0
3332 | 1057.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1057.6 | 0 | 0
3333 | 1518.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1518.4 | 0 | 0
3334 | 1292 | 0 | 0 | 0 | 0 | 0 | 0 | 986.126 | 0 | 317.7434
3335 | 1396.8 | 0 | 0 | 0 | 0 | 0 | 0 | 804.8 | 0 | 614.9724
3336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3337 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3339 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3340 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3341 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3343 | 1413.981 | 131.85 | 468.8386 | 468.8386 | 0 | 0 | 0 | 962.656 | 0 | 0
3344 | 1218.646 | 357.25 | 1595.0411 | 1265.9353 | -329.1058 | 0 | 0 | 0 | 0 | 0
3345 | 1283.48 | 577.34 | 2601.9888 | 1333.2851 | -614.9724 | 0 | 653.7313 | 0 | 0 | 0
3346 | 1235.312 | 759.75 | 3329.5759 | 1283.248 | -93.9329 | 0 | 1952.3951 | 0 | 0 | 0
3347 | 1227.421 | 709.16 | 3029.0383 | 1275.0508 | 0 | 0 | 1753.9875 | 0 | 0 | 0
3348 | 1268.221 | 940.13 | 3998.1008 | 1317.434 | 0 | 0 | 2680.6668 | 0 | 0 | 0
3349 | 1361.861 | 416.77 | 1792.1782 | 1414.7077 | 0 | 0 | 377.4705 | 0 | 0 | 0
3350 | 1362.378 | 643.03 | 2759.1527 | 1415.2447 | 0 | 0 | 1343.9079 | 0 | 0 | 0
3351 | 1092.7 | 135.64 | 568.4599 | 568.4599 | 0 | 0 | 0 | 545.475 | 0 | 0
3352 | 1161.964 | 37.26 | 132.6865 | 132.6865 | 0 | 0 | 0 | 1034.234 | 0 | 0
3353 | 1302.91 | 92.01 | 383.4696 | 383.4696 | 0 | 0 | 0 | 933.765 | 0 | 0
3354 | 1031.53 | 35.22 | 123.5617 | 123.5617 | 0 | 0 | 0 | 912.584 | 0 | 0
3355 | 1155.338 | 0 | 0 | 0 | 0 | 0 | 0 | 1155.338 | 0 | 0
3356 | 992.8 | 0 | 0 | 0 | 0 | 0 | 0 | 992.8 | 0 | 0
3357 | 1484 | 0 | 0 | 0 | 0 | 0 | 0 | 1484 | 0 | 0
3358 | 1380 | 0 | 0 | 0 | 0 | 0 | 0 | 1074.126 | 0 | 317.7434
3359 | 799.2 | 0 | 0 | 0 | 0 | 0 | 0 | 207.2 | 0 | 614.9724
3360 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3361 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3362 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3364 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3365 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3366 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3367 | 1303.011 | 132.88 | 474.2383 | 474.2383 | 0 | 0 | 0 | 846.488 | 0 | 0
3368 | 993.966 | 355.12 | 1581.6758 | 1032.5366 | -549.1392 | 0 | 0 | 0 | 0 | 0
3369 | 1093.9 | 575.27 | 2589.3382 | 1136.3485 | -488.8719 | 0 | 964.1178 | 0 | 0 | 0
3370 | 1363.693 | 756.9 | 3323.6735 | 1416.6108 | 0 | 0 | 1907.0627 | 0 | 0 | 0
3371 | 1239.039 | 884.85 | 3823.0695 | 1287.1196 | 0 | 0 | 2535.9499 | 0 | 0 | 0
3372 | 1503.503 | 943.34 | 4051.646 | 1561.8461 | 0 | 0 | 2489.7999 | 0 | 0 | 0
3373 | 1361.769 | 933.1 | 4011.1347 | 1414.6121 | 0 | 0 | 2596.5226 | 0 | 0 | 0
3374 | 1532.198 | 844.9 | 3669.5663 | 1591.6546 | 0 | 0 | 2077.9118 | 0 | 0 | 0
3375 | 1256.603 | 697.9 | 3084.7899 | 1305.3652 | 0 | 0 | 1779.4247 | 0 | 0 | 0
3376 | 1138.22 | 501.21 | 2262.0752 | 1182.3883 | 0 | 0 | 1079.6869 | 0 | 0 | 0
3377 | 1339.573 | 127.97 | 548.0443 | 548.0443 | 0 | 0 | 0 | 812.001 | 0 | 0
3378 | 1110.796 | 19.59 | 55.9054 | 55.9054 | 0 | 0 | 0 | 1056.979 | 0 | 0
3379 | 989.602 | 0 | 0 | 0 | 0 | 0 | 0 | 989.602 | 0 | 0
3380 | 1045.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1045.6 | 0 | 0
3381 | 1416.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1416.8 | 0 | 0
3382 | 1268 | 0 | 0 | 0 | 0 | 0 | 0 | 962.126 | 0 | 317.7434
3383 | 1352.8 | 0 | 0 | 0 | 0 | 0 | 0 | 760.8 | 0 | 614.9724
3384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3385 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3386 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3387 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3389 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3390 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3391 | 1304.669 | 110.07 | 454.4199 | 454.4199 | 0 | 0 | 0 | 867.224 | 0 | 0
3392 | 935.942 | 287.3 | 1286.6324 | 972.261 | -314.3714 | 0 | 0 | 0 | 0 | 0
3393 | 898.574 | 451.13 | 2002.64 | 933.4429 | -614.9724 | 0 | 454.2246 | 0 | 0 | 0
3394 | 1261.705 | 561.14 | 2443.6594 | 1310.6662 | -108.6673 | 0 | 1024.3259 | 0 | 0 | 0
3395 | 1281.246 | 626.85 | 2692.9102 | 1330.9644 | 0 | 0 | 1361.9457 | 0 | 0 | 0
3396 | 1130.342 | 601.16 | 2572.7495 | 1174.2046 | 0 | 0 | 1398.5449 | 0 | 0 | 0
3397 | 1247.462 | 674.01 | 2875.6172 | 1295.8694 | 0 | 0 | 1579.7478 | 0 | 0 | 0
3398 | 1339.387 | 404.71 | 1746.1851 | 1391.3616 | 0 | 0 | 354.8235 | 0 | 0 | 0
3399 | 1391.303 | 353.62 | 1537.0664 | 1445.2922 | 0 | 0 | 91.7742 | 0 | 0 | 0
3400 | 1345.155 | 414.57 | 1835.5992 | 1397.3534 | 0 | 0 | 438.2458 | 0 | 0 | 0
3401 | 1198.38 | 224.87 | 984.5802 | 984.5802 | 0 | 0 | 0 | 250.579 | 0 | 0
3402 | 1181.647 | 64.74 | 234.425 | 234.425 | 0 | 0 | 0 | 955.979 | 0 | 0
3403 | 1283.014 | 0 | 0 | 0 | 0 | 0 | 0 | 1283.014 | 0 | 0
3404 | 1180.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1180.8 | 0 | 0
3405 | 1619.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1619.2 | 0 | 0
3406 | 1483.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1177.326 | 0 | 317.7434
3407 | 1326.4 | 0 | 0 | 0 | 0 | 0 | 0 | 734.4 | 0 | 614.9724
3408 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3409 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3413 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3414 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3415 | 619.025 | 77.29 | 319.4034 | 319.4034 | 0 | 0 | 0 | 311.553 | 0 | 0
3416 | 887.264 | 212.41 | 944.0159 | 921.6941 | -22.3218 | 0 | 0 | 0 | 0 | 0
3417 | 690.747 | 573.62 | 2578.3269 | 717.5513 | -614.9724 | 0 | 1245.8032 | 0 | 0 | 0
3418 | 307.348 | 755.98 | 3303.7855 | 319.2746 | -400.7169 | 0 | 2583.7941 | 0 | 0 | 0
3419 | 235.767 | 884.75 | 3780.3414 | 244.9159 | 0 | 0 | 3535.4255 | 0 | 0 | 0
3420 | 197.082 | 943.17 | 3981.8072 | 204.7297 | 0 | 0 | 3777.0774 | 0 | 0 | 0
3421 | 683.53 | 796.75 | 3346.4015 | 710.0542 | 0 | 0 | 2636.3473 | 0 | 0 | 0
3422 | 1150.936 | 747.47 | 3164.0372 | 1195.5978 | 0 | 0 | 1968.4394 | 0 | 0 | 0
3423 | 1786.232 | 89.1 | 359.0805 | 359.0805 | 0 | 0 | 0 | 1440.565 | 0 | 0
3424 | 1729.544 | 73.82 | 295.8474 | 295.8474 | 0 | 0 | 0 | 1444.748 | 0 | 0
3425 | 1610.063 | 236.88 | 1036.0852 | 1036.0852 | 0 | 0 | 0 | 612.681 | 0 | 0
3426 | 1527.327 | 53.31 | 198.285 | 198.285 | 0 | 0 | 0 | 1336.449 | 0 | 0
3427 | 1637.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1637.6 | 0 | 0
3428 | 1442.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1442.4 | 0 | 0
3429 | 1472.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1472.8 | 0 | 0
3430 | 1553.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1247.726 | 0 | 317.7434
3431 | 1444 | 0 | 0 | 0 | 0 | 0 | 0 | 852 | 0 | 614.9724
3432 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3433 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3438 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3439 | 1362.282 | 130.56 | 465.9704 | 465.9704 | 0 | 0 | 0 | 913.718 | 0 | 0
3440 | 1064.339 | 351.77 | 1571.2192 | 1105.6404 | -465.5788 | 0 | 0 | 0 | 0 | 0
3441 | 1658.966 | 571.84 | 2586.1688 | 1723.3418 | -572.4323 | 0 | 290.3948 | 0 | 0 | 0
3442 | 1820.422 | 753.64 | 3321.1076 | 1891.063 | 0 | 0 | 1430.0446 | 0 | 0 | 0
3443 | 1766.438 | 872.89 | 3772.4994 | 1834.9842 | 0 | 0 | 1937.5152 | 0 | 0 | 0
3444 | 1632.862 | 931.33 | 3988.2592 | 1696.2248 | 0 | 0 | 2292.0344 | 0 | 0 | 0
3445 | 1633.953 | 702.82 | 3006.9138 | 1697.3581 | 0 | 0 | 1309.5557 | 0 | 0 | 0
3446 | 1730.896 | 652.58 | 2815.0757 | 1798.063 | 0 | 0 | 1017.0127 | 0 | 0 | 0
3447 | 1836.767 | 606.71 | 2656.8585 | 1908.0423 | 0 | 0 | 748.8162 | 0 | 0 | 0
3448 | 1998.015 | 357.52 | 1593.113 | 1593.113 | 0 | 0 | 0 | 464.413 | 0 | 0
3449 | 1627.268 | 34.3 | 124.2587 | 124.2587 | 0 | 0 | 0 | 1507.651 | 0 | 0
3450 | 1652.685 | 64.25 | 236.4538 | 236.4538 | 0 | 0 | 0 | 1425.064 | 0 | 0
3451 | 1494.002 | 0 | 0 | 0 | 0 | 0 | 0 | 1494.002 | 0 | 0
3452 | 1398.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1398.4 | 0 | 0
3453 | 1210.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1210.4 | 0 | 0
3454 | 1628 | 0 | 0 | 0 | 0 | 0 | 0 | 1322.126 | 0 | 317.7434
3455 | 1786.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1194.4 | 0 | 614.9724
3456 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3457 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3458 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3459 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3460 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3461 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3462 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3463 | 1177.554 | 105.62 | 439.0321 | 439.0321 | 0 | 0 | 0 | 754.922 | 0 | 0
3464 | 1356.489 | 281.72 | 1265.9217 | 1265.9217 | 0 | 0 | 0 | 137.856 | 0 | 0
3465 | 1166.426 | 452.56 | 2012.0547 | 1211.6889 | -614.9724 | 0 | 185.3934 | 0 | 0 | 0
3466 | 975.268 | 618.9 | 2689.344 | 1013.113 | -423.0387 | 0 | 1253.1922 | 0 | 0 | 0
3467 | 1314.143 | 688.36 | 2946.7452 | 1365.138 | 0 | 0 | 1581.6072 | 0 | 0 | 0
3468 | 1169.049 | 785.92 | 3330.032 | 1214.4137 | 0 | 0 | 2115.6183 | 0 | 0 | 0
3469 | 1078.088 | 918.95 | 3915.9376 | 1119.9229 | 0 | 0 | 2796.0147 | 0 | 0 | 0
3470 | 944.397 | 650.53 | 2791.2954 | 981.0441 | 0 | 0 | 1810.2513 | 0 | 0 | 0
3471 | 1126.43 | 545.79 | 2376.5058 | 1170.1408 | 0 | 0 | 1206.365 | 0 | 0 | 0
3472 | 898.155 | 211.71 | 925.9023 | 925.9023 | 0 | 0 | 0 | 6.84 | 0 | 0
3473 | 1152.652 | 84.9 | 352.8415 | 352.8415 | 0 | 0 | 0 | 812.991 | 0 | 0
3474 | 869.487 | 11.75 | 23.2952 | 23.2952 | 0 | 0 | 0 | 847.062 | 0 | 0
3475 | 1185.808 | 0 | 0 | 0 | 0 | 0 | 0 | 1185.808 | 0 | 0
3476 | 980.8 | 0 | 0 | 0 | 0 | 0 | 0 | 980.8 | 0 | 0
3477 | 808.8 | 0 | 0 | 0 | 0 | 0 | 0 | 808.8 | 0 | 0
3478 | 850.4 | 0 | 0 | 0 | 0 | 0 | 0 | 850.4 | 0 | 0
3479 | 840 | 0 | 0 | 0 | 0 | 0 | 0 | 534.126 | 0 | 317.7434
3480 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3485 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3487 | 1097.92 | 127.87 | 469.3943 | 469.3943 | 0 | 0 | 0 | 54.06 | 0 | 614.9724
3488 | 961.001 | 347.38 | 1543.4062 | 998.2924 | -545.1138 | 0 | 0 | 0 | 0 | 0
3489 | 988.449 | 564.66 | 2526.7274 | 1026.8066 | -492.8973 | 0 | 1007.0236 | 0 | 0 | 0
3490 | 1114.766 | 746.76 | 3244.7991 | 1158.0242 | 0 | 0 | 2086.7749 | 0 | 0 | 0
3491 | 1334.239 | 872.49 | 3710.0351 | 1386.0138 | 0 | 0 | 2324.0213 | 0 | 0 | 0
3492 | 1375.817 | 933.01 | 3933.5609 | 1429.2052 | 0 | 0 | 2504.3557 | 0 | 0 | 0
3493 | 1313.727 | 921.54 | 3892.3349 | 1364.7058 | 0 | 0 | 2527.6291 | 0 | 0 | 0
3494 | 1220.12 | 712.38 | 3028.1574 | 1267.4664 | 0 | 0 | 1760.6909 | 0 | 0 | 0
3495 | 1436.12 | 698.58 | 3055.9766 | 1491.8483 | 0 | 0 | 1564.1283 | 0 | 0 | 0
3496 | 1317.272 | 426.23 | 1884.8094 | 1368.3884 | 0 | 0 | 516.421 | 0 | 0 | 0
3497 | 1561.218 | 278.03 | 1177.0697 | 1177.0697 | 0 | 0 | 0 | 428.118 | 0 | 0
3498 | 1522.874 | 58.68 | 218.6165 | 218.6165 | 0 | 0 | 0 | 1312.424 | 0 | 0
3499 | 1531.013 | 0 | 0 | 0 | 0 | 0 | 0 | 1531.013 | 0 | 0
3500 | 820.8 | 0 | 0 | 0 | 0 | 0 | 0 | 820.8 | 0 | 0
3501 | 1276 | 0 | 0 | 0 | 0 | 0 | 0 | 1276 | 0 | 0
3502 | 1128 | 0 | 0 | 0 | 0 | 0 | 0 | 822.126 | 0 | 317.7434
3503 | 905.6 | 0 | 0 | 0 | 0 | 0 | 0 | 313.6 | 0 | 614.9724
3504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3505 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3507 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3508 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3509 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3510 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3511 | 803.82 | 131.16 | 461.4693 | 461.4693 | 0 | 0 | 0 | 359.589 | 0 | 0
3512 | 740.237 | 355.63 | 1585.0166 | 768.9617 | -614.9724 | 0 | 201.0825 | 0 | 0 | 0
3513 | 558.473 | 575.2 | 2597.2872 | 580.1444 | -423.0387 | 0 | 1594.1041 | 0 | 0 | 0
3514 | 1199.225 | 755.83 | 3316.0092 | 1245.7606 | 0 | 0 | 2070.2485 | 0 | 0 | 0
3515 | 1228.803 | 884.63 | 3798.2078 | 1276.4864 | 0 | 0 | 2521.7214 | 0 | 0 | 0
3516 | 1419.01 | 943.3 | 3999.5084 | 1474.0743 | 0 | 0 | 2525.4341 | 0 | 0 | 0
3517 | 1282.017 | 933.35 | 3947.0446 | 1331.7653 | 0 | 0 | 2615.2793 | 0 | 0 | 0
3518 | 1153.519 | 846.74 | 3620.4143 | 1198.281 | 0 | 0 | 2422.1332 | 0 | 0 | 0
3519 | 1350.247 | 700.04 | 3052.5049 | 1402.643 | 0 | 0 | 1649.8619 | 0 | 0 | 0
3520 | 1241.158 | 503.61 | 2250.2537 | 1289.3208 | 0 | 0 | 960.9328 | 0 | 0 | 0
3521 | 1171.973 | 183.93 | 797.2723 | 797.2723 | 0 | 0 | 0 | 404.483 | 0 | 0
3522 | 1371.137 | 52.15 | 194.3936 | 194.3936 | 0 | 0 | 0 | 1184.005 | 0 | 0
3523 | 1506.995 | 0 | 0 | 0 | 0 | 0 | 0 | 1506.995 | 0 | 0
3524 | 1457.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1457.6 | 0 | 0
3525 | 1496 | 0 | 0 | 0 | 0 | 0 | 0 | 1496 | 0 | 0
3526 | 1008.8 | 0 | 0 | 0 | 0 | 0 | 0 | 702.926 | 0 | 317.7434
3527 | 940.8 | 0 | 0 | 0 | 0 | 0 | 0 | 348.8 | 0 | 614.9724
3528 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3529 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3530 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3532 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3533 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3534 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3535 | 1415.654 | 128.99 | 461.0849 | 461.0849 | 0 | 0 | 0 | 971.793 | 0 | 0
3536 | 996.848 | 347.99 | 1544.7432 | 1035.5304 | -509.2127 | 0 | 0 | 0 | 0 | 0
3537 | 1420.083 | 564.92 | 2533.8473 | 1475.189 | -528.7994 | 0 | 529.859 | 0 | 0 | 0
3538 | 1718.45 | 745.49 | 3240.3395 | 1785.134 | 0 | 0 | 1455.2055 | 0 | 0 | 0
3539 | 1514.737 | 648.36 | 2754.5934 | 1573.516 | 0 | 0 | 1181.0774 | 0 | 0 | 0
3540 | 1481.469 | 774.46 | 3254.3976 | 1538.957 | 0 | 0 | 1715.4406 | 0 | 0 | 0
3541 | 1629.559 | 781.05 | 3285.2688 | 1692.7936 | 0 | 0 | 1592.4752 | 0 | 0 | 0
3542 | 1581.445 | 714.48 | 3039.2757 | 1642.8126 | 0 | 0 | 1396.4631 | 0 | 0 | 0
3543 | 1376.542 | 384.33 | 1669.085 | 1429.9584 | 0 | 0 | 239.1266 | 0 | 0 | 0
3544 | 1606.679 | 225.19 | 981.0555 | 981.0555 | 0 | 0 | 0 | 662.271 | 0 | 0
3545 | 1530.064 | 89.74 | 372.7481 | 372.7481 | 0 | 0 | 0 | 1171.24 | 0 | 0
3546 | 1776.413 | 29.4 | 98.4382 | 98.4382 | 0 | 0 | 0 | 1681.652 | 0 | 0
3547 | 1785.434 | 0 | 0 | 0 | 0 | 0 | 0 | 1785.434 | 0 | 0
3548 | 1460 | 0 | 0 | 0 | 0 | 0 | 0 | 1460 | 0 | 0
3549 | 1711.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1711.2 | 0 | 0
3550 | 1587.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1281.326 | 0 | 317.7434
3551 | 1569.6 | 0 | 0 | 0 | 0 | 0 | 0 | 977.6 | 0 | 614.9724
3552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3553 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3554 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3555 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3556 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3557 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3559 | 1421.245 | 88.56 | 367.6029 | 367.6029 | 0 | 0 | 0 | 1067.374 | 0 | 0
3560 | 1472.409 | 307.1 | 1370.8774 | 1370.8774 | 0 | 0 | 0 | 152.741 | 0 | 0
3561 | 1472.679 | 483.84 | 2132.4646 | 1529.8259 | -602.6387 | 0 | 0 | 0 | 0 | 0
3562 | 1255.664 | 571.51 | 2461.7969 | 1304.3887 | -435.3735 | 0 | 722.0347 | 0 | 0 | 0
3563 | 1306.374 | 706.91 | 2990.6628 | 1357.0675 | 0 | 0 | 1633.5953 | 0 | 0 | 0
3564 | 1147.369 | 733.13 | 3090.2488 | 1191.8924 | 0 | 0 | 1898.3565 | 0 | 0 | 0
3565 | 1451.78 | 701.56 | 2963.3931 | 1508.116 | 0 | 0 | 1455.2772 | 0 | 0 | 0
3566 | 1625.359 | 148.25 | 619.2315 | 619.2315 | 0 | 0 | 0 | 1029.259 | 0 | 0
3567 | 1496.668 | 63.74 | 246.3827 | 246.3827 | 0 | 0 | 0 | 1259.489 | 0 | 0
3568 | 1406.455 | 27.45 | 89.8691 | 89.8691 | 0 | 0 | 0 | 1319.943 | 0 | 0
3569 | 1189.61 | 100.06 | 419.4507 | 419.4507 | 0 | 0 | 0 | 785.828 | 0 | 0
3570 | 1307.693 | 52.79 | 198.1603 | 198.1603 | 0 | 0 | 0 | 1116.935 | 0 | 0
3571 | 1408 | 0 | 0 | 0 | 0 | 0 | 0 | 1408 | 0 | 0
3572 | 1389.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1389.6 | 0 | 0
3573 | 1545.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1545.6 | 0 | 0
3574 | 1364 | 0 | 0 | 0 | 0 | 0 | 0 | 1058.126 | 0 | 317.7434
3575 | 1421.6 | 0 | 0 | 0 | 0 | 0 | 0 | 829.6 | 0 | 614.9724
3576 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3578 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3580 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3582 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3583 | 1709.965 | 97.1 | 402.9804 | 402.9804 | 0 | 0 | 0 | 1322.038 | 0 | 0
3584 | 1408.436 | 260.19 | 1157.1454 | 1157.1454 | 0 | 0 | 0 | 294.516 | 0 | 0
3585 | 1450.739 | 431.83 | 1893.0887 | 1507.0346 | -386.0541 | 0 | 0 | 0 | 0 | 0
3586 | 1655.173 | 581.84 | 2484.4532 | 1719.4016 | -614.9724 | 0 | 150.0792 | 0 | 0 | 0
3587 | 1645.765 | 576.6 | 2436.4324 | 1709.6285 | -36.9846 | 0 | 689.8193 | 0 | 0 | 0
3588 | 1950.329 | 703.61 | 2939.8673 | 2026.011 | 0 | 0 | 913.8563 | 0 | 0 | 0
3589 | 1604.172 | 566.6 | 2396.8321 | 1666.4215 | 0 | 0 | 730.4106 | 0 | 0 | 0
3590 | 1638.537 | 76.81 | 299.8042 | 299.8042 | 0 | 0 | 0 | 1349.932 | 0 | 0
3591 | 1750.351 | 184.26 | 783.4042 | 783.4042 | 0 | 0 | 0 | 917.843 | 0 | 81.4091
3592 | 1625.121 | 402.57 | 1778.7838 | 1688.1834 | -90.6004 | 0 | 0 | 0 | 0 | 0
3593 | 1456.088 | 217.81 | 956.146 | 956.146 | 0 | 0 | 0 | 535.659 | 0 | 0
3594 | 1657.048 | 63.44 | 235.7619 | 235.7619 | 0 | 0 | 0 | 1430.093 | 0 | 0
3595 | 1497.593 | 0 | 0 | 0 | 0 | 0 | 0 | 1497.593 | 0 | 0
3596 | 1270.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1270.4 | 0 | 0
3597 | 1587.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1587.2 | 0 | 0
3598 | 1514.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1208.526 | 0 | 317.7434
3599 | 1600.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1008.8 | 0 | 614.9724
3600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3601 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3602 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3603 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3604 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3605 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3606 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3607 | 1586.458 | 128.71 | 455.0173 | 455.0173 | 0 | 0 | 0 | 1148.438 | 0 | 0
3608 | 1339.324 | 346.37 | 1528.515 | 1391.2961 | -137.2188 | 0 | 0 | 0 | 0 | 0
3609 | 1167.329 | 562.88 | 2488.3041 | 1212.6269 | -614.9724 | 0 | 660.7048 | 0 | 0 | 0
3610 | 1838.145 | 744.48 | 3136.4247 | 1909.4738 | -285.8199 | 0 | 941.1311 | 0 | 0 | 0
3611 | 1601.039 | 871.84 | 3563.2977 | 1663.1669 | 0 | 0 | 1900.1307 | 0 | 0 | 0
3612 | 1499.82 | 932.79 | 3782.8844 | 1558.0201 | 0 | 0 | 2224.8642 | 0 | 0 | 0
3613 | 1916.994 | 811.62 | 3309.1842 | 1991.3825 | 0 | 0 | 1317.8017 | 0 | 0 | 0
3614 | 1203.199 | 774.04 | 3190.3719 | 1249.8888 | 0 | 0 | 1940.4831 | 0 | 0 | 0
3615 | 1339.569 | 179.35 | 764.4554 | 764.4554 | 0 | 0 | 0 | 603.67 | 0 | 0
3616 | 1487.923 | 29.41 | 99.1248 | 99.1248 | 0 | 0 | 0 | 1392.501 | 0 | 0
3617 | 1570.841 | 110.02 | 466.8929 | 466.8929 | 0 | 0 | 0 | 1121.389 | 0 | 0
3618 | 1493.196 | 44.62 | 166.1714 | 166.1714 | 0 | 0 | 0 | 1333.232 | 0 | 0
3619 | 1175.793 | 0 | 0 | 0 | 0 | 0 | 0 | 1175.793 | 0 | 0
3620 | 1504 | 0 | 0 | 0 | 0 | 0 | 0 | 1504 | 0 | 0
3621 | 1400 | 0 | 0 | 0 | 0 | 0 | 0 | 1400 | 0 | 0
3622 | 1072 | 0 | 0 | 0 | 0 | 0 | 0 | 766.126 | 0 | 317.7434
3623 | 1568.8 | 0 | 0 | 0 | 0 | 0 | 0 | 976.8 | 0 | 614.9724
3624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3625 | 1048.116 | 0 | 0 | 0 | 0 | 0 | 0 | 1048.116 | 0 | 0
3626 | 1148.1467 | 0 | 0 | 0 | 0 | 0 | 0 | 1148.147 | 0 | 0
3627 | 1165.0637 | 0 | 0 | 0 | 0 | 0 | 0 | 1165.064 | 0 | 0
3628 | 1257.0037 | 0 | 0 | 0 | 0 | 0 | 0 | 1257.004 | 0 | 0
3629 | 1164.3282 | 0 | 0 | 0 | 0 | 0 | 0 | 1164.328 | 0 | 0
3630 | 1084.892 | 0 | 0 | 0 | 0 | 0 | 0 | 1084.892 | 0 | 0
3631 | 1136.1375 | 127.17 | 457.2413 | 457.2413 | 0 | 0 | 0 | 695.977 | 0 | 0
3632 | 857.2624 | 343.49 | 1525.357 | 890.5289 | -614.9724 | 0 | 19.8557 | 0 | 0 | 0
3633 | 1126.9766 | 558.77 | 2510.387 | 1170.7091 | -423.0387 | 0 | 916.6392 | 0 | 0 | 0
3634 | 1088.1963 | 474.39 | 2065.3464 | 1130.4242 | 0 | 0 | 934.9222 | 0 | 0 | 0
3635 | 1073.6523 | 647.43 | 2767.6511 | 1115.3148 | 0 | 0 | 1652.3363 | 0 | 0 | 0
3636 | 1056.4835 | 568.89 | 2432.4818 | 1097.4806 | 0 | 0 | 1335.0012 | 0 | 0 | 0
3637 | 976.002 | 408.27 | 1756.8723 | 1013.8755 | 0 | 0 | 742.9968 | 0 | 0 | 0
3638 | 1109.748 | 140.46 | 588.1359 | 588.1359 | 0 | 0 | 0 | 11.635 | 0 | 552.5901
3639 | 1130.2855 | 551.75 | 2402.8468 | 1174.1465 | -614.9724 | 0 | 613.7279 | 0 | 0 | 0
3640 | 1121.2717 | 253.22 | 1115.3865 | 1115.3865 | 0 | 0 | 0 | 47.551 | 0 | 0
3641 | 781.8035 | 84.92 | 353.8346 | 353.8346 | 0 | 0 | 0 | 441.186 | 0 | 0
3642 | 946.9489 | 32.34 | 112.5431 | 112.5431 | 0 | 0 | 0 | 838.61 | 0 | 0
3643 | 1087.8341 | 0 | 0 | 0 | 0 | 0 | 0 | 1087.834 | 0 | 0
3644 | 1190.0714 | 0 | 0 | 0 | 0 | 0 | 0 | 1190.071 | 0 | 0
3645 | 939.259 | 0 | 0 | 0 | 0 | 0 | 0 | 939.259 | 0 | 0
3646 | 1095.1893 | 0 | 0 | 0 | 0 | 0 | 0 | 948.923 | 0 | 151.9418
3647 | 1081.2144 | 0 | 0 | 0 | 0 | 0 | 0 | 489.214 | 0 | 614.9724
3648 | 159.6078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 165.8015
3649 | 82.3782 | 0 | 0 | 0 | 0 | 0 | 0 | 82.378 | 0 | 0
3650 | 157.4013 | 0 | 0 | 0 | 0 | 0 | 0 | 157.401 | 0 | 0
3651 | 100.7662 | 0 | 0 | 0 | 0 | 0 | 0 | 100.766 | 0 | 0
3652 | 105.1794 | 0 | 0 | 0 | 0 | 0 | 0 | 105.179 | 0 | 0
3653 | 78.7006 | 0 | 0 | 0 | 0 | 0 | 0 | 78.701 | 0 | 0
3654 | 81.6427 | 0 | 0 | 0 | 0 | 0 | 0 | 81.643 | 0 | 0
3655 | 78.8376 | 43.13 | 165.9823 | 81.8973 | -84.085 | 0 | 0 | 0 | 0 | 0
3656 | 193.0078 | 343.31 | 1528.6334 | 200.4976 | -614.9724 | 0 | 713.1634 | 0 | 0 | 0
3657 | 787.8808 | 216.58 | 951.6688 | 818.4535 | -133.2153 | 0 | 0 | 0 | 0 | 0
3658 | 1235.6617 | 495.58 | 2167.7289 | 1283.6105 | -205.7384 | 0 | 678.38 | 0 | 0 | 0
3659 | 1134.1783 | 370.76 | 1612.0858 | 1178.1905 | 0 | 0 | 433.8952 | 0 | 0 | 0
3660 | 928.5379 | 923.05 | 3950.777 | 964.5697 | 0 | 0 | 2986.2073 | 0 | 0 | 0
3661 | 1150.8718 | 774.81 | 3307.813 | 1195.5313 | 0 | 0 | 2112.2817 | 0 | 0 | 0
3662 | 1024.287 | 639.27 | 2768.5206 | 1064.0342 | 0 | 0 | 1704.4864 | 0 | 0 | 0
3663 | 1039.8662 | 626.09 | 2743.7056 | 1080.2177 | 0 | 0 | 1663.4879 | 0 | 0 | 0
3664 | 1200.7723 | 191.13 | 839.1963 | 839.1963 | 0 | 0 | 0 | 392.924 | 0 | 0
3665 | 1211.6653 | 143.24 | 626.3577 | 626.3577 | 0 | 0 | 0 | 608.705 | 0 | 0
3666 | 1362.6896 | 49.7 | 189.5195 | 189.5195 | 0 | 0 | 0 | 1180.249 | 0 | 0
3667 | 1236.4091 | 0 | 0 | 0 | 0 | 0 | 0 | 1236.409 | 0 | 0
3668 | 1330.5557 | 0 | 0 | 0 | 0 | 0 | 0 | 1330.556 | 0 | 0
3669 | 1363.6541 | 0 | 0 | 0 | 0 | 0 | 0 | 1363.654 | 0 | 0
3670 | 988.5389 | 0 | 0 | 0 | 0 | 0 | 0 | 682.665 | 0 | 317.7434
3671 | 1133.4363 | 0 | 0 | 0 | 0 | 0 | 0 | 541.436 | 0 | 614.9724
3672 | 1025.3149 | 0 | 0 | 0 | 0 | 0 | 0 | 1025.315 | 0 | 0
3673 | 1040.0253 | 0 | 0 | 0 | 0 | 0 | 0 | 1040.025 | 0 | 0
3674 | 1289.3666 | 0 | 0 | 0 | 0 | 0 | 0 | 1289.367 | 0 | 0
3675 | 807.601 | 0 | 0 | 0 | 0 | 0 | 0 | 807.601 | 0 | 0
3676 | 906.1606 | 0 | 0 | 0 | 0 | 0 | 0 | 906.161 | 0 | 0
3677 | 1054.7357 | 0 | 0 | 0 | 0 | 0 | 0 | 1054.736 | 0 | 0
3678 | 1198.1621 | 0 | 0 | 0 | 0 | 0 | 0 | 1198.162 | 0 | 0
3679 | 1087.0664 | 126.98 | 447.1577 | 447.1577 | 0 | 0 | 0 | 656.613 | 0 | 0
3680 | 1228.1419 | 344.9 | 1526.4748 | 1275.7997 | -250.675 | 0 | 0 | 0 | 0 | 0
3681 | 1131.3953 | 560.91 | 2518.152 | 1175.2995 | -614.9724 | 0 | 727.8801 | 0 | 0 | 0
3682 | 1253.8934 | 740.76 | 3236.0222 | 1302.551 | -172.3637 | 0 | 1761.1075 | 0 | 0 | 0
3683 | 1272.5121 | 860.99 | 3688.7448 | 1321.8915 | 0 | 0 | 2366.8533 | 0 | 0 | 0
3684 | 1338.8744 | 919.74 | 3910.6148 | 1390.8287 | 0 | 0 | 2519.7861 | 0 | 0 | 0
3685 | 1355.3308 | 780.56 | 3288.2429 | 1407.9243 | 0 | 0 | 1880.3187 | 0 | 0 | 0
3686 | 1295.2535 | 241.6 | 1037.3743 | 1037.3743 | 0 | 0 | 0 | 296.63 | 0 | 0
3687 | 1302.0681 | 259.66 | 1127.3504 | 1127.3504 | 0 | 0 | 0 | 216.83 | 0 | 0
3688 | 1469.4209 | 189.18 | 823.1281 | 823.1281 | 0 | 0 | 0 | 677.041 | 0 | 0
3689 | 1487.386 | 117.08 | 500.5377 | 500.5377 | 0 | 0 | 0 | 1005.546 | 0 | 0
3690 | 1238.9154 | 48.62 | 183.4405 | 183.4405 | 0 | 0 | 0 | 1062.327 | 0 | 0
3691 | 1209.1949 | 0 | 0 | 0 | 0 | 0 | 0 | 1209.195 | 0 | 0
3692 | 1137.1139 | 0 | 0 | 0 | 0 | 0 | 0 | 1137.114 | 0 | 0
3693 | 1054.7357 | 0 | 0 | 0 | 0 | 0 | 0 | 1054.736 | 0 | 0
3694 | 1102.5445 | 0 | 0 | 0 | 0 | 0 | 0 | 796.671 | 0 | 317.7434
3695 | 1087.8341 | 0 | 0 | 0 | 0 | 0 | 0 | 495.834 | 0 | 614.9724
3696 | 1305.548 | 0 | 0 | 0 | 0 | 0 | 0 | 1305.548 | 0 | 0
3697 | 1315.1098 | 0 | 0 | 0 | 0 | 0 | 0 | 1315.11 | 0 | 0
3698 | 1071.6526 | 0 | 0 | 0 | 0 | 0 | 0 | 1071.653 | 0 | 0
3699 | 1255.5327 | 0 | 0 | 0 | 0 | 0 | 0 | 1255.533 | 0 | 0
3700 | 806.1299 | 0 | 0 | 0 | 0 | 0 | 0 | 806.13 | 0 | 0
3701 | 750.2304 | 0 | 0 | 0 | 0 | 0 | 0 | 750.23 | 0 | 0
3702 | 706.0992 | 0 | 0 | 0 | 0 | 0 | 0 | 706.099 | 0 | 0
3703 | 1144.1924 | 34.29 | 125.5074 | 125.5074 | 0 | 0 | 0 | 1023.374 | 0 | 0
3704 | 1174.6209 | 93.42 | 395.8594 | 395.8594 | 0 | 0 | 0 | 793.549 | 0 | 0
3705 | 1421.8944 | 235.41 | 1040.8813 | 1040.8813 | 0 | 0 | 0 | 419.895 | 0 | 0
3706 | 1445.488 | 528.04 | 2322.6646 | 1501.5798 | -614.9724 | 0 | 206.1124 | 0 | 0 | 0
3707 | 1314.3991 | 700.66 | 3035.2181 | 1365.4039 | -423.0387 | 0 | 1246.7755 | 0 | 0 | 0
3708 | 1630.578 | 639.12 | 2768.3845 | 1693.8522 | 0 | 0 | 1074.5324 | 0 | 0 | 0
3709 | 1339.1925 | 911.23 | 3957.2166 | 1391.159 | 0 | 0 | 2566.0576 | 0 | 0 | 0
3710 | 1441.9686 | 832.37 | 3654.4621 | 1497.9242 | 0 | 0 | 2156.5379 | 0 | 0 | 0
3711 | 1484.2371 | 690.27 | 3088.5099 | 1541.8324 | 0 | 0 | 1546.6774 | 0 | 0 | 0
3712 | 1687.8042 | 499.34 | 2283.5079 | 1753.2988 | 0 | 0 | 530.2091 | 0 | 0 | 0
3713 | 1368.332 | 280.26 | 1206.9945 | 1206.9945 | 0 | 0 | 0 | 206.425 | 0 | 0
3714 | 1435.4445 | 78.14 | 278.8869 | 278.8869 | 0 | 0 | 0 | 1166.976 | 0 | 0
3715 | 1408.5208 | 0 | 0 | 0 | 0 | 0 | 0 | 1408.521 | 0 | 0
3716 | 1324.6715 | 0 | 0 | 0 | 0 | 0 | 0 | 1324.672 | 0 | 0
3717 | 1376.1579 | 0 | 0 | 0 | 0 | 0 | 0 | 1376.158 | 0 | 0
3718 | 889.2437 | 0 | 0 | 0 | 0 | 0 | 0 | 583.37 | 0 | 317.7434
3719 | 1277.5983 | 0 | 0 | 0 | 0 | 0 | 0 | 685.598 | 0 | 614.9724
3720 | 914.2514 | 0 | 0 | 0 | 0 | 0 | 0 | 914.251 | 0 | 0
3721 | 1040.0253 | 0 | 0 | 0 | 0 | 0 | 0 | 1040.025 | 0 | 0
3722 | 1225.3763 | 0 | 0 | 0 | 0 | 0 | 0 | 1225.376 | 0 | 0
3723 | 1041.4963 | 0 | 0 | 0 | 0 | 0 | 0 | 1041.496 | 0 | 0
3724 | 1069.4461 | 0 | 0 | 0 | 0 | 0 | 0 | 1069.446 | 0 | 0
3725 | 1206.9883 | 0 | 0 | 0 | 0 | 0 | 0 | 1206.988 | 0 | 0
3726 | 1139.3205 | 0 | 0 | 0 | 0 | 0 | 0 | 1139.32 | 0 | 0
3727 | 968.3737 | 108.89 | 448.3938 | 448.3938 | 0 | 0 | 0 | 536.73 | 0 | 0
3728 | 1216.8397 | 291.36 | 1303.381 | 1264.0592 | -39.3219 | 0 | 0 | 0 | 0 | 0
3729 | 1270.5584 | 559.93 | 2506.5725 | 1319.8627 | -614.9724 | 0 | 571.7374 | 0 | 0 | 0
3730 | 1288.7009 | 740.58 | 3219.9363 | 1338.7087 | -383.7168 | 0 | 1497.5108 | 0 | 0 | 0
3731 | 1265.5835 | 718.71 | 3048.466 | 1314.6947 | 0 | 0 | 1733.7714 | 0 | 0 | 0
3732 | 1527.2199 | 750.15 | 3167.3074 | 1586.4834 | 0 | 0 | 1580.824 | 0 | 0 | 0
3733 | 1609.8915 | 654.22 | 2789.9709 | 1672.3624 | 0 | 0 | 1117.6085 | 0 | 0 | 0
3734 | 1684.8217 | 741.13 | 3164.5691 | 1750.2001 | 0 | 0 | 1414.369 | 0 | 0 | 0
3735 | 1461.4939 | 648.48 | 2816.7378 | 1518.2069 | 0 | 0 | 1298.5309 | 0 | 0 | 0
3736 | 1490.238 | 492.84 | 2236.7398 | 1548.0663 | 0 | 0 | 688.6735 | 0 | 0 | 0
3737 | 1239.2694 | 256.74 | 1136.7298 | 1136.7298 | 0 | 0 | 0 | 145.002 | 0 | 0
3738 | 1422.6934 | 54.26 | 207.895 | 207.895 | 0 | 0 | 0 | 1222.564 | 0 | 0
3739 | 1531.3527 | 0 | 0 | 0 | 0 | 0 | 0 | 1531.353 | 0 | 0
3740 | 1093.7182 | 0 | 0 | 0 | 0 | 0 | 0 | 1093.718 | 0 | 0
3741 | 818.6338 | 0 | 0 | 0 | 0 | 0 | 0 | 818.634 | 0 | 0
3742 | 913.5158 | 0 | 0 | 0 | 0 | 0 | 0 | 607.642 | 0 | 317.7434
3743 | 1149.6178 | 0 | 0 | 0 | 0 | 0 | 0 | 557.618 | 0 | 614.9724
3744 | 1036.3477 | 0 | 0 | 0 | 0 | 0 | 0 | 1036.348 | 0 | 0
3745 | 967.2088 | 0 | 0 | 0 | 0 | 0 | 0 | 967.209 | 0 | 0
3746 | 1274.6562 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.656 | 0 | 0
3747 | 962.0602 | 0 | 0 | 0 | 0 | 0 | 0 | 962.06 | 0 | 0
3748 | 1158.444 | 0 | 0 | 0 | 0 | 0 | 0 | 1158.444 | 0 | 0
3749 | 1215.0791 | 0 | 0 | 0 | 0 | 0 | 0 | 1215.079 | 0 | 0
3750 | 663.439 | 0 | 0 | 0 | 0 | 0 | 0 | 663.439 | 0 | 0
3751 | 831.19 | 102.83 | 425.1277 | 425.1277 | 0 | 0 | 0 | 421.943 | 0 | 0
3752 | 900.2029 | 276.02 | 1233.7967 | 935.1352 | -298.6616 | 0 | 0 | 0 | 0 | 0
3753 | 1016.1898 | 457.32 | 2023.0671 | 1055.623 | -614.9724 | 0 | 352.4716 | 0 | 0 | 0
3754 | 1501.8804 | 460.94 | 2005.2422 | 1560.1611 | -124.3771 | 0 | 320.704 | 0 | 0 | 0
3755 | 1433.3713 | 860.19 | 3664.2726 | 1488.9926 | 0 | 0 | 2175.28 | 0 | 0 | 0
3756 | 1371.731 | 522.16 | 2235.995 | 1424.9607 | 0 | 0 | 811.0343 | 0 | 0 | 0
3757 | 1529.9046 | 252.45 | 1084.5267 | 1084.5267 | 0 | 0 | 0 | 485.89 | 0 | 0
3758 | 1387.7571 | 88.02 | 355.3128 | 355.3128 | 0 | 0 | 0 | 1045.717 | 0 | 0
3759 | 1085.9861 | 142.92 | 606.1966 | 606.1966 | 0 | 0 | 0 | 502.434 | 0 | 0
3760 | 1513.4915 | 119.23 | 505.9727 | 505.9727 | 0 | 0 | 0 | 1026.42 | 0 | 0
3761 | 1215.0892 | 78.8 | 325.4887 | 325.4887 | 0 | 0 | 0 | 901.759 | 0 | 0
3762 | 1339.0123 | 19.59 | 57.1883 | 57.1883 | 0 | 0 | 0 | 1283.96 | 0 | 0
3763 | 1233.4671 | 0 | 0 | 0 | 0 | 0 | 0 | 1233.467 | 0 | 0
3764 | 1164.3282 | 0 | 0 | 0 | 0 | 0 | 0 | 1164.328 | 0 | 0
3765 | 1034.1411 | 0 | 0 | 0 | 0 | 0 | 0 | 1034.141 | 0 | 0
3766 | 1329.8202 | 0 | 0 | 0 | 0 | 0 | 0 | 1023.947 | 0 | 317.7434
3767 | 1057.6778 | 0 | 0 | 0 | 0 | 0 | 0 | 465.678 | 0 | 614.9724
3768 | 1348.9437 | 0 | 0 | 0 | 0 | 0 | 0 | 1348.944 | 0 | 0
3769 | 972.3574 | 0 | 0 | 0 | 0 | 0 | 0 | 972.357 | 0 | 0
3770 | 1018.6952 | 0 | 0 | 0 | 0 | 0 | 0 | 1018.695 | 0 | 0
3771 | 1329.8202 | 0 | 0 | 0 | 0 | 0 | 0 | 1329.82 | 0 | 0
3772 | 1226.8474 | 0 | 0 | 0 | 0 | 0 | 0 | 1226.847 | 0 | 0
3773 | 759.7922 | 0 | 0 | 0 | 0 | 0 | 0 | 759.792 | 0 | 0
3774 | 961.3246 | 0 | 0 | 0 | 0 | 0 | 0 | 961.325 | 0 | 0
3775 | 883.3154 | 55.97 | 223.7918 | 223.7918 | 0 | 0 | 0 | 667.884 | 0 | 0
3776 | 819.4309 | 342.89 | 1484.8872 | 851.2288 | -614.9724 | 0 | 18.686 | 0 | 0 | 0
3777 | 938.7295 | 436.58 | 1878.0499 | 975.1572 | -423.0387 | 0 | 479.854 | 0 | 0 | 0
3778 | 1175.0134 | 738.05 | 3061.394 | 1220.6091 | 0 | 0 | 1840.7849 | 0 | 0 | 0
3779 | 1296.981 | 505.07 | 2108.9856 | 1347.31 | 0 | 0 | 761.6755 | 0 | 0 | 0
3780 | 1264.4646 | 917.77 | 3681.0389 | 1313.5312 | 0 | 0 | 2367.5077 | 0 | 0 | 0
3781 | 1379.1589 | 909.81 | 3695.0908 | 1432.6769 | 0 | 0 | 2262.4139 | 0 | 0 | 0
3782 | 1238.6166 | 465.71 | 1973.6324 | 1286.6812 | 0 | 0 | 686.9512 | 0 | 0 | 0
3783 | 1071.4449 | 615.89 | 2616.289 | 1113.0222 | 0 | 0 | 1503.2668 | 0 | 0 | 0
3784 | 1163.5669 | 474.52 | 2073.419 | 1208.7189 | 0 | 0 | 864.7 | 0 | 0 | 0
3785 | 930.6139 | 200.3 | 872.9533 | 872.9533 | 0 | 0 | 0 | 90.27 | 0 | 0
3786 | 930.0798 | 75.56 | 230.4921 | 230.4921 | 0 | 0 | 0 | 708.198 | 0 | 0
3787 | 892.9213 | 0 | 0 | 0 | 0 | 0 | 0 | 892.921 | 0 | 0
3788 | 1206.2528 | 0 | 0 | 0 | 0 | 0 | 0 | 1206.253 | 0 | 0
3789 | 1006.9269 | 0 | 0 | 0 | 0 | 0 | 0 | 1006.927 | 0 | 0
3790 | 984.8613 | 0 | 0 | 0 | 0 | 0 | 0 | 678.988 | 0 | 317.7434
3791 | 1077.5368 | 0 | 0 | 0 | 0 | 0 | 0 | 485.537 | 0 | 614.9724
3792 | 956.176 | 0 | 0 | 0 | 0 | 0 | 0 | 956.176 | 0 | 0
3793 | 959.8536 | 0 | 0 | 0 | 0 | 0 | 0 | 959.854 | 0 | 0
3794 | 1045.1739 | 0 | 0 | 0 | 0 | 0 | 0 | 1045.174 | 0 | 0
3795 | 993.6875 | 0 | 0 | 0 | 0 | 0 | 0 | 993.688 | 0 | 0
3796 | 951.0274 | 0 | 0 | 0 | 0 | 0 | 0 | 951.027 | 0 | 0
3797 | 970.1509 | 0 | 0 | 0 | 0 | 0 | 0 | 970.151 | 0 | 0
3798 | 989.2744 | 0 | 0 | 0 | 0 | 0 | 0 | 989.274 | 0 | 0
3799 | 814.7659 | 121.82 | 433.3841 | 433.3841 | 0 | 0 | 0 | 397.571 | 0 | 0
3800 | 269.8053 | 295.28 | 1314.0672 | 280.2747 | -614.9724 | 0 | 418.8201 | 0 | 0 | 0
3801 | 129.9866 | 549.81 | 2450.8915 | 135.0311 | -423.0387 | 0 | 1892.8217 | 0 | 0 | 0
3802 | 207.7449 | 727.04 | 3146.6975 | 215.8065 | 0 | 0 | 2930.891 | 0 | 0 | 0
3803 | 159.9664 | 654.13 | 2762.6545 | 166.1745 | 0 | 0 | 2596.48 | 0 | 0 | 0
3804 | 171.8487 | 777.03 | 3227.7139 | 178.5176 | 0 | 0 | 3049.1963 | 0 | 0 | 0
3805 | 132.4947 | 745.97 | 3104.9323 | 137.6354 | 0 | 0 | 2967.2969 | 0 | 0 | 0
3806 | 124.5833 | 796.66 | 3361.6657 | 129.4174 | 0 | 0 | 3232.2482 | 0 | 0 | 0
3807 | 178.8941 | 587.55 | 2515.715 | 185.8359 | 0 | 0 | 2329.8791 | 0 | 0 | 0
3808 | 197.9358 | 441.13 | 1931.1692 | 205.6169 | 0 | 0 | 1725.5523 | 0 | 0 | 0
3809 | 169.2818 | 163.02 | 705.9665 | 175.8509 | 0 | 0 | 530.1156 | 0 | 0 | 0
3810 | 186.6658 | 55.15 | 209.6692 | 193.9095 | 0 | 0 | 15.7597 | 0 | 0 | 0
3811 | 128.716 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 133.7108
3812 | 181.6734 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 188.7228
3813 | 183.1445 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 190.2509
3814 | 100.0307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.9127
3815 | 90.469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.9796
3816 | 94.1466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.8004
3817 | 85.3203 | 0 | 0 | 0 | 0 | 0 | 0 | 85.32 | 0 | 0
3818 | 91.2045 | 0 | 0 | 0 | 0 | 0 | 0 | 91.204 | 0 | 0
3819 | 86.7914 | 0 | 0 | 0 | 0 | 0 | 0 | 86.791 | 0 | 0
3820 | 90.469 | 0 | 0 | 0 | 0 | 0 | 0 | 90.469 | 0 | 0
3821 | 85.3203 | 0 | 0 | 0 | 0 | 0 | 0 | 51.683 | 0 | 34.9433
3822 | 86.0558 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.3954
3823 | 73.9979 | 31.35 | 112.2771 | 76.8695 | -35.4077 | 0 | 0 | 0 | 0 | 0
3824 | 92.8447 | 86.15 | 361.0376 | 96.4468 | -264.5908 | 0 | 0 | 0 | 0 | 0
3825 | 624.5034 | 215.31 | 942.0702 | 648.7367 | -293.3335 | 0 | 0 | 0 | 0 | 0
3826 | 1169.1854 | 340.87 | 1481.9007 | 1214.5549 | -267.3458 | 0 | 0 | 0 | 0 | 0
3827 | 1182.7428 | 648.57 | 2763.7359 | 1228.638 | -177.3344 | 0 | 1357.7635 | 0 | 0 | 0
3828 | 1218.137 | 678.22 | 2871.8921 | 1265.4065 | 0 | 0 | 1606.4856 | 0 | 0 | 0
3829 | 1041.8558 | 673.51 | 2856.3734 | 1082.285 | 0 | 0 | 1774.0884 | 0 | 0 | 0
3830 | 1119.2978 | 338.48 | 1457.8596 | 1162.731 | 0 | 0 | 295.1286 | 0 | 0 | 0
3831 | 1117.0011 | 508.52 | 2204.3665 | 1160.3459 | 0 | 0 | 1044.0206 | 0 | 0 | 0
3832 | 1182.9589 | 367.03 | 1616.1901 | 1228.8634 | 0 | 0 | 387.3267 | 0 | 0 | 0
3833 | 1307.3767 | 195.25 | 854.5488 | 854.5488 | 0 | 0 | 0 | 484.749 | 0 | 0
3834 | 1228.2872 | 61.82 | 235.9749 | 235.9749 | 0 | 0 | 0 | 1001.128 | 0 | 0
3835 | 1151.8243 | 0 | 0 | 0 | 0 | 0 | 0 | 1151.824 | 0 | 0
3836 | 1090.7762 | 0 | 0 | 0 | 0 | 0 | 0 | 1090.776 | 0 | 0
3837 | 1351.8858 | 0 | 0 | 0 | 0 | 0 | 0 | 1351.886 | 0 | 0
3838 | 1092.9827 | 0 | 0 | 0 | 0 | 0 | 0 | 787.109 | 0 | 317.7434
3839 | 716.3965 | 0 | 0 | 0 | 0 | 0 | 0 | 124.396 | 0 | 614.9724
3840 | 1042.2318 | 0 | 0 | 0 | 0 | 0 | 0 | 1042.232 | 0 | 0
3841 | 806.8654 | 0 | 0 | 0 | 0 | 0 | 0 | 806.865 | 0 | 0
3842 | 816.4272 | 0 | 0 | 0 | 0 | 0 | 0 | 816.427 | 0 | 0
3843 | 912.0448 | 0 | 0 | 0 | 0 | 0 | 0 | 912.045 | 0 | 0
3844 | 945.1432 | 0 | 0 | 0 | 0 | 0 | 0 | 945.143 | 0 | 0
3845 | 937.788 | 0 | 0 | 0 | 0 | 0 | 0 | 937.788 | 0 | 0
3846 | 909.1027 | 0 | 0 | 0 | 0 | 0 | 0 | 909.103 | 0 | 0
3847 | 944.3424 | 103.23 | 425.1579 | 425.1579 | 0 | 0 | 0 | 535.067 | 0 | 0
3848 | 881.4527 | 290.46 | 1304.3035 | 915.6576 | -388.6459 | 0 | 0 | 0 | 0 | 0
3849 | 933.853 | 451.09 | 2016.2837 | 970.0909 | -614.9724 | 0 | 431.2203 | 0 | 0 | 0
3850 | 994.1031 | 611.95 | 2680.4965 | 1032.6789 | -34.3927 | 0 | 1613.4248 | 0 | 0 | 0
3851 | 1339.2413 | 689.53 | 2974.6714 | 1391.2109 | 0 | 0 | 1583.4605 | 0 | 0 | 0
3852 | 1246.3699 | 762.05 | 3250.2455 | 1294.7351 | 0 | 0 | 1955.5105 | 0 | 0 | 0
3853 | 1003.5325 | 752.34 | 3205.6839 | 1042.4748 | 0 | 0 | 2163.2091 | 0 | 0 | 0
3854 | 1101.4945 | 705.98 | 3025.7266 | 1144.2382 | 0 | 0 | 1881.4884 | 0 | 0 | 0
3855 | 1463.9441 | 548.95 | 2389.9957 | 1520.753 | 0 | 0 | 869.2427 | 0 | 0 | 0
3856 | 1017.2747 | 369.07 | 1631.8615 | 1056.7491 | 0 | 0 | 575.1124 | 0 | 0 | 0
3857 | 1145.9282 | 59.52 | 236.6667 | 236.6667 | 0 | 0 | 0 | 918.102 | 0 | 0
3858 | 1215.9093 | 12.73 | 27.6956 | 27.6956 | 0 | 0 | 0 | 1189.249 | 0 | 0
3859 | 1031.199 | 0 | 0 | 0 | 0 | 0 | 0 | 1031.199 | 0 | 0
3860 | 1098.8669 | 0 | 0 | 0 | 0 | 0 | 0 | 1098.867 | 0 | 0
3861 | 1268.772 | 0 | 0 | 0 | 0 | 0 | 0 | 1268.772 | 0 | 0
3862 | 1276.1272 | 0 | 0 | 0 | 0 | 0 | 0 | 970.254 | 0 | 317.7434
3863 | 1315.8453 | 0 | 0 | 0 | 0 | 0 | 0 | 723.845 | 0 | 614.9724
3864 | 1015.0176 | 0 | 0 | 0 | 0 | 0 | 0 | 1015.018 | 0 | 0
3865 | 1181.9806 | 0 | 0 | 0 | 0 | 0 | 0 | 1181.981 | 0 | 0
3866 | 934.1104 | 0 | 0 | 0 | 0 | 0 | 0 | 934.11 | 0 | 0
3867 | 1097.3959 | 0 | 0 | 0 | 0 | 0 | 0 | 1097.396 | 0 | 0
3868 | 1369.5383 | 0 | 0 | 0 | 0 | 0 | 0 | 1369.538 | 0 | 0
3869 | 1001.0427 | 0 | 0 | 0 | 0 | 0 | 0 | 1001.043 | 0 | 0
3870 | 1035.6122 | 0 | 0 | 0 | 0 | 0 | 0 | 1035.612 | 0 | 0
3871 | 734.6806 | 98.27 | 404.6124 | 404.6124 | 0 | 0 | 0 | 345.183 | 0 | 0
3872 | 858.4429 | 262.71 | 1176.4599 | 891.7547 | -284.7052 | 0 | 0 | 0 | 0 | 0
3873 | 945.9468 | 408.02 | 1818.6552 | 982.6532 | -614.9724 | 0 | 221.0296 | 0 | 0 | 0
3874 | 1313.9909 | 539.21 | 2361.0817 | 1364.9801 | -138.3335 | 0 | 857.7681 | 0 | 0 | 0
3875 | 1203.8265 | 645.5 | 2782.3419 | 1250.5412 | 0 | 0 | 1531.8007 | 0 | 0 | 0
3876 | 1170.5985 | 755.74 | 3218.6648 | 1216.0228 | 0 | 0 | 2002.6421 | 0 | 0 | 0
3877 | 1180.2871 | 740.27 | 3153.564 | 1226.0877 | 0 | 0 | 1927.4762 | 0 | 0 | 0
3878 | 935.0749 | 675.89 | 2901.5032 | 971.3604 | 0 | 0 | 1930.1429 | 0 | 0 | 0
3879 | 1443.3311 | 583.12 | 2538.0223 | 1499.3391 | 0 | 0 | 1038.6832 | 0 | 0 | 0
3880 | 1115.1485 | 154.88 | 665.8873 | 665.8873 | 0 | 0 | 0 | 474.136 | 0 | 0
3881 | 1294.3433 | 91.12 | 380.4892 | 380.4892 | 0 | 0 | 0 | 928.068 | 0 | 0
3882 | 1231.2495 | 55.13 | 211.3074 | 211.3074 | 0 | 0 | 0 | 1027.836 | 0 | 0
3883 | 1327.6136 | 0 | 0 | 0 | 0 | 0 | 0 | 1327.614 | 0 | 0
3884 | 1377.629 | 0 | 0 | 0 | 0 | 0 | 0 | 1377.629 | 0 | 0
3885 | 1547.5341 | 0 | 0 | 0 | 0 | 0 | 0 | 1547.534 | 0 | 0
3886 | 1445.2968 | 0 | 0 | 0 | 0 | 0 | 0 | 1139.423 | 0 | 317.7434
3887 | 1164.3282 | 0 | 0 | 0 | 0 | 0 | 0 | 572.328 | 0 | 614.9724
3888 | 1151.8243 | 0 | 0 | 0 | 0 | 0 | 0 | 1151.824 | 0 | 0
3889 | 1028.257 | 0 | 0 | 0 | 0 | 0 | 0 | 1028.257 | 0 | 0
3890 | 1179.7741 | 0 | 0 | 0 | 0 | 0 | 0 | 1179.774 | 0 | 0
3891 | 1259.2103 | 0 | 0 | 0 | 0 | 0 | 0 | 1259.21 | 0 | 0
3892 | 1282.0114 | 0 | 0 | 0 | 0 | 0 | 0 | 1282.011 | 0 | 0
3893 | 1181.9806 | 0 | 0 | 0 | 0 | 0 | 0 | 1181.981 | 0 | 0
3894 | 970.8864 | 0 | 0 | 0 | 0 | 0 | 0 | 970.886 | 0 | 0
3895 | 956.4739 | 106.56 | 436.3531 | 436.3531 | 0 | 0 | 0 | 536.421 | 0 | 0
3896 | 799.5406 | 280.31 | 1259.6224 | 830.5659 | -429.0565 | 0 | 0 | 0 | 0 | 0
3897 | 1009.7099 | 324.48 | 1446.3517 | 1048.8915 | -397.4602 | 0 | 0 | 0 | 0 | 0
3898 | 1208.6635 | 540.8 | 2375.9729 | 1255.5649 | -211.4955 | 0 | 908.9126 | 0 | 0 | 0
3899 | 1010.5833 | 392.88 | 1715.8707 | 1049.7995 | 0 | 0 | 666.0712 | 0 | 0 | 0
3900 | 1237.7156 | 344.57 | 1498.1704 | 1285.7453 | 0 | 0 | 212.4252 | 0 | 0 | 0
3901 | 1291.5998 | 675.07 | 2901.5094 | 1341.7202 | 0 | 0 | 1559.7892 | 0 | 0 | 0
3902 | 1072.2006 | 69.21 | 272.3341 | 272.3341 | 0 | 0 | 0 | 810.04 | 0 | 0
3903 | 1315.8048 | 51.04 | 193.4701 | 193.4701 | 0 | 0 | 0 | 1129.561 | 0 | 0
3904 | 1295.1505 | 59.61 | 235.6082 | 235.6082 | 0 | 0 | 0 | 1068.344 | 0 | 0
3905 | 1370.3069 | 33.32 | 120.172 | 120.172 | 0 | 0 | 0 | 1254.623 | 0 | 0
3906 | 1281.582 | 24.49 | 79.1413 | 79.1413 | 0 | 0 | 0 | 1205.397 | 0 | 0
3907 | 1545.3275 | 0 | 0 | 0 | 0 | 0 | 0 | 1545.328 | 0 | 0
3908 | 1218.0211 | 0 | 0 | 0 | 0 | 0 | 0 | 1218.021 | 0 | 0
3909 | 1410.7274 | 0 | 0 | 0 | 0 | 0 | 0 | 1410.727 | 0 | 0
3910 | 1444.5613 | 0 | 0 | 0 | 0 | 0 | 0 | 1138.688 | 0 | 317.7434
3911 | 1081.9499 | 0 | 0 | 0 | 0 | 0 | 0 | 489.95 | 0 | 614.9724
3912 | 1302.6059 | 0 | 0 | 0 | 0 | 0 | 0 | 1302.606 | 0 | 0
3913 | 1140.056 | 0 | 0 | 0 | 0 | 0 | 0 | 1140.056 | 0 | 0
3914 | 1240.0867 | 0 | 0 | 0 | 0 | 0 | 0 | 1240.087 | 0 | 0
3915 | 1393.0749 | 0 | 0 | 0 | 0 | 0 | 0 | 1393.075 | 0 | 0
3916 | 1256.2682 | 0 | 0 | 0 | 0 | 0 | 0 | 1256.268 | 0 | 0
3917 | 1270.2431 | 0 | 0 | 0 | 0 | 0 | 0 | 1270.243 | 0 | 0
3918 | 1252.5906 | 0 | 0 | 0 | 0 | 0 | 0 | 1252.591 | 0 | 0
3919 | 624.6762 | 57.97 | 233.3072 | 233.3072 | 0 | 0 | 0 | 400.084 | 0 | 0
3920 | 1045.7035 | 162.14 | 712.9857 | 712.9857 | 0 | 0 | 0 | 359.351 | 0 | 0
3921 | 811.5093 | 356.2 | 1577.7076 | 843.0004 | -614.9724 | 0 | 119.7347 | 0 | 0 | 0
3922 | 397.7894 | 464.72 | 2034.9479 | 413.2251 | -423.0387 | 0 | 1198.6841 | 0 | 0 | 0
3923 | 357.9482 | 490.4 | 2137.4675 | 371.8381 | 0 | 0 | 1765.6294 | 0 | 0 | 0
3924 | 364.5053 | 610.54 | 2646.621 | 378.6495 | 0 | 0 | 2267.9715 | 0 | 0 | 0
3925 | 782.6071 | 631.74 | 2742.8601 | 812.9759 | 0 | 0 | 1929.8842 | 0 | 0 | 0
3926 | 1248.8063 | 245.32 | 1068.873 | 1068.873 | 0 | 0 | 0 | 219.862 | 0 | 0
3927 | 1519.8933 | 182.17 | 791.2223 | 791.2223 | 0 | 0 | 0 | 758.227 | 0 | 0
3928 | 1361.4245 | 82.28 | 340.8059 | 340.8059 | 0 | 0 | 0 | 1033.349 | 0 | 0
3929 | 1399.7203 | 158.95 | 702.0627 | 702.0627 | 0 | 0 | 0 | 723.883 | 0 | 0
3930 | 1546.8023 | 78.39 | 294.6352 | 294.6352 | 0 | 0 | 0 | 1263.173 | 0 | 0
3931 | 1616.673 | 0 | 0 | 0 | 0 | 0 | 0 | 1616.673 | 0 | 0
3932 | 1468.8335 | 0 | 0 | 0 | 0 | 0 | 0 | 1468.833 | 0 | 0
3933 | 1634.3255 | 0 | 0 | 0 | 0 | 0 | 0 | 1634.325 | 0 | 0
3934 | 1700.5223 | 0 | 0 | 0 | 0 | 0 | 0 | 1394.649 | 0 | 317.7434
3935 | 1246.7064 | 0 | 0 | 0 | 0 | 0 | 0 | 654.706 | 0 | 614.9724
3936 | 1177.5675 | 0 | 0 | 0 | 0 | 0 | 0 | 1177.568 | 0 | 0
3937 | 1148.1467 | 0 | 0 | 0 | 0 | 0 | 0 | 1148.147 | 0 | 0
3938 | 1455.5941 | 0 | 0 | 0 | 0 | 0 | 0 | 1455.594 | 0 | 0
3939 | 1526.204 | 0 | 0 | 0 | 0 | 0 | 0 | 1526.204 | 0 | 0
3940 | 902.483 | 0 | 0 | 0 | 0 | 0 | 0 | 902.483 | 0 | 0
3941 | 1237.1447 | 0 | 0 | 0 | 0 | 0 | 0 | 1237.145 | 0 | 0
3942 | 1238.6157 | 0 | 0 | 0 | 0 | 0 | 0 | 1238.616 | 0 | 0
3943 | 993.8319 | 64.22 | 262.3927 | 262.3927 | 0 | 0 | 0 | 741.241 | 0 | 0
3944 | 1094.5292 | 179.86 | 804.3341 | 804.3341 | 0 | 0 | 0 | 320.242 | 0 | 0
3945 | 975.5698 | 296.84 | 1332.3118 | 1013.4267 | -318.885 | 0 | 0 | 0 | 0 | 0
3946 | 1525.9328 | 449.35 | 1997.5602 | 1585.1464 | -412.4138 | 0 | 0 | 0 | 0 | 0
3947 | 1595.194 | 578.31 | 2541.0265 | 1657.0951 | -306.7123 | 0 | 577.2191 | 0 | 0 | 0
3948 | 1689.2072 | 533.38 | 2335.6341 | 1754.7563 | 0 | 0 | 580.8778 | 0 | 0 | 0
3949 | 1412.9376 | 512.79 | 2246.2615 | 1467.7667 | 0 | 0 | 778.4948 | 0 | 0 | 0
3950 | 1322.0172 | 588.91 | 2585.1747 | 1373.3175 | 0 | 0 | 1211.8572 | 0 | 0 | 0
3951 | 1567.5485 | 560.65 | 2491.1005 | 1628.3763 | 0 | 0 | 862.7242 | 0 | 0 | 0
3952 | 1329.2253 | 400.9 | 1809.6425 | 1380.8052 | 0 | 0 | 428.8373 | 0 | 0 | 0
3953 | 1391.3492 | 144.34 | 635.6602 | 635.6602 | 0 | 0 | 0 | 779.434 | 0 | 0
3954 | 1660.1588 | 51.65 | 200.6742 | 200.6742 | 0 | 0 | 0 | 1466.981 | 0 | 0
3955 | 1308.4901 | 0 | 0 | 0 | 0 | 0 | 0 | 1308.49 | 0 | 0
3956 | 1471.04 | 0 | 0 | 0 | 0 | 0 | 0 | 1471.04 | 0 | 0
3957 | 1597.5495 | 0 | 0 | 0 | 0 | 0 | 0 | 1597.549 | 0 | 0
3958 | 1294.5152 | 0 | 0 | 0 | 0 | 0 | 0 | 988.642 | 0 | 317.7434
3959 | 1450.4455 | 0 | 0 | 0 | 0 | 0 | 0 | 858.445 | 0 | 614.9724
3960 | 1306.2835 | 0 | 0 | 0 | 0 | 0 | 0 | 1306.284 | 0 | 0
3961 | 956.176 | 0 | 0 | 0 | 0 | 0 | 0 | 956.176 | 0 | 0
3962 | 976.035 | 0 | 0 | 0 | 0 | 0 | 0 | 976.035 | 0 | 0
3963 | 779.6512 | 0 | 0 | 0 | 0 | 0 | 0 | 779.651 | 0 | 0
3964 | 1012.811 | 0 | 0 | 0 | 0 | 0 | 0 | 1012.811 | 0 | 0
3965 | 668.5877 | 0 | 0 | 0 | 0 | 0 | 0 | 668.588 | 0 | 0
3966 | 831.1376 | 0 | 0 | 0 | 0 | 0 | 0 | 831.138 | 0 | 0
3967 | 843.9182 | 55.91 | 225.028 | 225.028 | 0 | 0 | 0 | 627.296 | 0 | 0
3968 | 837.4805 | 155 | 686.7455 | 686.7455 | 0 | 0 | 0 | 176.389 | 0 | 0
3969 | 846.0043 | 286.97 | 1285.8865 | 878.833 | -407.0536 | 0 | 0 | 0 | 0 | 0
3970 | 975.8383 | 412.96 | 1835.8589 | 1013.7051 | -614.9724 | 0 | 207.1813 | 0 | 0 | 0
3971 | 936.9532 | 625.9 | 2744.8473 | 973.3112 | -15.9851 | 0 | 1755.5509 | 0 | 0 | 0
3972 | 911.1879 | 534.32 | 2339.1172 | 946.5464 | 0 | 0 | 1392.5707 | 0 | 0 | 0
3973 | 1051.1298 | 479.88 | 2102.5928 | 1091.9188 | 0 | 0 | 1010.6739 | 0 | 0 | 0
3974 | 1012.9324 | 430 | 1890.7649 | 1052.2386 | 0 | 0 | 838.5263 | 0 | 0 | 0
3975 | 1027.0912 | 465.07 | 2059.7275 | 1066.947 | 0 | 0 | 992.7805 | 0 | 0 | 0
3976 | 478.6691 | 237.27 | 1054.7088 | 497.2436 | 0 | 0 | 557.4652 | 0 | 0 | 0
3977 | 176.7969 | 172.93 | 766.6847 | 183.6576 | 0 | 0 | 583.0271 | 0 | 0 | 0
3978 | 236.4577 | 41.04 | 153.4741 | 153.4741 | 0 | 0 | 0 | 0 | 0 | 92.1596
3979 | 138.2778 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 143.6438
3980 | 145.633 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151.2843
3981 | 115.4766 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.9581
3982 | 110.328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.6093
3983 | 105.9149 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.025
3984 | 106.6504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.7885
3985 | 98.5597 | 0 | 0 | 0 | 0 | 0 | 0 | 98.56 | 0 | 0
3986 | 108.1214 | 0 | 0 | 0 | 0 | 0 | 0 | 108.121 | 0 | 0
3987 | 88.9979 | 0 | 0 | 0 | 0 | 0 | 0 | 88.998 | 0 | 0
3988 | 94.8821 | 0 | 0 | 0 | 0 | 0 | 0 | 94.882 | 0 | 0
3989 | 88.9979 | 0 | 0 | 0 | 0 | 0 | 0 | 88.998 | 0 | 0
3990 | 93.411 | 0 | 0 | 0 | 0 | 0 | 0 | 6.535 | 0 | 90.2472
3991 | 80.6148 | 34.3 | 126.1275 | 83.7422 | -42.3853 | 0 | 0 | 0 | 0 | 0
3992 | 145.6072 | 93.19 | 396.9481 | 151.2583 | -245.6898 | 0 | 0 | 0 | 0 | 0
3993 | 662.3137 | 264.57 | 1179.837 | 688.0149 | -491.8221 | 0 | 0 | 0 | 0 | 0
3994 | 881.3451 | 498.6 | 2207.5307 | 915.5454 | -258.1139 | 0 | 1033.8715 | 0 | 0 | 0
3995 | 1021.1849 | 477.88 | 2102.6696 | 1060.8118 | 0 | 0 | 1041.8578 | 0 | 0 | 0
3996 | 1073.9732 | 645.45 | 2815.8205 | 1115.6483 | 0 | 0 | 1700.1723 | 0 | 0 | 0
3997 | 1076.9171 | 381.48 | 1679.4159 | 1118.7065 | 0 | 0 | 560.7094 | 0 | 0 | 0
3998 | 1076.9383 | 65.42 | 258.5959 | 258.5959 | 0 | 0 | 0 | 828.003 | 0 | 0
3999 | 1164.3879 | 46.13 | 174.0019 | 174.0019 | 0 | 0 | 0 | 996.886 | 0 | 0
4000 | 1132.1777 | 29.41 | 101.538 | 101.538 | 0 | 0 | 0 | 1034.433 | 0 | 0
4001 | 1128.9285 | 107.28 | 463.9593 | 463.9593 | 0 | 0 | 0 | 682.301 | 0 | 0
4002 | 1028.4225 | 51.69 | 201.472 | 201.472 | 0 | 0 | 0 | 834.476 | 0 | 0
4003 | 1248.913 | 0 | 0 | 0 | 0 | 0 | 0 | 1248.913 | 0 | 0
4004 | 980.4482 | 0 | 0 | 0 | 0 | 0 | 0 | 980.448 | 0 | 0
4005 | 989.2744 | 0 | 0 | 0 | 0 | 0 | 0 | 989.274 | 0 | 0
4006 | 925.2842 | 0 | 0 | 0 | 0 | 0 | 0 | 619.411 | 0 | 317.7434
4007 | 992.2165 | 0 | 0 | 0 | 0 | 0 | 0 | 400.216 | 0 | 614.9724
4008 | 1404.8432 | 0 | 0 | 0 | 0 | 0 | 0 | 1404.843 | 0 | 0
4009 | 1122.4035 | 0 | 0 | 0 | 0 | 0 | 0 | 1122.404 | 0 | 0
4010 | 848.7901 | 0 | 0 | 0 | 0 | 0 | 0 | 848.79 | 0 | 0
4011 | 1120.197 | 0 | 0 | 0 | 0 | 0 | 0 | 1120.197 | 0 | 0
4012 | 1104.0155 | 0 | 0 | 0 | 0 | 0 | 0 | 1104.016 | 0 | 0
4013 | 823.7824 | 0 | 0 | 0 | 0 | 0 | 0 | 823.782 | 0 | 0
4014 | 1180.5096 | 0 | 0 | 0 | 0 | 0 | 0 | 1180.51 | 0 | 0
4015 | 1004.4362 | 44.11 | 171.1929 | 171.1929 | 0 | 0 | 0 | 839.639 | 0 | 0
4016 | 1200.8854 | 123.2 | 537.3342 | 537.3342 | 0 | 0 | 0 | 683.623 | 0 | 0
4017 | 1296.0874 | 298.65 | 1339.012 | 1339.012 | 0 | 0 | 0 | 7.094 | 0 | 0
4018 | 905.5732 | 418.47 | 1861.9225 | 940.7135 | -614.9724 | 0 | 306.2365 | 0 | 0 | 0
4019 | 1261.7184 | 642.86 | 2824.7335 | 1310.6797 | -423.0387 | 0 | 1091.0151 | 0 | 0 | 0
4020 | 1336.4693 | 725.12 | 3157.7981 | 1388.3303 | 0 | 0 | 1769.4678 | 0 | 0 | 0
4021 | 1087.4829 | 704.67 | 3064.9841 | 1129.6825 | 0 | 0 | 1935.3016 | 0 | 0 | 0
4022 | 1175.372 | 464.56 | 2043.3404 | 1220.982 | 0 | 0 | 822.3584 | 0 | 0 | 0
4023 | 1147.4094 | 143.9 | 618.3142 | 618.3142 | 0 | 0 | 0 | 552.192 | 0 | 0
4024 | 998.7939 | 82.3 | 342.2072 | 342.2072 | 0 | 0 | 0 | 669.369 | 0 | 0
4025 | 1349.1184 | 67.1 | 275.758 | 275.758 | 0 | 0 | 0 | 1083.661 | 0 | 0
4026 | 1296.8027 | 21.55 | 66.8928 | 66.8928 | 0 | 0 | 0 | 1232.408 | 0 | 0
4027 | 1050.3226 | 0 | 0 | 0 | 0 | 0 | 0 | 1050.323 | 0 | 0
4028 | 905.4251 | 0 | 0 | 0 | 0 | 0 | 0 | 905.425 | 0 | 0
4029 | 1113.5773 | 0 | 0 | 0 | 0 | 0 | 0 | 1113.577 | 0 | 0
4030 | 1034.8766 | 0 | 0 | 0 | 0 | 0 | 0 | 729.003 | 0 | 317.7434
4031 | 1276.8627 | 0 | 0 | 0 | 0 | 0 | 0 | 684.863 | 0 | 614.9724
4032 | 906.1606 | 0 | 0 | 0 | 0 | 0 | 0 | 906.161 | 0 | 0
4033 | 1189.3358 | 0 | 0 | 0 | 0 | 0 | 0 | 1189.336 | 0 | 0
4034 | 1040.0253 | 0 | 0 | 0 | 0 | 0 | 0 | 1040.025 | 0 | 0
4035 | 1162.8571 | 0 | 0 | 0 | 0 | 0 | 0 | 1162.857 | 0 | 0
4036 | 711.9834 | 0 | 0 | 0 | 0 | 0 | 0 | 711.983 | 0 | 0
4037 | 1019.4307 | 0 | 0 | 0 | 0 | 0 | 0 | 1019.431 | 0 | 0
4038 | 675.2074 | 0 | 0 | 0 | 0 | 0 | 0 | 675.207 | 0 | 0
4039 | 747.1449 | 63.21 | 257.4657 | 257.4657 | 0 | 0 | 0 | 499.297 | 0 | 0
4040 | 1067.6514 | 179.14 | 799.0465 | 799.0465 | 0 | 0 | 0 | 298.453 | 0 | 0
4041 | 1143.193 | 397.11 | 1788.7127 | 1187.5543 | -601.1584 | 0 | 0 | 0 | 0 | 0
4042 | 1219.8369 | 465.15 | 2067.1498 | 1267.1725 | -436.8527 | 0 | 363.1246 | 0 | 0 | 0
4043 | 1490.4715 | 506.41 | 2231.3349 | 1548.3094 | 0 | 0 | 683.0255 | 0 | 0 | 0
4044 | 1150.4507 | 612.18 | 2681.4189 | 1195.0929 | 0 | 0 | 1486.326 | 0 | 0 | 0
4045 | 1240.471 | 677.58 | 2959.59 | 1288.6072 | 0 | 0 | 1670.9829 | 0 | 0 | 0
4046 | 1223.9724 | 674.03 | 2958.6385 | 1271.469 | 0 | 0 | 1687.1695 | 0 | 0 | 0
4047 | 1179.3466 | 459.1 | 2038.2481 | 1225.1102 | 0 | 0 | 813.1379 | 0 | 0 | 0
4048 | 1321.3359 | 426.35 | 1920.1994 | 1372.6101 | 0 | 0 | 547.5893 | 0 | 0 | 0
4049 | 1489.5089 | 74.66 | 308.5634 | 308.5634 | 0 | 0 | 0 | 1192.472 | 0 | 0
4050 | 1368.6657 | 18.61 | 53.6636 | 53.6636 | 0 | 0 | 0 | 1317.007 | 0 | 0
4051 | 1199.6331 | 0 | 0 | 0 | 0 | 0 | 0 | 1199.633 | 0 | 0
4052 | 1119.4615 | 0 | 0 | 0 | 0 | 0 | 0 | 1119.461 | 0 | 0
4053 | 1075.3302 | 0 | 0 | 0 | 0 | 0 | 0 | 1075.33 | 0 | 0
4054 | 1176.832 | 0 | 0 | 0 | 0 | 0 | 0 | 870.958 | 0 | 317.7434
4055 | 1138.585 | 0 | 0 | 0 | 0 | 0 | 0 | 546.585 | 0 | 614.9724
4056 | 1338.6464 | 0 | 0 | 0 | 0 | 0 | 0 | 1338.646 | 0 | 0
4057 | 1243.0288 | 0 | 0 | 0 | 0 | 0 | 0 | 1243.029 | 0 | 0
4058 | 1127.5522 | 0 | 0 | 0 | 0 | 0 | 0 | 1127.552 | 0 | 0
4059 | 1088.5696 | 0 | 0 | 0 | 0 | 0 | 0 | 1088.57 | 0 | 0
4060 | 1187.8648 | 0 | 0 | 0 | 0 | 0 | 0 | 1187.865 | 0 | 0
4061 | 1379.1 | 0 | 0 | 0 | 0 | 0 | 0 | 1379.1 | 0 | 0
4062 | 1313.6387 | 0 | 0 | 0 | 0 | 0 | 0 | 1313.639 | 0 | 0
4063 | 1192.7735 | 95.03 | 391.0155 | 391.0155 | 0 | 0 | 0 | 816.364 | 0 | 0
4064 | 1204.4444 | 294.23 | 1325.3746 | 1251.1821 | -74.1925 | 0 | 0 | 0 | 0 | 0
4065 | 914.0068 | 327.48 | 1466.9679 | 949.4748 | -517.4931 | 0 | 0 | 0 | 0 | 0
4066 | 1054.7081 | 707.1 | 3173.8072 | 1095.6357 | -446.3256 | 0 | 1631.8459 | 0 | 0 | 0
4067 | 1164.4744 | 684.59 | 3007.7127 | 1209.6611 | 0 | 0 | 1798.0516 | 0 | 0 | 0
4068 | 1401.6253 | 751.21 | 3279.4079 | 1456.0157 | 0 | 0 | 1823.3922 | 0 | 0 | 0
4069 | 1428.7283 | 738.84 | 3231.6582 | 1484.1705 | 0 | 0 | 1747.4877 | 0 | 0 | 0
4070 | 1276.9675 | 690.89 | 3038.8384 | 1326.5204 | 0 | 0 | 1712.318 | 0 | 0 | 0
4071 | 1519.5135 | 600.39 | 2671.5492 | 1578.4784 | 0 | 0 | 1093.0709 | 0 | 0 | 0
4072 | 1443.7099 | 497.67 | 2282.6093 | 1499.7328 | 0 | 0 | 782.8765 | 0 | 0 | 0
4073 | 1342.0133 | 248.99 | 1111.2759 | 1111.2759 | 0 | 0 | 0 | 272.249 | 0 | 0
4074 | 1332.7466 | 67.7 | 264.4797 | 264.4797 | 0 | 0 | 0 | 1078.146 | 0 | 0
4075 | 1262.1523 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.152 | 0 | 0
4076 | 1451.9165 | 0 | 0 | 0 | 0 | 0 | 0 | 1451.916 | 0 | 0
4077 | 1443.0903 | 0 | 0 | 0 | 0 | 0 | 0 | 1443.09 | 0 | 0
4078 | 1423.9667 | 0 | 0 | 0 | 0 | 0 | 0 | 1118.093 | 0 | 317.7434
4079 | 1318.0519 | 0 | 0 | 0 | 0 | 0 | 0 | 726.052 | 0 | 614.9724
4080 | 1204.7818 | 0 | 0 | 0 | 0 | 0 | 0 | 1204.782 | 0 | 0
4081 | 1000.3072 | 0 | 0 | 0 | 0 | 0 | 0 | 1000.307 | 0 | 0
4082 | 1279.8048 | 0 | 0 | 0 | 0 | 0 | 0 | 1279.805 | 0 | 0
4083 | 1320.9939 | 0 | 0 | 0 | 0 | 0 | 0 | 1320.994 | 0 | 0
4084 | 1414.405 | 0 | 0 | 0 | 0 | 0 | 0 | 1414.405 | 0 | 0
4085 | 1349.6792 | 0 | 0 | 0 | 0 | 0 | 0 | 1349.679 | 0 | 0
4086 | 1217.2856 | 0 | 0 | 0 | 0 | 0 | 0 | 1217.286 | 0 | 0
4087 | 842.1704 | 74.49 | 306.2511 | 306.2511 | 0 | 0 | 0 | 547.36 | 0 | 0
4088 | 1414.8031 | 208.21 | 934.0153 | 934.0153 | 0 | 0 | 0 | 515.678 | 0 | 0
4089 | 1229.2948 | 538.32 | 2472.1112 | 1276.9975 | -614.9724 | 0 | 580.1413 | 0 | 0 | 0
4090 | 1233.0561 | 716.79 | 3234.7923 | 1280.9044 | -423.0387 | 0 | 1530.8492 | 0 | 0 | 0
4091 | 1290.0993 | 646.22 | 2850.2351 | 1340.162 | 0 | 0 | 1510.0731 | 0 | 0 | 0
4092 | 1374.5232 | 332.65 | 1464.0696 | 1427.861 | 0 | 0 | 36.2086 | 0 | 0 | 0
4093 | 1301.6783 | 711.06 | 3121.1491 | 1352.1893 | 0 | 0 | 1768.9598 | 0 | 0 | 0
4094 | 1473.8341 | 144.25 | 615.0919 | 615.0919 | 0 | 0 | 0 | 878.594 | 0 | 3.2463
4095 | 1200.2556 | 282.11 | 1250.4446 | 1246.8316 | -3.613 | 0 | 0 | 0 | 0 | 0
4096 | 1652.6215 | 44.13 | 166.4612 | 166.4612 | 0 | 0 | 0 | 1492.378 | 0 | 0
4097 | 1554.1529 | 35.28 | 129.5161 | 129.5161 | 0 | 0 | 0 | 1429.474 | 0 | 0
4098 | 1601.1342 | 13.71 | 32.6455 | 32.6455 | 0 | 0 | 0 | 1569.708 | 0 | 0
4099 | 1579.897 | 0 | 0 | 0 | 0 | 0 | 0 | 1579.897 | 0 | 0
4100 | 1123.8746 | 0 | 0 | 0 | 0 | 0 | 0 | 1123.875 | 0 | 0
4101 | 1184.1872 | 0 | 0 | 0 | 0 | 0 | 0 | 1184.187 | 0 | 0
4102 | 1214.3435 | 0 | 0 | 0 | 0 | 0 | 0 | 908.47 | 0 | 317.7434
4103 | 1265.0944 | 0 | 0 | 0 | 0 | 0 | 0 | 673.094 | 0 | 614.9724
4104 | 1221.6987 | 0 | 0 | 0 | 0 | 0 | 0 | 1221.699 | 0 | 0
4105 | 1285.689 | 0 | 0 | 0 | 0 | 0 | 0 | 1285.689 | 0 | 0
4106 | 1382.7776 | 0 | 0 | 0 | 0 | 0 | 0 | 1382.778 | 0 | 0
4107 | 1180.5096 | 0 | 0 | 0 | 0 | 0 | 0 | 1180.51 | 0 | 0
4108 | 1251.1195 | 0 | 0 | 0 | 0 | 0 | 0 | 1251.12 | 0 | 0
4109 | 1314.3743 | 0 | 0 | 0 | 0 | 0 | 0 | 1314.374 | 0 | 0
4110 | 1123.8746 | 0 | 0 | 0 | 0 | 0 | 0 | 1123.875 | 0 | 0
4111 | 1094.6009 | 113.88 | 401.3059 | 401.3059 | 0 | 0 | 0 | 708.285 | 0 | 0
4112 | 1132.8406 | 228.03 | 1026.8595 | 1026.8595 | 0 | 0 | 0 | 144.339 | 0 | 0
4113 | 1145.5301 | 290.25 | 1301.5891 | 1189.983 | -111.6061 | 0 | 0 | 0 | 0 | 0
4114 | 1243.3736 | 553.1 | 2464.4116 | 1291.6228 | -614.9724 | 0 | 557.8163 | 0 | 0 | 0
4115 | 952.8174 | 651.45 | 2870.283 | 989.7908 | -311.4326 | 0 | 1569.0595 | 0 | 0 | 0
4116 | 1336.7828 | 584.5 | 2568.7398 | 1388.6565 | 0 | 0 | 1180.0832 | 0 | 0 | 0
4117 | 1269.4781 | 655.05 | 2871.5254 | 1318.7408 | 0 | 0 | 1552.7846 | 0 | 0 | 0
4118 | 1515.3156 | 645.25 | 2841.3107 | 1574.1175 | 0 | 0 | 1267.1932 | 0 | 0 | 0
4119 | 1178.0217 | 547.26 | 2433.9299 | 1223.7338 | 0 | 0 | 1210.1961 | 0 | 0 | 0
4120 | 1291.1281 | 189.27 | 834.7554 | 834.7554 | 0 | 0 | 0 | 487.555 | 0 | 0
4121 | 1202.7821 | 212.95 | 950.953 | 950.953 | 0 | 0 | 0 | 287.352 | 0 | 0
4122 | 1153.1952 | 34.3 | 123.5554 | 123.5554 | 0 | 0 | 0 | 1034.255 | 0 | 0
4123 | 1228.3184 | 0 | 0 | 0 | 0 | 0 | 0 | 1228.318 | 0 | 0
4124 | 785.5354 | 0 | 0 | 0 | 0 | 0 | 0 | 785.535 | 0 | 0
4125 | 1207.7239 | 0 | 0 | 0 | 0 | 0 | 0 | 1207.724 | 0 | 0
4126 | 1132.7008 | 0 | 0 | 0 | 0 | 0 | 0 | 826.827 | 0 | 317.7434
4127 | 1078.2723 | 0 | 0 | 0 | 0 | 0 | 0 | 486.272 | 0 | 614.9724
4128 | 1233.4671 | 0 | 0 | 0 | 0 | 0 | 0 | 1233.467 | 0 | 0
4129 | 1003.9848 | 0 | 0 | 0 | 0 | 0 | 0 | 1003.985 | 0 | 0
4130 | 1147.4112 | 0 | 0 | 0 | 0 | 0 | 0 | 1147.411 | 0 | 0
4131 | 1050.3226 | 0 | 0 | 0 | 0 | 0 | 0 | 1050.323 | 0 | 0
4132 | 1001.0427 | 0 | 0 | 0 | 0 | 0 | 0 | 1001.043 | 0 | 0
4133 | 899.541 | 0 | 0 | 0 | 0 | 0 | 0 | 899.541 | 0 | 0
4134 | 956.9115 | 0 | 0 | 0 | 0 | 0 | 0 | 956.912 | 0 | 0
4135 | 789.213 | 47.02 | 184.5873 | 184.5873 | 0 | 0 | 0 | 611.521 | 0 | 0
4136 | 1053.7961 | 132.98 | 584.149 | 584.149 | 0 | 0 | 0 | 491.468 | 0 | 0
4137 | 1095.8283 | 336.35 | 1514.623 | 1138.3524 | -376.2707 | 0 | 0 | 0 | 0 | 0
4138 | 1072.8488 | 453.14 | 2017.6206 | 1114.4806 | -614.9724 | 0 | 288.1676 | 0 | 0 | 0
4139 | 1035.489 | 461.37 | 2035.8236 | 1075.6709 | -46.768 | 0 | 913.3847 | 0 | 0 | 0
4140 | 1331.4199 | 129.49 | 543.8517 | 543.8517 | 0 | 0 | 0 | 807.884 | 0 | 0
4141 | 846.3463 | 142.01 | 600.3481 | 600.3481 | 0 | 0 | 0 | 25.206 | 0 | 252.6571
4142 | 916.9976 | 281.56 | 1233.7614 | 952.5819 | -281.1795 | 0 | 0 | 0 | 0 | 0
4143 | 791.3395 | 50.06 | 189.7387 | 189.7387 | 0 | 0 | 0 | 550.282 | 0 | 60.6724
4144 | 216.0103 | 29.42 | 100.5438 | 100.5438 | 0 | 0 | 0 | 0 | 0 | 123.8484
4145 | 168.3081 | 40.18 | 151.759 | 151.759 | 0 | 0 | 0 | 0 | 0 | 23.0802
4146 | 126.4653 | 9.79 | 15.9799 | 15.9799 | 0 | 0 | 0 | 0 | 0 | 115.3935
4147 | 136.0712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141.3512
4148 | 92.6755 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.2723
4149 | 88.2624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.687
4150 | 94.1466 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.8004
4151 | 83.8493 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.1027
4152 | 91.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.5077
4153 | 82.3782 | 0 | 0 | 0 | 0 | 0 | 0 | 82.378 | 0 | 0
4154 | 88.2624 | 0 | 0 | 0 | 0 | 0 | 0 | 88.262 | 0 | 0
4155 | 82.3782 | 0 | 0 | 0 | 0 | 0 | 0 | 82.378 | 0 | 0
4156 | 82.3782 | 0 | 0 | 0 | 0 | 0 | 0 | 82.378 | 0 | 0
4157 | 83.8493 | 0 | 0 | 0 | 0 | 0 | 0 | 83.849 | 0 | 0
4158 | 84.5848 | 0 | 0 | 0 | 0 | 0 | 0 | 84.585 | 0 | 0
4159 | 66.9323 | 34.3 | 126.1275 | 69.5293 | -56.5982 | 0 | 0 | 0 | 0 | 0
4160 | 82.3874 | 152.88 | 675.7986 | 85.584 | -590.2146 | 0 | 0 | 0 | 0 | 0
4161 | 584.9195 | 304.43 | 1363.1061 | 607.6177 | -391.1983 | 0 | 364.2901 | 0 | 0 | 0
4162 | 1157.201 | 359.65 | 1596.7977 | 1202.1059 | 0 | 0 | 394.6918 | 0 | 0 | 0
4163 | 1150.5013 | 533.13 | 2350.9211 | 1195.1459 | 0 | 0 | 1155.7752 | 0 | 0 | 0
4164 | 990.4614 | 653.68 | 2859.2945 | 1028.8956 | 0 | 0 | 1830.3989 | 0 | 0 | 0
4165 | 1247.0319 | 765.86 | 3337.2943 | 1295.4228 | 0 | 0 | 2041.8715 | 0 | 0 | 0
4166 | 1015.0755 | 814.55 | 3611.5024 | 1054.4658 | 0 | 0 | 2557.0366 | 0 | 0 | 0
4167 | 1035.2371 | 558.23 | 2480.3853 | 1075.4091 | 0 | 0 | 1404.9762 | 0 | 0 | 0
4168 | 965.4739 | 406.47 | 1832.0392 | 1002.939 | 0 | 0 | 829.1002 | 0 | 0 | 0
4169 | 874.7245 | 183.01 | 813.9378 | 813.9378 | 0 | 0 | 0 | 91.191 | 0 | 0
4170 | 1044.9992 | 46.73 | 179.6789 | 179.6789 | 0 | 0 | 0 | 872.032 | 0 | 0
4171 | 962.7957 | 0 | 0 | 0 | 0 | 0 | 0 | 962.796 | 0 | 0
4172 | 1037.8187 | 0 | 0 | 0 | 0 | 0 | 0 | 1037.819 | 0 | 0
4173 | 715.661 | 0 | 0 | 0 | 0 | 0 | 0 | 715.661 | 0 | 0
4174 | 1001.7782 | 0 | 0 | 0 | 0 | 0 | 0 | 695.905 | 0 | 317.7434
4175 | 876.0043 | 0 | 0 | 0 | 0 | 0 | 0 | 284.004 | 0 | 614.9724
4176 | 918.6645 | 0 | 0 | 0 | 0 | 0 | 0 | 918.664 | 0 | 0
4177 | 882.624 | 0 | 0 | 0 | 0 | 0 | 0 | 882.624 | 0 | 0
4178 | 1200.3686 | 0 | 0 | 0 | 0 | 0 | 0 | 1200.369 | 0 | 0
4179 | 1074.5947 | 0 | 0 | 0 | 0 | 0 | 0 | 1074.595 | 0 | 0
4180 | 1248.913 | 0 | 0 | 0 | 0 | 0 | 0 | 1248.913 | 0 | 0
4181 | 1179.0386 | 0 | 0 | 0 | 0 | 0 | 0 | 1179.039 | 0 | 0
4182 | 1068.7106 | 0 | 0 | 0 | 0 | 0 | 0 | 1068.711 | 0 | 0
4183 | 955.4405 | 78.36 | 322.8034 | 322.8034 | 0 | 0 | 0 | 644.695 | 0 | 0
4184 | 993.9174 | 221.3 | 991.6243 | 991.6243 | 0 | 0 | 0 | 39.336 | 0 | 0
4185 | 746.5353 | 276.12 | 1226.4274 | 775.5041 | -450.9233 | 0 | 0 | 0 | 0 | 0
4186 | 1054.2475 | 80.22 | 324.1756 | 324.1756 | 0 | 0 | 0 | 352.135 | 0 | 405.1816
4187 | 1269.1333 | 448.84 | 1952.3182 | 1318.3824 | -614.9724 | 0 | 18.9634 | 0 | 0 | 0
4188 | 1079.2074 | 454.76 | 1967.9605 | 1121.0864 | -423.0387 | 0 | 423.8355 | 0 | 0 | 0
4189 | 1049.5751 | 293.41 | 1266.6905 | 1090.3035 | 0 | 0 | 176.387 | 0 | 0 | 0
4190 | 1119.0192 | 210.2 | 901.507 | 901.507 | 0 | 0 | 0 | 251.189 | 0 | 0
4191 | 1490.9597 | 211.52 | 913.4293 | 913.4293 | 0 | 0 | 0 | 213.156 | 0 | 413.9595
4192 | 567.8021 | 239.37 | 1050.5277 | 589.8354 | -460.6922 | 0 | 0 | 0 | 0 | 0
4193 | 1329.9719 | 244.93 | 1080.3995 | 1080.3995 | 0 | 0 | 0 | 289.931 | 0 | 0
4194 | 1208.3058 | 67.16 | 262.5995 | 262.5995 | 0 | 0 | 0 | 955.516 | 0 | 0
4195 | 1031.9346 | 0 | 0 | 0 | 0 | 0 | 0 | 1031.935 | 0 | 0
4196 | 898.0699 | 0 | 0 | 0 | 0 | 0 | 0 | 898.07 | 0 | 0
4197 | 1109.1642 | 0 | 0 | 0 | 0 | 0 | 0 | 1109.164 | 0 | 0
4198 | 1198.8976 | 0 | 0 | 0 | 0 | 0 | 0 | 893.024 | 0 | 317.7434
4199 | 1042.9674 | 0 | 0 | 0 | 0 | 0 | 0 | 450.967 | 0 | 614.9724
4200 | 873.0622 | 0 | 0 | 0 | 0 | 0 | 0 | 873.062 | 0 | 0
4201 | 1123.8746 | 0 | 0 | 0 | 0 | 0 | 0 | 1123.875 | 0 | 0
4202 | 782.5933 | 0 | 0 | 0 | 0 | 0 | 0 | 782.593 | 0 | 0
4203 | 1155.5019 | 0 | 0 | 0 | 0 | 0 | 0 | 1155.502 | 0 | 0
4204 | 1004.7203 | 0 | 0 | 0 | 0 | 0 | 0 | 1004.72 | 0 | 0
4205 | 945.8787 | 0 | 0 | 0 | 0 | 0 | 0 | 945.879 | 0 | 0
4206 | 1001.0427 | 0 | 0 | 0 | 0 | 0 | 0 | 1001.043 | 0 | 0
4207 | 1244.4999 | 106.82 | 374.2377 | 374.2377 | 0 | 0 | 0 | 884.242 | 0 | 0
4208 | 641.0608 | 235.99 | 1054.0523 | 665.9372 | -388.1151 | 0 | 0 | 0 | 0 | 0
4209 | 822.6911 | 527.05 | 2373.324 | 854.6153 | -614.9724 | 0 | 903.7362 | 0 | 0 | 0
4210 | 1162.7946 | 707.42 | 3110.5803 | 1207.9159 | -34.9236 | 0 | 1867.7408 | 0 | 0 | 0
4211 | 1141.8157 | 655.65 | 2820.3923 | 1186.1239 | 0 | 0 | 1634.2684 | 0 | 0 | 0
4212 | 1203.114 | 681.89 | 2914.5849 | 1249.8005 | 0 | 0 | 1664.7843 | 0 | 0 | 0
4213 | 999.0366 | 666.38 | 2847.9809 | 1037.8033 | 0 | 0 | 1810.1775 | 0 | 0 | 0
4214 | 1206.6721 | 620.59 | 2671.6677 | 1253.4966 | 0 | 0 | 1418.171 | 0 | 0 | 0
4215 | 1353.2033 | 483.38 | 2106.1174 | 1405.7137 | 0 | 0 | 700.4037 | 0 | 0 | 0
4216 | 1525.3618 | 486.75 | 2153.8079 | 1584.5533 | 0 | 0 | 569.2546 | 0 | 0 | 0
4217 | 1270.7349 | 179.62 | 787.5501 | 787.5501 | 0 | 0 | 0 | 512.604 | 0 | 0
4218 | 1248.3052 | 63.34 | 247.6666 | 247.6666 | 0 | 0 | 0 | 1009.89 | 0 | 0
4219 | 1187.8648 | 0 | 0 | 0 | 0 | 0 | 0 | 1187.865 | 0 | 0
4220 | 1119.4615 | 0 | 0 | 0 | 0 | 0 | 0 | 1119.461 | 0 | 0
4221 | 1184.1872 | 0 | 0 | 0 | 0 | 0 | 0 | 1184.187 | 0 | 0
4222 | 1246.7064 | 0 | 0 | 0 | 0 | 0 | 0 | 940.833 | 0 | 317.7434
4223 | 890.7147 | 0 | 0 | 0 | 0 | 0 | 0 | 298.715 | 0 | 614.9724
4224 | 1162.1216 | 0 | 0 | 0 | 0 | 0 | 0 | 1162.122 | 0 | 0
4225 | 1210.6659 | 0 | 0 | 0 | 0 | 0 | 0 | 1210.666 | 0 | 0
4226 | 1075.3302 | 0 | 0 | 0 | 0 | 0 | 0 | 1075.33 | 0 | 0
4227 | 1067.2395 | 0 | 0 | 0 | 0 | 0 | 0 | 1067.24 | 0 | 0
4228 | 1099.6024 | 0 | 0 | 0 | 0 | 0 | 0 | 1099.602 | 0 | 0
4229 | 772.296 | 0 | 0 | 0 | 0 | 0 | 0 | 772.296 | 0 | 0
4230 | 1059.8843 | 0 | 0 | 0 | 0 | 0 | 0 | 1059.884 | 0 | 0
4231 | 649.4642 | 100.95 | 408.1069 | 408.1069 | 0 | 0 | 0 | 256.602 | 0 | 0
4232 | 882.1064 | 311.87 | 1382.0664 | 916.3359 | -465.7304 | 0 | 0 | 0 | 0 | 0
4233 | 827.5326 | 523.57 | 2377.9487 | 859.6452 | -572.2817 | 0 | 946.0218 | 0 | 0 | 0
4234 | 1054.0186 | 704.64 | 3122.4497 | 1094.9189 | 0 | 0 | 2027.5308 | 0 | 0 | 0
4235 | 1307.932 | 833.54 | 3615.9973 | 1358.686 | 0 | 0 | 2257.3113 | 0 | 0 | 0
4236 | 1422.7357 | 897.42 | 3837.3936 | 1477.9449 | 0 | 0 | 2359.4487 | 0 | 0 | 0
4237 | 1374.2539 | 892.27 | 3794.3746 | 1427.5805 | 0 | 0 | 2366.794 | 0 | 0 | 0
4238 | 1156.3257 | 809.96 | 3471.2575 | 1201.1959 | 0 | 0 | 2270.0616 | 0 | 0 | 0
4239 | 1129.0885 | 672.44 | 2928.3584 | 1172.902 | 0 | 0 | 1755.4564 | 0 | 0 | 0
4240 | 1626.5602 | 487.8 | 2179.9006 | 1689.6783 | 0 | 0 | 490.2223 | 0 | 0 | 0
4241 | 1795.9293 | 268.1 | 1181.3277 | 1181.3277 | 0 | 0 | 0 | 658.731 | 0 | 0
4242 | 1420.2091 | 46.76 | 178.4199 | 178.4199 | 0 | 0 | 0 | 1248.455 | 0 | 0
4243 | 1461.4783 | 0 | 0 | 0 | 0 | 0 | 0 | 1461.478 | 0 | 0
4244 | 1213.608 | 0 | 0 | 0 | 0 | 0 | 0 | 1213.608 | 0 | 0
4245 | 1603.4336 | 0 | 0 | 0 | 0 | 0 | 0 | 1603.434 | 0 | 0
4246 | 1394.5459 | 0 | 0 | 0 | 0 | 0 | 0 | 1088.672 | 0 | 317.7434
4247 | 1470.3045 | 0 | 0 | 0 | 0 | 0 | 0 | 878.304 | 0 | 614.9724
4248 | 1418.0826 | 0 | 0 | 0 | 0 | 0 | 0 | 1418.083 | 0 | 0
4249 | 1318.7874 | 0 | 0 | 0 | 0 | 0 | 0 | 1318.787 | 0 | 0
4250 | 1217.2856 | 0 | 0 | 0 | 0 | 0 | 0 | 1217.286 | 0 | 0
4251 | 1218.7567 | 0 | 0 | 0 | 0 | 0 | 0 | 1218.757 | 0 | 0
4252 | 1394.5459 | 0 | 0 | 0 | 0 | 0 | 0 | 1394.546 | 0 | 0
4253 | 1187.1293 | 0 | 0 | 0 | 0 | 0 | 0 | 1187.129 | 0 | 0
4254 | 1418.0826 | 0 | 0 | 0 | 0 | 0 | 0 | 1418.083 | 0 | 0
4255 | 920.1355 | 106.25 | 423.1997 | 423.1997 | 0 | 0 | 0 | 512.744 | 0 | 0
4256 | 761.6585 | 313.95 | 1389.1458 | 791.215 | -597.9308 | 0 | 0 | 0 | 0 | 0
4257 | 976.5554 | 527.78 | 2391.6807 | 1014.451 | -440.0803 | 0 | 937.1494 | 0 | 0 | 0
4258 | 1245.0055 | 708.65 | 3131.0905 | 1293.3181 | 0 | 0 | 1837.7723 | 0 | 0 | 0
4259 | 1420.1043 | 835.6 | 3619.2082 | 1475.2108 | 0 | 0 | 2143.9974 | 0 | 0 | 0
4260 | 1490.1332 | 900.98 | 3872.5228 | 1547.9572 | 0 | 0 | 2324.5656 | 0 | 0 | 0
4261 | 860.9694 | 895.98 | 3855.9165 | 894.3797 | 0 | 0 | 2961.5368 | 0 | 0 | 0
4262 | 1268.3941 | 816.9 | 3555.5264 | 1317.6137 | 0 | 0 | 2237.9127 | 0 | 0 | 0
4263 | 1179.3631 | 680.79 | 3017.7964 | 1225.1289 | 0 | 0 | 1792.6674 | 0 | 0 | 0
4264 | 1177.8001 | 494.37 | 2235.273 | 1223.5042 | 0 | 0 | 1011.7688 | 0 | 0 | 0
4265 | 933.8677 | 272.08 | 1204.1492 | 970.1055 | 0 | 0 | 234.0437 | 0 | 0 | 0
4266 | 1077.5727 | 29.39 | 101.1474 | 101.1474 | 0 | 0 | 0 | 980.204 | 0 | 0
4267 | 1109.8997 | 0 | 0 | 0 | 0 | 0 | 0 | 1109.9 | 0 | 0
4268 | 1127.5522 | 0 | 0 | 0 | 0 | 0 | 0 | 1127.552 | 0 | 0
4269 | 1183.4517 | 0 | 0 | 0 | 0 | 0 | 0 | 1183.452 | 0 | 0
4270 | 1332.0267 | 0 | 0 | 0 | 0 | 0 | 0 | 1026.153 | 0 | 317.7434
4271 | 1148.1467 | 0 | 0 | 0 | 0 | 0 | 0 | 556.147 | 0 | 614.9724
4272 | 1170.2123 | 0 | 0 | 0 | 0 | 0 | 0 | 1170.212 | 0 | 0
4273 | 1298.1928 | 0 | 0 | 0 | 0 | 0 | 0 | 1298.193 | 0 | 0
4274 | 1256.2682 | 0 | 0 | 0 | 0 | 0 | 0 | 1256.268 | 0 | 0
4275 | 1237.1447 | 0 | 0 | 0 | 0 | 0 | 0 | 1237.145 | 0 | 0
4276 | 1329.0847 | 0 | 0 | 0 | 0 | 0 | 0 | 1329.085 | 0 | 0
4277 | 1320.2584 | 0 | 0 | 0 | 0 | 0 | 0 | 1320.258 | 0 | 0
4278 | 1256.2682 | 0 | 0 | 0 | 0 | 0 | 0 | 1256.268 | 0 | 0
4279 | 957.647 | 106.65 | 375.5622 | 375.5622 | 0 | 0 | 0 | 596.114 | 0 | 0
4280 | 1212.8063 | 314.24 | 1389.0035 | 1259.8686 | -129.1349 | 0 | 0 | 0 | 0 | 0
4281 | 817.3512 | 528.81 | 2397.1635 | 849.0691 | -614.9724 | 0 | 933.1219 | 0 | 0 | 0
4282 | 1350.9121 | 709.68 | 3136.7146 | 1403.3338 | -293.9049 | 0 | 1439.4759 | 0 | 0 | 0
4283 | 1576.5504 | 848.41 | 3669.9621 | 1637.7276 | 0 | 0 | 2032.2345 | 0 | 0 | 0
4284 | 1514.752 | 912.78 | 3906.392 | 1573.5316 | 0 | 0 | 2332.8604 | 0 | 0 | 0
4285 | 1347.5913 | 777.03 | 3300.3606 | 1399.8839 | 0 | 0 | 1900.4767 | 0 | 0 | 0
4286 | 1384.7626 | 777.64 | 3295.6299 | 1438.4984 | 0 | 0 | 1857.1315 | 0 | 0 | 0
4287 | 1490.5497 | 602.48 | 2623.2905 | 1548.3894 | 0 | 0 | 1074.9011 | 0 | 0 | 0
4288 | 1528.8197 | 325.07 | 1436.4519 | 1436.4519 | 0 | 0 | 0 | 146.027 | 0 | 0
4289 | 1453.0225 | 47.74 | 183.588 | 183.588 | 0 | 0 | 0 | 1276.292 | 0 | 0
4290 | 1062.5736 | 5.87 | 0 | 0 | 0 | 0 | 0 | 1062.574 | 0 | 0
4291 | 1421.0247 | 0 | 0 | 0 | 0 | 0 | 0 | 1421.025 | 0 | 0
4292 | 1195.22 | 0 | 0 | 0 | 0 | 0 | 0 | 1195.22 | 0 | 0
4293 | 1395.2815 | 0 | 0 | 0 | 0 | 0 | 0 | 1395.281 | 0 | 0
4294 | 1417.3471 | 0 | 0 | 0 | 0 | 0 | 0 | 1111.473 | 0 | 317.7434
4295 | 1162.8571 | 0 | 0 | 0 | 0 | 0 | 0 | 570.857 | 0 | 614.9724
4296 | 1393.0749 | 0 | 0 | 0 | 0 | 0 | 0 | 1393.075 | 0 | 0
4297 | 1050.3226 | 0 | 0 | 0 | 0 | 0 | 0 | 1050.323 | 0 | 0
4298 | 1021.6373 | 0 | 0 | 0 | 0 | 0 | 0 | 1021.637 | 0 | 0
4299 | 1457.0651 | 0 | 0 | 0 | 0 | 0 | 0 | 1457.065 | 0 | 0
4300 | 1272.4496 | 0 | 0 | 0 | 0 | 0 | 0 | 1272.45 | 0 | 0
4301 | 1186.3938 | 0 | 0 | 0 | 0 | 0 | 0 | 1186.394 | 0 | 0
4302 | 1309.2256 | 0 | 0 | 0 | 0 | 0 | 0 | 1309.226 | 0 | 0
4303 | 1074.5947 | 36.26 | 134.4722 | 134.4722 | 0 | 0 | 0 | 945.145 | 0 | 0
4304 | 998.1356 | 321.32 | 1418.8037 | 1036.8674 | -381.9363 | 0 | 0 | 0 | 0 | 0
4305 | 975.2784 | 536.19 | 2436.7627 | 1013.1234 | -614.9724 | 0 | 808.6669 | 0 | 0 | 0
4306 | 1046.5245 | 720.01 | 3189.249 | 1087.1351 | -41.1024 | 0 | 2061.0115 | 0 | 0 | 0
4307 | 950.4987 | 846.9 | 3680.6899 | 987.3818 | 0 | 0 | 2693.308 | 0 | 0 | 0
4308 | 1002.5404 | 910.74 | 3922.0167 | 1041.4433 | 0 | 0 | 2880.5734 | 0 | 0 | 0
4309 | 1043.7397 | 906.98 | 3911.9746 | 1084.241 | 0 | 0 | 2827.7335 | 0 | 0 | 0
4310 | 1077.3961 | 835.51 | 3639.7236 | 1119.2041 | 0 | 0 | 2520.5195 | 0 | 0 | 0
4311 | 1015.4608 | 698.92 | 3099.1368 | 1054.8657 | 0 | 0 | 2044.2711 | 0 | 0 | 0
4312 | 206.3667 | 511.52 | 2318.5478 | 214.374 | 0 | 0 | 2104.1738 | 0 | 0 | 0
4313 | 168.6547 | 241.03 | 1068.902 | 175.1996 | 0 | 0 | 893.7024 | 0 | 0 | 0
4314 | 147.1628 | 5.87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152.8736
4315 | 189.7642 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197.1277
4316 | 137.5422 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142.8793
4317 | 106.6504 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 110.7885
4318 | 100.7662 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.6762
4319 | 91.2045 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.7431
4320 | 100.0307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.9127
4321 | 92.6755 | 0 | 0 | 0 | 0 | 0 | 0 | 92.676 | 0 | 0
4322 | 100.7662 | 0 | 0 | 0 | 0 | 0 | 0 | 100.766 | 0 | 0
4323 | 91.94 | 0 | 0 | 0 | 0 | 0 | 0 | 91.94 | 0 | 0
4324 | 95.6176 | 0 | 0 | 0 | 0 | 0 | 0 | 95.618 | 0 | 0
4325 | 86.0558 | 0 | 0 | 0 | 0 | 0 | 0 | 86.056 | 0 | 0
4326 | 93.411 | 0 | 0 | 0 | 0 | 0 | 0 | 68.658 | 0 | 25.7135
4327 | 86.0558 | 107.55 | 368.3591 | 89.3954 | -278.9637 | 0 | 0 | 0 | 0 | 0
4328 | 91.951 | 318.51 | 1407.9461 | 95.5191 | -614.9724 | 0 | 697.4545 | 0 | 0 | 0
4329 | 200.9569 | 534.62 | 2434.4981 | 208.7551 | -144.0749 | 0 | 2081.6681 | 0 | 0 | 0
4330 | 878.5446 | 716.82 | 3183.0276 | 912.6367 | 0 | 0 | 2270.3909 | 0 | 0 | 0
4331 | 1068.5028 | 847.59 | 3686.8406 | 1109.966 | 0 | 0 | 2576.8746 | 0 | 0 | 0
4332 | 1462.838 | 911.81 | 3926.2519 | 1519.6041 | 0 | 0 | 2406.6478 | 0 | 0 | 0
4333 | 1268.6028 | 906.34 | 3911.8572 | 1317.8308 | 0 | 0 | 2594.0263 | 0 | 0 | 0
4334 | 1480.9778 | 824.44 | 3591.6726 | 1538.447 | 0 | 0 | 2053.2256 | 0 | 0 | 0
4335 | 1662.323 | 540.9 | 2371.1529 | 1726.829 | 0 | 0 | 644.3238 | 0 | 0 | 0
4336 | 1889.88 | 423.43 | 1886.5307 | 1886.5307 | 0 | 0 | 0 | 73.821 | 0 | 0
4337 | 1479.2732 | 15.67 | 41.2852 | 41.2852 | 0 | 0 | 0 | 1439.53 | 0 | 0
4338 | 1404.2291 | 30.37 | 105.2808 | 105.2808 | 0 | 0 | 0 | 1302.881 | 0 | 0
4339 | 1635.7965 | 0 | 0 | 0 | 0 | 0 | 0 | 1635.796 | 0 | 0
4340 | 1688.7539 | 0 | 0 | 0 | 0 | 0 | 0 | 1688.754 | 0 | 0
4341 | 1451.9165 | 0 | 0 | 0 | 0 | 0 | 0 | 1451.916 | 0 | 0
4342 | 1428.3799 | 0 | 0 | 0 | 0 | 0 | 0 | 1122.506 | 0 | 317.7434
4343 | 1283.4824 | 0 | 0 | 0 | 0 | 0 | 0 | 691.482 | 0 | 614.9724
4344 | 1275.3917 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.392 | 0 | 0
4345 | 1141.0098 | 0 | 0 | 0 | 0 | 0 | 0 | 1141.01 | 0 | 0
4346 | 1317.8249 | 0 | 0 | 0 | 0 | 0 | 0 | 1317.825 | 0 | 0
4347 | 1357.1939 | 0 | 0 | 0 | 0 | 0 | 0 | 1357.194 | 0 | 0
4348 | 1237.7056 | 0 | 0 | 0 | 0 | 0 | 0 | 1237.706 | 0 | 0
4349 | 1136.175 | 0 | 0 | 0 | 0 | 0 | 0 | 1136.175 | 0 | 0
4350 | 1195.5738 | 0 | 0 | 0 | 0 | 0 | 0 | 1195.574 | 0 | 0
4351 | 1022.9029 | 84.42 | 344.4136 | 344.4136 | 0 | 0 | 0 | 691.355 | 0 | 0
4352 | 1129.8233 | 224.13 | 1010.6137 | 1010.6137 | 0 | 0 | 0 | 156.961 | 0 | 0
4353 | 1224.9167 | 375.28 | 1690.5758 | 1272.4486 | -418.1272 | 0 | 0 | 0 | 0 | 0
4354 | 1366.0648 | 547.51 | 2429.489 | 1419.0748 | -614.9724 | 0 | 395.4418 | 0 | 0 | 0
4355 | 1337.9229 | 848.09 | 3743.148 | 1389.8408 | -4.9125 | 0 | 2348.3947 | 0 | 0 | 0
4356 | 1315.4265 | 911.03 | 3981.0862 | 1366.4718 | 0 | 0 | 2614.6144 | 0 | 0 | 0
4357 | 1307.2764 | 734.96 | 3186.3684 | 1358.0045 | 0 | 0 | 1828.3639 | 0 | 0 | 0
4358 | 1149.254 | 577.88 | 2529.5893 | 1193.8505 | 0 | 0 | 1335.7388 | 0 | 0 | 0
4359 | 1075.5123 | 268.57 | 1182.9181 | 1117.247 | 0 | 0 | 65.6712 | 0 | 0 | 0
4360 | 1067.8206 | 307.5 | 1374.3667 | 1109.2575 | 0 | 0 | 265.1092 | 0 | 0 | 0
4361 | 1122.6445 | 15.67 | 42.0726 | 42.0726 | 0 | 0 | 0 | 1082.144 | 0 | 0
4362 | 1180.3883 | 45.86 | 176.4026 | 176.4026 | 0 | 0 | 0 | 1010.575 | 0 | 0
4363 | 1047.7675 | 0 | 0 | 0 | 0 | 0 | 0 | 1047.767 | 0 | 0
4364 | 988.3687 | 0 | 0 | 0 | 0 | 0 | 0 | 988.369 | 0 | 0
4365 | 1236.3242 | 0 | 0 | 0 | 0 | 0 | 0 | 1236.324 | 0 | 0
4366 | 1285.3627 | 0 | 0 | 0 | 0 | 0 | 0 | 979.489 | 0 | 317.7434
4367 | 1237.0149 | 0 | 0 | 0 | 0 | 0 | 0 | 645.015 | 0 | 614.9724
4368 | 955.9065 | 0 | 0 | 0 | 0 | 0 | 0 | 955.907 | 0 | 0
4369 | 1144.4632 | 0 | 0 | 0 | 0 | 0 | 0 | 1144.463 | 0 | 0
4370 | 1100.2595 | 0 | 0 | 0 | 0 | 0 | 0 | 1100.259 | 0 | 0
4371 | 1259.8074 | 0 | 0 | 0 | 0 | 0 | 0 | 1259.807 | 0 | 0
4372 | 1195.5738 | 0 | 0 | 0 | 0 | 0 | 0 | 1195.574 | 0 | 0
4373 | 1084.3737 | 0 | 0 | 0 | 0 | 0 | 0 | 1084.374 | 0 | 0
4374 | 1230.7987 | 0 | 0 | 0 | 0 | 0 | 0 | 1230.799 | 0 | 0
4375 | 855.7574 | 55.75 | 224.2998 | 224.2998 | 0 | 0 | 0 | 639.836 | 0 | 0
4376 | 848.1616 | 197.27 | 885.3078 | 881.0737 | -4.2342 | 0 | 0 | 0 | 0 | 0
4377 | 955.36 | 318.02 | 1426.6996 | 992.4325 | -434.2671 | 0 | 0 | 0 | 0 | 0
4378 | 1003.5499 | 167.49 | 725.5179 | 725.5179 | 0 | 0 | 0 | 0 | 0 | 316.9746
4379 | 826.6632 | 552.84 | 2421.8247 | 858.7414 | -614.9724 | 0 | 948.1109 | 0 | 0 | 0
4380 | 1123.7505 | 740.25 | 3198.3676 | 1167.3568 | -337.2968 | 0 | 1693.714 | 0 | 0 | 0
4381 | 1103.3684 | 779.66 | 3354.3088 | 1146.185 | 0 | 0 | 2208.1239 | 0 | 0 | 0
4382 | 1414.2487 | 677.27 | 2936.5317 | 1469.1286 | 0 | 0 | 1467.4031 | 0 | 0 | 0
4383 | 1156.956 | 479.36 | 2108.3768 | 1201.8514 | 0 | 0 | 906.5254 | 0 | 0 | 0
4384 | 1089.7222 | 422.09 | 1884.3066 | 1132.0084 | 0 | 0 | 752.2982 | 0 | 0 | 0
4385 | 1137.5314 | 46.42 | 180.0456 | 180.0456 | 0 | 0 | 0 | 964.211 | 0 | 0
4386 | 926.8434 | 5.87 | 0 | 0 | 0 | 0 | 0 | 926.843 | 0 | 0
4387 | 835.7275 | 0 | 0 | 0 | 0 | 0 | 0 | 835.728 | 0 | 0
4388 | 1471.8474 | 0 | 0 | 0 | 0 | 0 | 0 | 1471.847 | 0 | 0
4389 | 1105.0942 | 0 | 0 | 0 | 0 | 0 | 0 | 1105.094 | 0 | 0
4390 | 823.2952 | 0 | 0 | 0 | 0 | 0 | 0 | 517.422 | 0 | 317.7434
4391 | 927.5885 | 0 | 0 | 0 | 0 | 0 | 0 | 335.588 | 0 | 614.9724
4392 | 973.8643 | 0 | 0 | 0 | 0 | 0 | 0 | 973.864 | 0 | 0
4393 | 1145.1539 | 0 | 0 | 0 | 0 | 0 | 0 | 1145.154 | 0 | 0
4394 | 1047.7675 | 0 | 0 | 0 | 0 | 0 | 0 | 1047.767 | 0 | 0
4395 | 804.6468 | 0 | 0 | 0 | 0 | 0 | 0 | 804.647 | 0 | 0
4396 | 1138.2471 | 0 | 0 | 0 | 0 | 0 | 0 | 1138.247 | 0 | 0
4397 | 993.2035 | 0 | 0 | 0 | 0 | 0 | 0 | 993.203 | 0 | 0
4398 | 968.3388 | 0 | 0 | 0 | 0 | 0 | 0 | 968.339 | 0 | 0
4399 | 1081.611 | 105.86 | 354.3083 | 354.3083 | 0 | 0 | 0 | 740.538 | 0 | 0
4400 | 1051.0551 | 319.03 | 1413.8309 | 1091.842 | -321.989 | 0 | 0 | 0 | 0 | 0
4401 | 1124.1761 | 272.56 | 1218.2427 | 1167.7994 | -50.4433 | 0 | 0 | 0 | 0 | 0
4402 | 1099.9253 | 548.3 | 2429.7903 | 1142.6073 | -614.9724 | 0 | 672.2106 | 0 | 0 | 0
4403 | 1173.32 | 623.67 | 2729.3639 | 1218.8504 | -50.6064 | 0 | 1459.9071 | 0 | 0 | 0
4404 | 1174.9733 | 798.5 | 3442.1429 | 1220.5675 | 0 | 0 | 2221.5754 | 0 | 0 | 0
4405 | 1130.4682 | 460.67 | 2018.1109 | 1174.3355 | 0 | 0 | 843.7754 | 0 | 0 | 0
4406 | 1162.7327 | 830.02 | 3645.277 | 1207.8515 | 0 | 0 | 2437.4255 | 0 | 0 | 0
4407 | 1439.1789 | 415.36 | 1838.4143 | 1495.026 | 0 | 0 | 343.3883 | 0 | 0 | 0
4408 | 1406.8437 | 233.3 | 1034.3878 | 1034.3878 | 0 | 0 | 0 | 411.095 | 0 | 0
4409 | 1304.5051 | 104.49 | 447.6428 | 447.6428 | 0 | 0 | 0 | 873.584 | 0 | 0
4410 | 1480.7011 | 5.87 | 0 | 0 | 0 | 0 | 0 | 1480.701 | 0 | 0
4411 | 1355.1218 | 0 | 0 | 0 | 0 | 0 | 0 | 1355.122 | 0 | 0
4412 | 982.8432 | 0 | 0 | 0 | 0 | 0 | 0 | 982.843 | 0 | 0
4413 | 1227.3453 | 0 | 0 | 0 | 0 | 0 | 0 | 1227.345 | 0 | 0
4414 | 1230.108 | 0 | 0 | 0 | 0 | 0 | 0 | 924.234 | 0 | 317.7434
4415 | 1073.3228 | 0 | 0 | 0 | 0 | 0 | 0 | 481.323 | 0 | 614.9724
4416 | 1058.8184 | 0 | 0 | 0 | 0 | 0 | 0 | 1058.818 | 0 | 0
4417 | 752.1548 | 0 | 0 | 0 | 0 | 0 | 0 | 752.155 | 0 | 0
4418 | 1158.2769 | 0 | 0 | 0 | 0 | 0 | 0 | 1158.277 | 0 | 0
4419 | 1156.8955 | 0 | 0 | 0 | 0 | 0 | 0 | 1156.896 | 0 | 0
4420 | 1170.7092 | 0 | 0 | 0 | 0 | 0 | 0 | 1170.709 | 0 | 0
4421 | 1391.7281 | 0 | 0 | 0 | 0 | 0 | 0 | 1391.728 | 0 | 0
4422 | 1459.4151 | 0 | 0 | 0 | 0 | 0 | 0 | 1459.415 | 0 | 0
4423 | 1333.7106 | 76.7 | 313.9798 | 313.9798 | 0 | 0 | 0 | 1031.459 | 0 | 0
4424 | 1049.1048 | 229.79 | 1034.849 | 1034.849 | 0 | 0 | 0 | 52.912 | 0 | 0
4425 | 1288.2412 | 534.43 | 2457.1306 | 1338.2309 | -614.9724 | 0 | 503.9273 | 0 | 0 | 0
4426 | 1625.402 | 417.12 | 1856.931 | 1688.4753 | -168.4557 | 0 | 0 | 0 | 0 | 0
4427 | 1252.525 | 325.21 | 1432.9979 | 1301.1289 | -131.869 | 0 | 0 | 0 | 0 | 0
4428 | 1499.6906 | 475.39 | 2090.0367 | 1557.8861 | -122.714 | 0 | 409.4366 | 0 | 0 | 0
4429 | 1174.5986 | 389.54 | 1711.5472 | 1220.179 | 0 | 0 | 491.3682 | 0 | 0 | 0
4430 | 1162.5522 | 729.09 | 3187.9474 | 1207.6645 | 0 | 0 | 1980.2828 | 0 | 0 | 0
4431 | 1383.5979 | 645.07 | 2849.0404 | 1437.2882 | 0 | 0 | 1411.7523 | 0 | 0 | 0
4432 | 1184.4607 | 29.42 | 100.7807 | 100.7807 | 0 | 0 | 0 | 1087.445 | 0 | 0
4433 | 1396.2434 | 184.82 | 821.8504 | 821.8504 | 0 | 0 | 0 | 605.093 | 0 | 0
4434 | 1222.7384 | 27.43 | 93.2223 | 93.2223 | 0 | 0 | 0 | 1132.998 | 0 | 0
4435 | 1330.2572 | 0 | 0 | 0 | 0 | 0 | 0 | 1330.257 | 0 | 0
4436 | 1078.8483 | 0 | 0 | 0 | 0 | 0 | 0 | 1078.848 | 0 | 0
4437 | 1160.349 | 0 | 0 | 0 | 0 | 0 | 0 | 1160.349 | 0 | 0
4438 | 1320.5876 | 0 | 0 | 0 | 0 | 0 | 0 | 1014.714 | 0 | 317.7434
4439 | 1039.4793 | 0 | 0 | 0 | 0 | 0 | 0 | 447.479 | 0 | 614.9724
4440 | 1082.9924 | 0 | 0 | 0 | 0 | 0 | 0 | 1082.992 | 0 | 0
4441 | 1015.996 | 0 | 0 | 0 | 0 | 0 | 0 | 1015.996 | 0 | 0
4442 | 1259.1168 | 0 | 0 | 0 | 0 | 0 | 0 | 1259.117 | 0 | 0
4443 | 955.2158 | 0 | 0 | 0 | 0 | 0 | 0 | 955.216 | 0 | 0
4444 | 1254.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 1254.973 | 0 | 0
4445 | 1275.6932 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.693 | 0 | 0
4446 | 932.4233 | 0 | 0 | 0 | 0 | 0 | 0 | 932.423 | 0 | 0
4447 | 1058.1277 | 97.7 | 390.6903 | 390.6903 | 0 | 0 | 0 | 682.031 | 0 | 0
4448 | 793.1348 | 316.68 | 1408.0521 | 823.9114 | -584.1407 | 0 | 0 | 0 | 0 | 0
4449 | 1186.5863 | 533.87 | 2456.9477 | 1232.6312 | -453.8715 | 0 | 770.4451 | 0 | 0 | 0
4450 | 1347.1392 | 717.62 | 3234.2479 | 1399.4144 | 0 | 0 | 1834.8336 | 0 | 0 | 0
4451 | 1551.5661 | 846.1 | 3748.0387 | 1611.7741 | 0 | 0 | 2136.2646 | 0 | 0 | 0
4452 | 1023.2024 | 911.95 | 4008.0775 | 1062.9071 | 0 | 0 | 2945.1704 | 0 | 0 | 0
4453 | 1250.4936 | 627.66 | 2753.298 | 1299.0181 | 0 | 0 | 1454.2799 | 0 | 0 | 0
4454 | 1279.245 | 716.18 | 3148.6961 | 1328.8858 | 0 | 0 | 1819.8104 | 0 | 0 | 0
4455 | 790.3815 | 527.54 | 2350.5669 | 821.0526 | 0 | 0 | 1529.5143 | 0 | 0 | 0
4456 | 1057.9646 | 420.19 | 1899.3402 | 1099.0191 | 0 | 0 | 800.3211 | 0 | 0 | 0
4457 | 1309.8432 | 129.49 | 565.9938 | 565.9938 | 0 | 0 | 0 | 764.993 | 0 | 0
4458 | 1349.9434 | 56.85 | 225.1869 | 225.1869 | 0 | 0 | 0 | 1133.168 | 0 | 0
4459 | 1201.79 | 0 | 0 | 0 | 0 | 0 | 0 | 1201.79 | 0 | 0
4460 | 1417.2834 | 0 | 0 | 0 | 0 | 0 | 0 | 1417.283 | 0 | 0
4461 | 1335.092 | 0 | 0 | 0 | 0 | 0 | 0 | 1335.092 | 0 | 0
4462 | 1290.1975 | 0 | 0 | 0 | 0 | 0 | 0 | 984.324 | 0 | 317.7434
4463 | 1175.544 | 0 | 0 | 0 | 0 | 0 | 0 | 583.544 | 0 | 614.9724
4464 | 1105.7849 | 0 | 0 | 0 | 0 | 0 | 0 | 1105.785 | 0 | 0
4465 | 1215.6037 | 0 | 0 | 0 | 0 | 0 | 0 | 1215.604 | 0 | 0
4466 | 895.1263 | 0 | 0 | 0 | 0 | 0 | 0 | 895.126 | 0 | 0
4467 | 966.2668 | 0 | 0 | 0 | 0 | 0 | 0 | 966.267 | 0 | 0
4468 | 1008.3985 | 0 | 0 | 0 | 0 | 0 | 0 | 1008.399 | 0 | 0
4469 | 1040.17 | 0 | 0 | 0 | 0 | 0 | 0 | 1040.17 | 0 | 0
4470 | 973.1736 | 0 | 0 | 0 | 0 | 0 | 0 | 973.174 | 0 | 0
4471 | 1027.7377 | 72.08 | 293.855 | 293.855 | 0 | 0 | 0 | 744.86 | 0 | 0
4472 | 181.6015 | 214.53 | 965.3124 | 188.648 | -614.9724 | 0 | 161.692 | 0 | 0 | 0
4473 | 87.356 | 359.1 | 1617.177 | 90.7458 | -423.0387 | 0 | 1103.3924 | 0 | 0 | 0
4474 | 0 | 429.06 | 1904.6454 | 0 | 0 | 0 | 1904.6454 | 0 | 0 | 0
4475 | 0 | 604.77 | 2650.7794 | 0 | 0 | 0 | 2650.7794 | 0 | 0 | 0
4476 | 0 | 724.96 | 3144.5098 | 0 | 0 | 0 | 3144.5098 | 0 | 0 | 0
4477 | 0 | 749.98 | 3247.4782 | 0 | 0 | 0 | 3247.4782 | 0 | 0 | 0
4478 | 0 | 703.14 | 3065.492 | 0 | 0 | 0 | 3065.492 | 0 | 0 | 0
4479 | 0 | 450.3 | 1995.9989 | 0 | 0 | 0 | 1995.9989 | 0 | 0 | 0
4480 | 0 | 393.31 | 1767.8192 | 0 | 0 | 0 | 1767.8192 | 0 | 0 | 0
4481 | 0 | 283.01 | 1267.0925 | 0 | 0 | 0 | 1267.0925 | 0 | 0 | 0
4482 | 0 | 88.79 | 345.2592 | 0 | 0 | 0 | 345.2592 | 0 | 0 | 0
4483 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4485 | 118.7976 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 123.4079
4486 | 193.3915 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.8955
4487 | 241.0487 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 250.4028
4488 | 237.5953 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246.8148
4489 | 234.8325 | 0 | 0 | 0 | 0 | 0 | 0 | 234.833 | 0 | 0
4490 | 251.4089 | 0 | 0 | 0 | 0 | 0 | 0 | 251.409 | 0 | 0
4491 | 171.9803 | 0 | 0 | 0 | 0 | 0 | 0 | 171.98 | 0 | 0
4492 | 178.8871 | 0 | 0 | 0 | 0 | 0 | 0 | 178.887 | 0 | 0
4493 | 246.5742 | 0 | 0 | 0 | 0 | 0 | 0 | 246.574 | 0 | 0
4494 | 227.9257 | 0 | 0 | 0 | 0 | 0 | 0 | 120.885 | 0 | 111.1947
4495 | 274.8922 | 81.17 | 330.5809 | 285.5591 | -45.0218 | 0 | 0 | 0 | 0 | 0
4496 | 119.5695 | 298.22 | 1340.0592 | 124.2088 | -614.9724 | 0 | 600.8779 | 0 | 0 | 0
4497 | 639.3445 | 421.31 | 1892.8352 | 664.1536 | -378.0179 | 0 | 850.6637 | 0 | 0 | 0
4498 | 1147.0671 | 715.45 | 3182.4833 | 1191.5786 | 0 | 0 | 1990.9046 | 0 | 0 | 0
4499 | 1141.3284 | 835.73 | 3644.4429 | 1185.6169 | 0 | 0 | 2458.8259 | 0 | 0 | 0
4500 | 1174.7929 | 662.16 | 2861.2755 | 1220.3795 | 0 | 0 | 1640.896 | 0 | 0 | 0
4501 | 1161.3384 | 897.35 | 3873.4515 | 1206.4045 | 0 | 0 | 2667.047 | 0 | 0 | 0
4502 | 906.2351 | 469.01 | 2049.5088 | 941.4012 | 0 | 0 | 1108.1076 | 0 | 0 | 0
4503 | 844.8066 | 147.96 | 634.7263 | 634.7263 | 0 | 0 | 0 | 0 | 0 | 242.8632
4504 | 961.5296 | 387.24 | 1735.6526 | 998.8419 | -270.2804 | 0 | 466.5303 | 0 | 0 | 0
4505 | 1098.1261 | 14.69 | 37.6785 | 37.6785 | 0 | 0 | 0 | 1061.855 | 0 | 0
4506 | 934.1267 | 16.64 | 45.7687 | 45.7687 | 0 | 0 | 0 | 890.068 | 0 | 0
4507 | 1015.996 | 0 | 0 | 0 | 0 | 0 | 0 | 1015.996 | 0 | 0
4508 | 813.6256 | 0 | 0 | 0 | 0 | 0 | 0 | 813.626 | 0 | 0
4509 | 770.8032 | 0 | 0 | 0 | 0 | 0 | 0 | 770.803 | 0 | 0
4510 | 861.9735 | 0 | 0 | 0 | 0 | 0 | 0 | 556.1 | 0 | 317.7434
4511 | 1115.4545 | 0 | 0 | 0 | 0 | 0 | 0 | 523.455 | 0 | 614.9724
4512 | 933.114 | 0 | 0 | 0 | 0 | 0 | 0 | 933.114 | 0 | 0
4513 | 1098.8781 | 0 | 0 | 0 | 0 | 0 | 0 | 1098.878 | 0 | 0
4514 | 1076.0855 | 0 | 0 | 0 | 0 | 0 | 0 | 1076.086 | 0 | 0
4515 | 1114.0731 | 0 | 0 | 0 | 0 | 0 | 0 | 1114.073 | 0 | 0
4516 | 739.0318 | 0 | 0 | 0 | 0 | 0 | 0 | 739.032 | 0 | 0
4517 | 871.6431 | 0 | 0 | 0 | 0 | 0 | 0 | 871.643 | 0 | 0
4518 | 1126.5055 | 0 | 0 | 0 | 0 | 0 | 0 | 1126.505 | 0 | 0
4519 | 891.6729 | 75.94 | 309.8993 | 309.8993 | 0 | 0 | 0 | 593.35 | 0 | 0
4520 | 1175.0536 | 224.52 | 1010.1524 | 1010.1524 | 0 | 0 | 0 | 202.635 | 0 | 0
4521 | 977.329 | 359.72 | 1614.3036 | 1015.254 | -599.0496 | 0 | 0 | 0 | 0 | 0
4522 | 1380.4794 | 386.39 | 1706.7157 | 1434.0492 | -272.6665 | 0 | 0 | 0 | 0 | 0
4523 | 1327.1344 | 630.45 | 2736.7332 | 1378.6341 | -166.295 | 0 | 1191.8041 | 0 | 0 | 0
4524 | 1231.0111 | 271.25 | 1178.5365 | 1178.5365 | 0 | 0 | 0 | 0 | 0 | 100.2447
4525 | 1202.3589 | 781.74 | 3344.9523 | 1249.0152 | -111.5614 | 0 | 1984.3757 | 0 | 0 | 0
4526 | 1118.7189 | 628.84 | 2727.9033 | 1162.1306 | 0 | 0 | 1565.7727 | 0 | 0 | 0
4527 | 1397.5799 | 589.58 | 2588.6111 | 1451.8127 | 0 | 0 | 1136.7983 | 0 | 0 | 0
4528 | 1387.754 | 316.76 | 1412.7485 | 1412.7485 | 0 | 0 | 0 | 27.779 | 0 | 0
4529 | 1404.902 | 18.61 | 54.8821 | 54.8821 | 0 | 0 | 0 | 1352.07 | 0 | 0
4530 | 1178.5865 | 38.23 | 141.7522 | 141.7522 | 0 | 0 | 0 | 1042.129 | 0 | 0
4531 | 1232.8708 | 0 | 0 | 0 | 0 | 0 | 0 | 1232.871 | 0 | 0
4532 | 1013.2333 | 0 | 0 | 0 | 0 | 0 | 0 | 1013.233 | 0 | 0
4533 | 1301.9392 | 0 | 0 | 0 | 0 | 0 | 0 | 1301.939 | 0 | 0
4534 | 1252.9006 | 0 | 0 | 0 | 0 | 0 | 0 | 947.027 | 0 | 317.7434
4535 | 1488.4238 | 0 | 0 | 0 | 0 | 0 | 0 | 896.424 | 0 | 614.9724
4536 | 1379.9864 | 0 | 0 | 0 | 0 | 0 | 0 | 1379.986 | 0 | 0
4537 | 1263.2609 | 0 | 0 | 0 | 0 | 0 | 0 | 1263.261 | 0 | 0
4538 | 1365.4821 | 0 | 0 | 0 | 0 | 0 | 0 | 1365.482 | 0 | 0
4539 | 1331.6386 | 0 | 0 | 0 | 0 | 0 | 0 | 1331.639 | 0 | 0
4540 | 1141.0098 | 0 | 0 | 0 | 0 | 0 | 0 | 1141.01 | 0 | 0
4541 | 1093.3526 | 0 | 0 | 0 | 0 | 0 | 0 | 1093.353 | 0 | 0
4542 | 949.6904 | 0 | 0 | 0 | 0 | 0 | 0 | 949.69 | 0 | 0
4543 | 966.9575 | 103.6 | 337.8609 | 337.8609 | 0 | 0 | 0 | 641.717 | 0 | 0
4544 | 843.7136 | 253.68 | 1141.3545 | 876.4531 | -264.9014 | 0 | 0 | 0 | 0 | 0
4545 | 1005.3405 | 440.11 | 1976.2814 | 1044.352 | -614.9724 | 0 | 316.957 | 0 | 0 | 0
4546 | 1563.6281 | 722.53 | 3210.557 | 1624.3042 | -158.1383 | 0 | 1428.1145 | 0 | 0 | 0
4547 | 1371.9495 | 848.08 | 3688.7448 | 1425.1871 | 0 | 0 | 2263.5576 | 0 | 0 | 0
4548 | 1263.6571 | 664.31 | 2856.5209 | 1312.6929 | 0 | 0 | 1543.828 | 0 | 0 | 0
4549 | 1241.5078 | 202.73 | 870.7833 | 870.7833 | 0 | 0 | 0 | 403.253 | 0 | 0
4550 | 1242.3884 | 95.77 | 391.9857 | 391.9857 | 0 | 0 | 0 | 865.045 | 0 | 0
4551 | 1546.4283 | 95.6 | 394.1797 | 394.1797 | 0 | 0 | 0 | 1166.973 | 0 | 0
4552 | 1391.9206 | 54.66 | 212.928 | 212.928 | 0 | 0 | 0 | 1186.947 | 0 | 0
4553 | 1102.5551 | 35.28 | 128.8419 | 128.8419 | 0 | 0 | 0 | 978.526 | 0 | 0
4554 | 1208.6278 | 33.32 | 119.2267 | 119.2267 | 0 | 0 | 0 | 1093.855 | 0 | 0
4555 | 1185.9043 | 0 | 0 | 0 | 0 | 0 | 0 | 1185.904 | 0 | 0
4556 | 1010.4706 | 0 | 0 | 0 | 0 | 0 | 0 | 1010.471 | 0 | 0
4557 | 1031.1911 | 0 | 0 | 0 | 0 | 0 | 0 | 1031.191 | 0 | 0
4558 | 1206.6248 | 0 | 0 | 0 | 0 | 0 | 0 | 900.751 | 0 | 317.7434
4559 | 1274.3118 | 0 | 0 | 0 | 0 | 0 | 0 | 682.312 | 0 | 614.9724
4560 | 1225.2732 | 0 | 0 | 0 | 0 | 0 | 0 | 1225.273 | 0 | 0
4561 | 1292.9603 | 0 | 0 | 0 | 0 | 0 | 0 | 1292.96 | 0 | 0
4562 | 1131.3402 | 0 | 0 | 0 | 0 | 0 | 0 | 1131.34 | 0 | 0
4563 | 1158.2769 | 0 | 0 | 0 | 0 | 0 | 0 | 1158.277 | 0 | 0
4564 | 1222.5105 | 0 | 0 | 0 | 0 | 0 | 0 | 1222.511 | 0 | 0
4565 | 826.7486 | 0 | 0 | 0 | 0 | 0 | 0 | 826.749 | 0 | 0
4566 | 1008.3985 | 0 | 0 | 0 | 0 | 0 | 0 | 1008.399 | 0 | 0
4567 | 964.1947 | 94.99 | 377.8569 | 377.8569 | 0 | 0 | 0 | 600.452 | 0 | 0
4568 | 949.7888 | 269.72 | 1208.7802 | 986.6453 | -222.1349 | 0 | 0 | 0 | 0 | 0
4569 | 1299.4648 | 414.56 | 1852.1993 | 1349.8894 | -502.3099 | 0 | 0 | 0 | 0 | 0
4570 | 1185.0608 | 489.96 | 2151.6191 | 1231.047 | -313.5663 | 0 | 607.0058 | 0 | 0 | 0
4571 | 1494.3067 | 627.89 | 2712.4854 | 1552.2922 | 0 | 0 | 1160.1932 | 0 | 0 | 0
4572 | 1253.3755 | 757.22 | 3225.7619 | 1302.0129 | 0 | 0 | 1923.749 | 0 | 0 | 0
4573 | 1225.6264 | 735.66 | 3142.0135 | 1273.1861 | 0 | 0 | 1868.8274 | 0 | 0 | 0
4574 | 1352.7545 | 587.3 | 2540.4656 | 1405.2483 | 0 | 0 | 1135.2173 | 0 | 0 | 0
4575 | 1293.0716 | 591.73 | 2581.1535 | 1343.2493 | 0 | 0 | 1237.9041 | 0 | 0 | 0
4576 | 998.7617 | 378.78 | 1687.288 | 1037.5187 | 0 | 0 | 649.7693 | 0 | 0 | 0
4577 | 1126.9881 | 162.34 | 715.9962 | 715.9962 | 0 | 0 | 0 | 437.738 | 0 | 0
4578 | 1225.8163 | 35.28 | 128.4461 | 128.4461 | 0 | 0 | 0 | 1102.168 | 0 | 0
4579 | 1032.5724 | 0 | 0 | 0 | 0 | 0 | 0 | 1032.572 | 0 | 0
4580 | 1021.5215 | 0 | 0 | 0 | 0 | 0 | 0 | 1021.521 | 0 | 0
4581 | 1216.2944 | 0 | 0 | 0 | 0 | 0 | 0 | 1216.294 | 0 | 0
4582 | 1219.0571 | 0 | 0 | 0 | 0 | 0 | 0 | 913.183 | 0 | 317.7434
4583 | 1163.1117 | 0 | 0 | 0 | 0 | 0 | 0 | 571.112 | 0 | 614.9724
4584 | 1101.6408 | 0 | 0 | 0 | 0 | 0 | 0 | 1101.641 | 0 | 0
4585 | 1022.2122 | 0 | 0 | 0 | 0 | 0 | 0 | 1022.212 | 0 | 0
4586 | 1254.9727 | 0 | 0 | 0 | 0 | 0 | 0 | 1254.973 | 0 | 0
4587 | 1133.4123 | 0 | 0 | 0 | 0 | 0 | 0 | 1133.412 | 0 | 0
4588 | 973.1736 | 0 | 0 | 0 | 0 | 0 | 0 | 973.174 | 0 | 0
4589 | 1258.4261 | 0 | 0 | 0 | 0 | 0 | 0 | 1258.426 | 0 | 0
4590 | 1203.862 | 0 | 0 | 0 | 0 | 0 | 0 | 1203.862 | 0 | 0
4591 | 1112.6918 | 52.72 | 208.9119 | 208.9119 | 0 | 0 | 0 | 911.584 | 0 | 0
4592 | 1002.4448 | 101.99 | 437.0148 | 437.0148 | 0 | 0 | 0 | 581.755 | 0 | 0
4593 | 715.8188 | 207.53 | 914.653 | 743.5951 | -171.0579 | 0 | 0 | 0 | 0 | 0
4594 | 888.077 | 472.76 | 2071.6623 | 922.5386 | -614.9724 | 0 | 534.1513 | 0 | 0 | 0
4595 | 1386.1353 | 589.68 | 2551.9558 | 1439.9236 | -251.9818 | 0 | 860.0503 | 0 | 0 | 0
4596 | 1199.0566 | 619.05 | 2669.6389 | 1245.5861 | 0 | 0 | 1424.0528 | 0 | 0 | 0
4597 | 1228.0489 | 469.8 | 2041.6315 | 1275.7031 | 0 | 0 | 765.9284 | 0 | 0 | 0
4598 | 1402.9448 | 566.28 | 2461.2474 | 1457.3859 | 0 | 0 | 1003.8614 | 0 | 0 | 0
4599 | 1345.1535 | 370.99 | 1633.2223 | 1397.3524 | 0 | 0 | 235.87 | 0 | 0 | 0
4600 | 1550.7356 | 32.36 | 113.5788 | 113.5788 | 0 | 0 | 0 | 1441.4 | 0 | 0
4601 | 1497.0151 | 16.65 | 46.1354 | 46.1354 | 0 | 0 | 0 | 1452.603 | 0 | 0
4602 | 1191.2752 | 9.79 | 16.1451 | 16.1451 | 0 | 0 | 0 | 1175.733 | 0 | 0
4603 | 1230.7987 | 0 | 0 | 0 | 0 | 0 | 0 | 1230.799 | 0 | 0
4604 | 1251.5192 | 0 | 0 | 0 | 0 | 0 | 0 | 1251.519 | 0 | 0
4605 | 1339.2361 | 0 | 0 | 0 | 0 | 0 | 0 | 1339.236 | 0 | 0
4606 | 1237.0149 | 0 | 0 | 0 | 0 | 0 | 0 | 931.141 | 0 | 317.7434
4607 | 1361.338 | 0 | 0 | 0 | 0 | 0 | 0 | 769.338 | 0 | 614.9724
4608 | 1507.763 | 0 | 0 | 0 | 0 | 0 | 0 | 1507.763 | 0 | 0
4609 | 607.8018 | 0 | 0 | 0 | 0 | 0 | 0 | 607.802 | 0 | 0
4610 | 762.515 | 0 | 0 | 0 | 0 | 0 | 0 | 762.515 | 0 | 0
4611 | 928.2792 | 0 | 0 | 0 | 0 | 0 | 0 | 928.279 | 0 | 0
4612 | 756.9896 | 0 | 0 | 0 | 0 | 0 | 0 | 756.99 | 0 | 0
4613 | 800.5026 | 0 | 0 | 0 | 0 | 0 | 0 | 800.503 | 0 | 0
4614 | 622.3062 | 0 | 0 | 0 | 0 | 0 | 0 | 622.306 | 0 | 0
4615 | 551.1658 | 46.92 | 183.0031 | 183.0031 | 0 | 0 | 0 | 374.999 | 0 | 0
4616 | 537.6301 | 318.19 | 1408.7501 | 558.4926 | -614.9724 | 0 | 235.2851 | 0 | 0 | 0
4617 | 520.8758 | 536.61 | 2460.6324 | 541.0885 | -423.0387 | 0 | 1496.5052 | 0 | 0 | 0
4618 | 948.3591 | 721.75 | 3231.3975 | 985.1598 | 0 | 0 | 2246.2376 | 0 | 0 | 0
4619 | 845.2702 | 854.48 | 3756.0697 | 878.0705 | 0 | 0 | 2877.9992 | 0 | 0 | 0
4620 | 618.959 | 922.7 | 4018.8946 | 642.9775 | 0 | 0 | 3375.917 | 0 | 0 | 0
4621 | 587.2298 | 525.16 | 2294.62 | 610.0173 | 0 | 0 | 1684.6027 | 0 | 0 | 0
4622 | 673.7052 | 850.13 | 3737.713 | 699.848 | 0 | 0 | 3037.865 | 0 | 0 | 0
4623 | 761.9789 | 485.35 | 2147.7641 | 791.5474 | 0 | 0 | 1356.2167 | 0 | 0 | 0
4624 | 727.5949 | 29.42 | 100.7921 | 100.7921 | 0 | 0 | 0 | 630.568 | 0 | 0
4625 | 423.3979 | 21.55 | 67.97 | 67.97 | 0 | 0 | 0 | 357.967 | 0 | 0
4626 | 585.8407 | 10.77 | 20.3793 | 20.3793 | 0 | 0 | 0 | 566.222 | 0 | 0
4627 | 736.9597 | 0 | 0 | 0 | 0 | 0 | 0 | 736.96 | 0 | 0
4628 | 609.1832 | 0 | 0 | 0 | 0 | 0 | 0 | 609.183 | 0 | 0
4629 | 715.5485 | 0 | 0 | 0 | 0 | 0 | 0 | 715.549 | 0 | 0
4630 | 707.951 | 0 | 0 | 0 | 0 | 0 | 0 | 402.077 | 0 | 317.7434
4631 | 652.0056 | 0 | 0 | 0 | 0 | 0 | 0 | 60.006 | 0 | 614.9724
4632 | 602.2764 | 0 | 0 | 0 | 0 | 0 | 0 | 602.276 | 0 | 0
4633 | 1192.8111 | 0 | 0 | 0 | 0 | 0 | 0 | 1192.811 | 0 | 0
4634 | 1270.8584 | 0 | 0 | 0 | 0 | 0 | 0 | 1270.858 | 0 | 0
4635 | 1317.8249 | 0 | 0 | 0 | 0 | 0 | 0 | 1317.825 | 0 | 0
4636 | 1299.8671 | 0 | 0 | 0 | 0 | 0 | 0 | 1299.867 | 0 | 0
4637 | 1154.1328 | 0 | 0 | 0 | 0 | 0 | 0 | 1154.133 | 0 | 0
4638 | 1298.4857 | 0 | 0 | 0 | 0 | 0 | 0 | 1298.486 | 0 | 0
4639 | 998.7289 | 101.39 | 329.8589 | 329.8589 | 0 | 0 | 0 | 681.192 | 0 | 0
4640 | 130.6101 | 318.23 | 1403.4159 | 135.6783 | -614.9724 | 0 | 652.7652 | 0 | 0 | 0
4641 | 175.9232 | 536.49 | 2440.4235 | 182.7496 | -423.0387 | 0 | 1834.6351 | 0 | 0 | 0
4642 | 234.3197 | 722.37 | 3202.6911 | 243.4127 | 0 | 0 | 2959.2784 | 0 | 0 | 0
4643 | 194.8402 | 507.75 | 2216.8571 | 202.4007 | 0 | 0 | 2014.4564 | 0 | 0 | 0
4644 | 182.0764 | 406.52 | 1774.4302 | 189.1414 | 0 | 0 | 1585.2888 | 0 | 0 | 0
4645 | 203.5454 | 390.82 | 1707.1769 | 211.4446 | 0 | 0 | 1495.7324 | 0 | 0 | 0
4646 | 203.7794 | 588.73 | 2572.4722 | 211.6876 | 0 | 0 | 2360.7846 | 0 | 0 | 0
4647 | 223.5096 | 593.41 | 2618.4476 | 232.1832 | 0 | 0 | 2386.2644 | 0 | 0 | 0
4648 | 227.8445 | 453.63 | 2035.0663 | 236.6854 | 0 | 0 | 1798.3809 | 0 | 0 | 0
4649 | 436.2411 | 20.57 | 63.2684 | 63.2684 | 0 | 0 | 0 | 375.337 | 0 | 0
4650 | 395.2318 | 67.63 | 270.0155 | 270.0155 | 0 | 0 | 0 | 135.303 | 0 | 0
4651 | 255.553 | 0 | 0 | 0 | 0 | 0 | 0 | 255.553 | 0 | 0
4652 | 228.6164 | 0 | 0 | 0 | 0 | 0 | 0 | 178.903 | 0 | 51.6431
4653 | 206.5145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214.5277
4654 | 243.8114 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.272
4655 | 205.1331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 213.0931
4656 | 192.7008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.1787
4657 | 223.7816 | 0 | 0 | 0 | 0 | 0 | 0 | 223.782 | 0 | 0
4658 | 188.5567 | 0 | 0 | 0 | 0 | 0 | 0 | 188.557 | 0 | 0
4659 | 172.671 | 0 | 0 | 0 | 0 | 0 | 0 | 172.671 | 0 | 0
4660 | 181.6499 | 0 | 0 | 0 | 0 | 0 | 0 | 181.65 | 0 | 0
4661 | 106.3653 | 0 | 0 | 0 | 0 | 0 | 0 | 106.365 | 0 | 0
4662 | 155.4039 | 0 | 0 | 0 | 0 | 0 | 0 | 155.404 | 0 | 0
4663 | 132.6113 | 100.53 | 338.3813 | 137.7569 | -200.6244 | 0 | 0 | 0 | 0 | 0
4664 | 210.6517 | 313.29 | 1379.8132 | 218.8263 | -614.9724 | 0 | 546.0145 | 0 | 0 | 0
4665 | 378.0493 | 530.49 | 2406.2468 | 392.7201 | -222.4143 | 0 | 1791.1123 | 0 | 0 | 0
4666 | 837.0277 | 715.66 | 3156.2898 | 869.5087 | 0 | 0 | 2286.7811 | 0 | 0 | 0
4667 | 1269.6825 | 566.89 | 2454.5169 | 1318.9517 | 0 | 0 | 1135.5653 | 0 | 0 | 0
4668 | 1312.5904 | 784.48 | 3342.4509 | 1363.5247 | 0 | 0 | 1978.9262 | 0 | 0 | 0
4669 | 1239.8562 | 763.38 | 3261.8843 | 1287.9683 | 0 | 0 | 1973.916 | 0 | 0 | 0
4670 | 1427.338 | 837.46 | 3632.8456 | 1482.7255 | 0 | 0 | 2150.1201 | 0 | 0 | 0
4671 | 1379.6333 | 704.34 | 3112.1416 | 1433.1693 | 0 | 0 | 1678.9723 | 0 | 0 | 0
4672 | 1408.1145 | 443.87 | 1979.002 | 1462.7565 | 0 | 0 | 516.2454 | 0 | 0 | 0
4673 | 1482.0911 | 301.48 | 1317.6802 | 1317.6802 | 0 | 0 | 0 | 213.633 | 0 | 0
4674 | 1357.8284 | 94.64 | 322.1354 | 322.1354 | 0 | 0 | 0 | 1047.726 | 0 | 0
4675 | 1372.3889 | 0 | 0 | 0 | 0 | 0 | 0 | 1372.389 | 0 | 0
4676 | 1344.7616 | 0 | 0 | 0 | 0 | 0 | 0 | 1344.762 | 0 | 0
4677 | 1383.4399 | 0 | 0 | 0 | 0 | 0 | 0 | 1383.44 | 0 | 0
4678 | 1246.6844 | 0 | 0 | 0 | 0 | 0 | 0 | 940.811 | 0 | 317.7434
4679 | 1187.2856 | 0 | 0 | 0 | 0 | 0 | 0 | 595.286 | 0 | 614.9724
4680 | 944.1649 | 0 | 0 | 0 | 0 | 0 | 0 | 944.165 | 0 | 0
4681 | 1060.1998 | 0 | 0 | 0 | 0 | 0 | 0 | 1060.2 | 0 | 0
4682 | 1112.0011 | 0 | 0 | 0 | 0 | 0 | 0 | 1112.001 | 0 | 0
4683 | 985.6059 | 0 | 0 | 0 | 0 | 0 | 0 | 985.606 | 0 | 0
4684 | 1117.5266 | 0 | 0 | 0 | 0 | 0 | 0 | 1117.527 | 0 | 0
4685 | 919.991 | 0 | 0 | 0 | 0 | 0 | 0 | 919.991 | 0 | 0
4686 | 716.2392 | 0 | 0 | 0 | 0 | 0 | 0 | 716.239 | 0 | 0
4687 | 888.9102 | 55.77 | 222.9992 | 222.9992 | 0 | 0 | 0 | 674.241 | 0 | 0
4688 | 709.9428 | 272.52 | 1225.1559 | 737.4922 | -487.6638 | 0 | 0 | 0 | 0 | 0
4689 | 511.2727 | 535.68 | 2443.517 | 531.1128 | -550.3473 | 0 | 1362.0569 | 0 | 0 | 0
4690 | 207.6748 | 721.43 | 3210.9652 | 215.7338 | 0 | 0 | 2995.2314 | 0 | 0 | 0
4691 | 138.7688 | 849.15 | 3711.9278 | 144.1539 | 0 | 0 | 3567.7739 | 0 | 0 | 0
4692 | 202.4179 | 917.34 | 3970.1684 | 210.2728 | 0 | 0 | 3759.8956 | 0 | 0 | 0
4693 | 689.9172 | 915.92 | 3966.195 | 716.6901 | 0 | 0 | 3249.5049 | 0 | 0 | 0
4694 | 1105.1745 | 645.64 | 2808.2393 | 1148.061 | 0 | 0 | 1660.1783 | 0 | 0 | 0
4695 | 1065.5889 | 502.08 | 2213.3501 | 1106.9389 | 0 | 0 | 1106.4112 | 0 | 0 | 0
4696 | 1205.8909 | 338.18 | 1508.2946 | 1252.6853 | 0 | 0 | 255.6093 | 0 | 0 | 0
4697 | 1007.9081 | 137.76 | 601.4835 | 601.4835 | 0 | 0 | 0 | 428.893 | 0 | 0
4698 | 1302.5098 | 40.19 | 150.3992 | 150.3992 | 0 | 0 | 0 | 1157.729 | 0 | 0
4699 | 973.1736 | 0 | 0 | 0 | 0 | 0 | 0 | 973.174 | 0 | 0
4700 | 879.9313 | 0 | 0 | 0 | 0 | 0 | 0 | 879.931 | 0 | 0
4701 | 879.2406 | 0 | 0 | 0 | 0 | 0 | 0 | 879.241 | 0 | 0
4702 | 925.5164 | 0 | 0 | 0 | 0 | 0 | 0 | 619.643 | 0 | 317.7434
4703 | 1076.0855 | 0 | 0 | 0 | 0 | 0 | 0 | 484.086 | 0 | 614.9724
4704 | 1077.4669 | 0 | 0 | 0 | 0 | 0 | 0 | 1077.467 | 0 | 0
4705 | 1165.8744 | 0 | 0 | 0 | 0 | 0 | 0 | 1165.874 | 0 | 0
4706 | 1019.4494 | 0 | 0 | 0 | 0 | 0 | 0 | 1019.449 | 0 | 0
4707 | 1090.5899 | 0 | 0 | 0 | 0 | 0 | 0 | 1090.59 | 0 | 0
4708 | 797.7399 | 0 | 0 | 0 | 0 | 0 | 0 | 797.74 | 0 | 0
4709 | 1000.1103 | 0 | 0 | 0 | 0 | 0 | 0 | 1000.11 | 0 | 0
4710 | 815.6977 | 0 | 0 | 0 | 0 | 0 | 0 | 815.698 | 0 | 0
4711 | 1003.5637 | 100.09 | 333.8511 | 333.8511 | 0 | 0 | 0 | 682.184 | 0 | 0
4712 | 951.6977 | 306.25 | 1373.4796 | 988.6284 | -384.8512 | 0 | 0 | 0 | 0 | 0
4713 | 1121.6603 | 421.71 | 1887.3524 | 1165.1857 | -614.9724 | 0 | 107.1943 | 0 | 0 | 0
4714 | 1083.6407 | 585.03 | 2556.297 | 1125.6914 | -38.1875 | 0 | 1392.418 | 0 | 0 | 0
4715 | 1503.6577 | 647.93 | 2779.8457 | 1562.006 | 0 | 0 | 1217.8396 | 0 | 0 | 0
4716 | 1480.6329 | 758.01 | 3195.2813 | 1538.0886 | 0 | 0 | 1657.1927 | 0 | 0 | 0
4717 | 1652.4707 | 710.88 | 2999.1841 | 1716.5937 | 0 | 0 | 1282.5904 | 0 | 0 | 0
4718 | 1615.0866 | 753.05 | 3174.5229 | 1677.76 | 0 | 0 | 1496.7629 | 0 | 0 | 0
4719 | 1540.0611 | 707.97 | 3074.6823 | 1599.8227 | 0 | 0 | 1474.8597 | 0 | 0 | 0
4720 | 1743.6635 | 362.49 | 1595.6508 | 1595.6508 | 0 | 0 | 0 | 207.619 | 0 | 0
4721 | 1217.598 | 139.71 | 605.3988 | 605.3988 | 0 | 0 | 0 | 634.814 | 0 | 0
4722 | 1425.4723 | 26.45 | 88.1956 | 88.1956 | 0 | 0 | 0 | 1340.571 | 0 | 0
4723 | 1408.9952 | 0 | 0 | 0 | 0 | 0 | 0 | 1408.995 | 0 | 0
4724 | 1178.3067 | 0 | 0 | 0 | 0 | 0 | 0 | 1178.307 | 0 | 0
4725 | 1460.1058 | 0 | 0 | 0 | 0 | 0 | 0 | 1460.106 | 0 | 0
4726 | 1165.1837 | 0 | 0 | 0 | 0 | 0 | 0 | 859.31 | 0 | 317.7434
4727 | 1237.7056 | 0 | 0 | 0 | 0 | 0 | 0 | 645.706 | 0 | 614.9724
4728 | 1343.3802 | 0 | 0 | 0 | 0 | 0 | 0 | 1343.38 | 0 | 0
4729 | 1258.4261 | 0 | 0 | 0 | 0 | 0 | 0 | 1258.426 | 0 | 0
4730 | 1290.1975 | 0 | 0 | 0 | 0 | 0 | 0 | 1290.198 | 0 | 0
4731 | 1518.8139 | 0 | 0 | 0 | 0 | 0 | 0 | 1518.814 | 0 | 0
4732 | 1493.2586 | 0 | 0 | 0 | 0 | 0 | 0 | 1493.259 | 0 | 0
4733 | 1221.1291 | 0 | 0 | 0 | 0 | 0 | 0 | 1221.129 | 0 | 0
4734 | 1216.2944 | 0 | 0 | 0 | 0 | 0 | 0 | 1216.294 | 0 | 0
4735 | 1270.1677 | 82.09 | 330.1789 | 330.1789 | 0 | 0 | 0 | 952.323 | 0 | 0
4736 | 1420.868 | 245.85 | 1106.7758 | 1106.7758 | 0 | 0 | 0 | 355.436 | 0 | 0
4737 | 1032.7373 | 408.81 | 1840.9158 | 1072.8121 | -614.9724 | 0 | 153.1312 | 0 | 0 | 0
4738 | 983.6487 | 547.94 | 2426.248 | 1021.8193 | -423.0387 | 0 | 981.39 | 0 | 0 | 0
4739 | 1036.9712 | 625.51 | 2733.4391 | 1077.2104 | 0 | 0 | 1656.2287 | 0 | 0 | 0
4740 | 1264.5447 | 631.45 | 2743.2268 | 1313.6154 | 0 | 0 | 1429.6114 | 0 | 0 | 0
4741 | 1287.5099 | 738.42 | 3184.9494 | 1337.4715 | 0 | 0 | 1847.4779 | 0 | 0 | 0
4742 | 1054.9635 | 680.13 | 2948.3533 | 1095.9006 | 0 | 0 | 1852.4527 | 0 | 0 | 0
4743 | 1243.8855 | 236.97 | 1035.2572 | 1035.2572 | 0 | 0 | 0 | 247.3 | 0 | 0
4744 | 986.9251 | 193.62 | 848.878 | 848.878 | 0 | 0 | 0 | 169.757 | 0 | 0
4745 | 1104.938 | 236.51 | 1053.3896 | 1053.3896 | 0 | 0 | 0 | 90.898 | 0 | 0
4746 | 1034.1178 | 5.87 | 0 | 0 | 0 | 0 | 0 | 1034.118 | 0 | 0
4747 | 840.5623 | 0 | 0 | 0 | 0 | 0 | 0 | 840.562 | 0 | 0
4748 | 1201.79 | 0 | 0 | 0 | 0 | 0 | 0 | 1201.79 | 0 | 0
4749 | 714.1672 | 0 | 0 | 0 | 0 | 0 | 0 | 714.167 | 0 | 0
4750 | 1128.5775 | 0 | 0 | 0 | 0 | 0 | 0 | 822.704 | 0 | 317.7434
4751 | 844.7064 | 0 | 0 | 0 | 0 | 0 | 0 | 252.706 | 0 | 614.9724
4752 | 1005.6358 | 0 | 0 | 0 | 0 | 0 | 0 | 1005.636 | 0 | 0
4753 | 1029.119 | 0 | 0 | 0 | 0 | 0 | 0 | 1029.119 | 0 | 0
4754 | 1085.7551 | 0 | 0 | 0 | 0 | 0 | 0 | 1085.755 | 0 | 0
4755 | 1188.667 | 0 | 0 | 0 | 0 | 0 | 0 | 1188.667 | 0 | 0
4756 | 1035.3352 | 0 | 0 | 0 | 0 | 0 | 0 | 1035.335 | 0 | 0
4757 | 943.4742 | 0 | 0 | 0 | 0 | 0 | 0 | 943.474 | 0 | 0
4758 | 1012.5426 | 0 | 0 | 0 | 0 | 0 | 0 | 1012.543 | 0 | 0
4759 | 1096.806 | 12.73 | 29.2029 | 29.2029 | 0 | 0 | 0 | 1068.694 | 0 | 0
4760 | 934.3477 | 34.3 | 125.7972 | 125.7972 | 0 | 0 | 0 | 813.25 | 0 | 0
4761 | 1094.2419 | 429.02 | 1931.1515 | 1136.7038 | -614.9724 | 0 | 179.4753 | 0 | 0 | 0
4762 | 1260.8348 | 602.89 | 2660.3301 | 1309.7614 | -423.0387 | 0 | 927.5301 | 0 | 0 | 0
4763 | 1083.1262 | 596.29 | 2604.1588 | 1125.1564 | 0 | 0 | 1479.0024 | 0 | 0 | 0
4764 | 1249.8858 | 691.6 | 2993.3834 | 1298.3875 | 0 | 0 | 1694.9959 | 0 | 0 | 0
4765 | 1115.5132 | 729.3 | 3153.5931 | 1158.8002 | 0 | 0 | 1994.7929 | 0 | 0 | 0
4766 | 1150.3401 | 639.18 | 2792.7445 | 1194.9787 | 0 | 0 | 1597.7658 | 0 | 0 | 0
4767 | 1467.4236 | 534.82 | 2371.9579 | 1524.367 | 0 | 0 | 847.5909 | 0 | 0 | 0
4768 | 1501.2835 | 483.77 | 2188.9725 | 1559.5399 | 0 | 0 | 629.4326 | 0 | 0 | 0
4769 | 1430.4064 | 271.4 | 1226.1137 | 1226.1137 | 0 | 0 | 0 | 250.094 | 0 | 0
4770 | 1592.421 | 88.93 | 349.8372 | 349.8372 | 0 | 0 | 0 | 1255.652 | 0 | 0
4771 | 1372.3889 | 0 | 0 | 0 | 0 | 0 | 0 | 1372.389 | 0 | 0
4772 | 1328.8758 | 0 | 0 | 0 | 0 | 0 | 0 | 1328.876 | 0 | 0
4773 | 1486.3518 | 0 | 0 | 0 | 0 | 0 | 0 | 1486.352 | 0 | 0
4774 | 1364.1007 | 0 | 0 | 0 | 0 | 0 | 0 | 1058.227 | 0 | 317.7434
4775 | 1410.3765 | 0 | 0 | 0 | 0 | 0 | 0 | 818.377 | 0 | 614.9724
4776 | 1210.7689 | 0 | 0 | 0 | 0 | 0 | 0 | 1210.769 | 0 | 0
4777 | 1007.0171 | 0 | 0 | 0 | 0 | 0 | 0 | 1007.017 | 0 | 0
4778 | 820.5325 | 0 | 0 | 0 | 0 | 0 | 0 | 820.532 | 0 | 0
4779 | 1060.8905 | 0 | 0 | 0 | 0 | 0 | 0 | 1060.89 | 0 | 0
4780 | 1237.7056 | 0 | 0 | 0 | 0 | 0 | 0 | 1237.706 | 0 | 0
4781 | 960.7413 | 0 | 0 | 0 | 0 | 0 | 0 | 960.741 | 0 | 0
4782 | 1200.4086 | 0 | 0 | 0 | 0 | 0 | 0 | 1200.409 | 0 | 0
4783 | 1122.3613 | 99.82 | 323.5669 | 323.5669 | 0 | 0 | 0 | 810.881 | 0 | 0
4784 | 1070.4651 | 317.85 | 1415.6935 | 1112.0041 | -303.6894 | 0 | 0 | 0 | 0 | 0
4785 | 1185.2757 | 538.67 | 2488.2802 | 1231.2703 | -614.9724 | 0 | 642.0374 | 0 | 0 | 0
4786 | 1241.5501 | 520.03 | 2319.8785 | 1289.728 | -119.3493 | 0 | 910.8011 | 0 | 0 | 0
4787 | 1273.3423 | 652.21 | 2864.6412 | 1322.7537 | 0 | 0 | 1541.8875 | 0 | 0 | 0
4788 | 1429.0673 | 929.29 | 4065.7623 | 1484.5216 | 0 | 0 | 2581.2407 | 0 | 0 | 0
4789 | 1265.5332 | 658.53 | 2871.4423 | 1314.6417 | 0 | 0 | 1556.8006 | 0 | 0 | 0
4790 | 1185.2801 | 679.89 | 2971.1873 | 1231.2745 | 0 | 0 | 1739.9128 | 0 | 0 | 0
4791 | 1296.2238 | 669.75 | 2938.8025 | 1346.5236 | 0 | 0 | 1592.2789 | 0 | 0 | 0
4792 | 1491.7106 | 386.56 | 1733.0743 | 1549.5965 | 0 | 0 | 183.4778 | 0 | 0 | 0
4793 | 1623.4698 | 167.8 | 741.8406 | 741.8406 | 0 | 0 | 0 | 909.341 | 0 | 0
4794 | 1365.0331 | 9.79 | 16.1337 | 16.1337 | 0 | 0 | 0 | 1349.502 | 0 | 0
4795 | 1483.589 | 0 | 0 | 0 | 0 | 0 | 0 | 1483.589 | 0 | 0
4796 | 1207.3155 | 0 | 0 | 0 | 0 | 0 | 0 | 1207.315 | 0 | 0
4797 | 1394.4908 | 0 | 0 | 0 | 0 | 0 | 0 | 1394.491 | 0 | 0
4798 | 1198.3366 | 0 | 0 | 0 | 0 | 0 | 0 | 892.463 | 0 | 317.7434
4799 | 1087.8272 | 0 | 0 | 0 | 0 | 0 | 0 | 495.827 | 0 | 614.9724
4800 | 982.8432 | 0 | 0 | 0 | 0 | 0 | 0 | 982.843 | 0 | 0
4801 | 1308.846 | 0 | 0 | 0 | 0 | 0 | 0 | 1308.846 | 0 | 0
4802 | 1232.1801 | 0 | 0 | 0 | 0 | 0 | 0 | 1232.18 | 0 | 0
4803 | 1165.8744 | 0 | 0 | 0 | 0 | 0 | 0 | 1165.874 | 0 | 0
4804 | 1230.108 | 0 | 0 | 0 | 0 | 0 | 0 | 1230.108 | 0 | 0
4805 | 1178.9974 | 0 | 0 | 0 | 0 | 0 | 0 | 1178.997 | 0 | 0
4806 | 1110.6197 | 0 | 0 | 0 | 0 | 0 | 0 | 1110.62 | 0 | 0
4807 | 929.6605 | 39.21 | 147.8676 | 147.8676 | 0 | 0 | 0 | 787.316 | 0 | 0
4808 | 777.6212 | 312.3 | 1385.7157 | 807.7974 | -577.9182 | 0 | 0 | 0 | 0 | 0
4809 | 947.273 | 400.15 | 1803.3328 | 984.0317 | -460.0929 | 0 | 359.2083 | 0 | 0 | 0
4810 | 1179.9083 | 338.99 | 1501.8426 | 1225.694 | 0 | 0 | 276.1486 | 0 | 0 | 0
4811 | 1059.5877 | 594.8 | 2605.3358 | 1100.705 | 0 | 0 | 1504.6308 | 0 | 0 | 0
4812 | 1194.5136 | 552.01 | 2409.517 | 1240.8658 | 0 | 0 | 1168.6512 | 0 | 0 | 0
4813 | 1267.6269 | 696.77 | 3020.4276 | 1316.8169 | 0 | 0 | 1703.6107 | 0 | 0 | 0
4814 | 887.0799 | 662.28 | 2887.6466 | 921.5029 | 0 | 0 | 1966.1437 | 0 | 0 | 0
4815 | 1241.5596 | 609.05 | 2687.0316 | 1289.7374 | 0 | 0 | 1397.2942 | 0 | 0 | 0
4816 | 536.721 | 390.93 | 1753.1575 | 557.5483 | 0 | 0 | 1195.6092 | 0 | 0 | 0
4817 | 511.4393 | 196.5 | 875.2304 | 531.2853 | 0 | 0 | 343.9451 | 0 | 0 | 0
4818 | 220.4508 | 59.13 | 234.7803 | 229.0055 | 0 | 0 | 5.7747 | 0 | 0 | 0
4819 | 219.6375 | 0 | 0 | 0 | 0 | 0 | 0 | 100.855 | 0 | 123.3913
4820 | 234.8325 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243.9456
4821 | 155.4039 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 161.4344
4822 | 212.04 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 220.2682
4823 | 91.1703 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.7078
4824 | 85.6448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.9684
4825 | 78.738 | 0 | 0 | 0 | 0 | 0 | 0 | 78.738 | 0 | 0
4826 | 84.9541 | 0 | 0 | 0 | 0 | 0 | 0 | 84.954 | 0 | 0
4827 | 77.3566 | 0 | 0 | 0 | 0 | 0 | 0 | 77.357 | 0 | 0
4828 | 82.1914 | 0 | 0 | 0 | 0 | 0 | 0 | 82.191 | 0 | 0
4829 | 78.738 | 0 | 0 | 0 | 0 | 0 | 0 | 78.738 | 0 | 0
4830 | 83.5728 | 0 | 0 | 0 | 0 | 0 | 0 | 83.573 | 0 | 0
4831 | 66.9963 | 71.86 | 291.2351 | 69.5968 | -221.6383 | 0 | 0 | 0 | 0 | 0
4832 | 81.1985 | 220.74 | 996.4672 | 84.3489 | -614.9724 | 0 | 297.1459 | 0 | 0 | 0
4833 | 713.0577 | 338.95 | 1528.8754 | 740.727 | -201.4003 | 0 | 586.7481 | 0 | 0 | 0
4834 | 1109.9109 | 596.18 | 2652.216 | 1152.9808 | 0 | 0 | 1499.2352 | 0 | 0 | 0
4835 | 1211.7488 | 745.4 | 3263.8653 | 1258.7696 | 0 | 0 | 2005.0957 | 0 | 0 | 0
4836 | 1105.1884 | 926.97 | 4069.3524 | 1148.0745 | 0 | 0 | 2921.2779 | 0 | 0 | 0
4837 | 969.134 | 733.96 | 3196.5404 | 1006.741 | 0 | 0 | 2189.7994 | 0 | 0 | 0
4838 | 1192.262 | 524.59 | 2305.6438 | 1238.5274 | 0 | 0 | 1067.1163 | 0 | 0 | 0
4839 | 1204.9136 | 546.24 | 2417.0992 | 1251.6704 | 0 | 0 | 1165.4288 | 0 | 0 | 0
4840 | 1193.8661 | 432.42 | 1938.8283 | 1240.1937 | 0 | 0 | 698.6346 | 0 | 0 | 0
4841 | 893.7415 | 163.68 | 722.8149 | 722.8149 | 0 | 0 | 0 | 197.927 | 0 | 0
4842 | 898.8077 | 25.47 | 84.5764 | 84.5764 | 0 | 0 | 0 | 817.391 | 0 | 0
4843 | 882.694 | 0 | 0 | 0 | 0 | 0 | 0 | 882.694 | 0 | 0
4844 | 1020.8308 | 0 | 0 | 0 | 0 | 0 | 0 | 1020.831 | 0 | 0
4845 | 1455.9617 | 0 | 0 | 0 | 0 | 0 | 0 | 1455.962 | 0 | 0
4846 | 774.9473 | 0 | 0 | 0 | 0 | 0 | 0 | 469.074 | 0 | 317.7434
4847 | 1051.2209 | 0 | 0 | 0 | 0 | 0 | 0 | 459.221 | 0 | 614.9724
4848 | 1114.0731 | 0 | 0 | 0 | 0 | 0 | 0 | 1114.073 | 0 | 0
4849 | 966.9575 | 0 | 0 | 0 | 0 | 0 | 0 | 966.957 | 0 | 0
4850 | 895.1263 | 0 | 0 | 0 | 0 | 0 | 0 | 895.126 | 0 | 0
4851 | 941.4022 | 0 | 0 | 0 | 0 | 0 | 0 | 941.402 | 0 | 0
4852 | 939.3301 | 0 | 0 | 0 | 0 | 0 | 0 | 939.33 | 0 | 0
4853 | 1111.3104 | 0 | 0 | 0 | 0 | 0 | 0 | 1111.31 | 0 | 0
4854 | 1126.5055 | 0 | 0 | 0 | 0 | 0 | 0 | 1126.505 | 0 | 0
4855 | 1100.2595 | 97.79 | 333.5914 | 333.5914 | 0 | 0 | 0 | 779.13 | 0 | 0
4856 | 882.8235 | 200.67 | 900.6603 | 900.6603 | 0 | 0 | 0 | 15.807 | 0 | 0
4857 | 886.201 | 348.05 | 1567.4878 | 920.5898 | -614.9724 | 0 | 31.9256 | 0 | 0 | 0
4858 | 1103.5739 | 412.36 | 1831.1572 | 1146.3979 | -423.0387 | 0 | 261.7206 | 0 | 0 | 0
4859 | 1112.4017 | 584.12 | 2566.5988 | 1155.5674 | 0 | 0 | 1411.0313 | 0 | 0 | 0
4860 | 1166.9312 | 595.95 | 2607.2285 | 1212.2135 | 0 | 0 | 1395.0151 | 0 | 0 | 0
4861 | 990.0065 | 750.35 | 3266.6036 | 1028.4229 | 0 | 0 | 2238.1807 | 0 | 0 | 0
4862 | 1284.0444 | 367.96 | 1620.8793 | 1333.871 | 0 | 0 | 287.0082 | 0 | 0 | 0
4863 | 1002.3878 | 274.51 | 1212.5417 | 1041.2854 | 0 | 0 | 171.2563 | 0 | 0 | 0
4864 | 1384.9171 | 204.9 | 907.3201 | 907.3201 | 0 | 0 | 0 | 511.49 | 0 | 0
4865 | 1471.9052 | 79.26 | 331.5148 | 331.5148 | 0 | 0 | 0 | 1152.774 | 0 | 0
4866 | 1181.0885 | 58.08 | 230.7165 | 230.7165 | 0 | 0 | 0 | 958.99 | 0 | 0
4867 | 1185.2136 | 0 | 0 | 0 | 0 | 0 | 0 | 1185.214 | 0 | 0
4868 | 1040.17 | 0 | 0 | 0 | 0 | 0 | 0 | 1040.17 | 0 | 0
4869 | 1251.5192 | 0 | 0 | 0 | 0 | 0 | 0 | 1251.519 | 0 | 0
4870 | 1156.8955 | 0 | 0 | 0 | 0 | 0 | 0 | 851.022 | 0 | 317.7434
4871 | 1042.9327 | 0 | 0 | 0 | 0 | 0 | 0 | 450.933 | 0 | 614.9724
4872 | 1049.8395 | 0 | 0 | 0 | 0 | 0 | 0 | 1049.84 | 0 | 0
4873 | 880.622 | 0 | 0 | 0 | 0 | 0 | 0 | 880.622 | 0 | 0
4874 | 931.0419 | 0 | 0 | 0 | 0 | 0 | 0 | 931.042 | 0 | 0
4875 | 782.5449 | 0 | 0 | 0 | 0 | 0 | 0 | 782.545 | 0 | 0
4876 | 743.1759 | 0 | 0 | 0 | 0 | 0 | 0 | 743.176 | 0 | 0
4877 | 860.5921 | 0 | 0 | 0 | 0 | 0 | 0 | 860.592 | 0 | 0
4878 | 848.8505 | 0 | 0 | 0 | 0 | 0 | 0 | 848.851 | 0 | 0
4879 | 506.2713 | 72.38 | 291.7494 | 291.7494 | 0 | 0 | 0 | 225.42 | 0 | 0
4880 | 90.0212 | 196.43 | 882.7472 | 93.5142 | -614.9724 | 0 | 174.2605 | 0 | 0 | 0
4881 | 76.9871 | 441.29 | 2003.0721 | 79.9755 | -423.0387 | 0 | 1500.0579 | 0 | 0 | 0
4882 | 90.8526 | 572.73 | 2557.1779 | 94.3775 | 0 | 0 | 2462.8004 | 0 | 0 | 0
4883 | 77.379 | 688.37 | 3033.1603 | 80.3817 | 0 | 0 | 2952.7786 | 0 | 0 | 0
4884 | 103.2926 | 750.7 | 3283.4883 | 107.3013 | 0 | 0 | 3176.1871 | 0 | 0 | 0
4885 | 71.5652 | 710.93 | 3110.7642 | 74.3421 | 0 | 0 | 3036.4221 | 0 | 0 | 0
4886 | 75.749 | 649.69 | 2862.1221 | 78.6884 | 0 | 0 | 2783.4337 | 0 | 0 | 0
4887 | 91.6762 | 600.16 | 2674.7134 | 95.2345 | 0 | 0 | 2579.4789 | 0 | 0 | 0
4888 | 85.3392 | 398.12 | 1798.0152 | 88.6506 | 0 | 0 | 1709.3646 | 0 | 0 | 0
4889 | 76.2014 | 267.55 | 1205.4508 | 79.159 | 0 | 0 | 1126.2918 | 0 | 0 | 0
4890 | 81.8383 | 88.51 | 347.6963 | 85.0147 | 0 | 0 | 262.6815 | 0 | 0 | 0
4891 | 78.0473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.0756
4892 | 82.8821 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.0982
4893 | 75.2845 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.2064
4894 | 79.4286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.5112
4895 | 75.9752 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 78.9232
4896 | 78.738 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.7934
4897 | 74.5939 | 0 | 0 | 0 | 0 | 0 | 0 | 31.096 | 0 | 45.1859
4898 | 80.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9458
4899 | 74.5939 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 77.4886
4900 | 77.3566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.3588
4901 | 71.8311 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 74.6184
4902 | 79.4286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.5112
4903 | 66.3057 | 42.13 | 160.8257 | 68.879 | -91.9467 | 0 | 0 | 0 | 0 | 0
4904 | 72.9207 | 129.94 | 569.5652 | 75.7496 | -493.8156 | 0 | 0 | 0 | 0 | 0
4905 | 154.285 | 362.47 | 1636.1497 | 160.272 | -452.2499 | 0 | 1023.6278 | 0 | 0 | 0
4906 | 105.3492 | 576.18 | 2568.9236 | 109.437 | 0 | 0 | 2459.4866 | 0 | 0 | 0
4907 | 130.5488 | 663.59 | 2926.5488 | 135.6149 | 0 | 0 | 2790.9339 | 0 | 0 | 0
4908 | 202.7269 | 625.23 | 2750.4714 | 210.5938 | 0 | 0 | 2539.8776 | 0 | 0 | 0
4909 | 354.6912 | 464.85 | 2052.2523 | 368.4547 | 0 | 0 | 1683.7976 | 0 | 0 | 0
4910 | 688.6006 | 549.88 | 2437.9813 | 715.3209 | 0 | 0 | 1722.6603 | 0 | 0 | 0
4911 | 987.823 | 458.34 | 2050.076 | 1026.1552 | 0 | 0 | 1023.9208 | 0 | 0 | 0
4912 | 1032.5448 | 412.68 | 1871.3257 | 1072.6126 | 0 | 0 | 798.7131 | 0 | 0 | 0
4913 | 1329.4033 | 191.54 | 859.0261 | 859.0261 | 0 | 0 | 0 | 502.466 | 0 | 0
4914 | 1196.1437 | 18.61 | 54.5217 | 54.5217 | 0 | 0 | 0 | 1143.659 | 0 | 0
4915 | 1400.707 | 0 | 0 | 0 | 0 | 0 | 0 | 1400.707 | 0 | 0
4916 | 823.2952 | 0 | 0 | 0 | 0 | 0 | 0 | 823.295 | 0 | 0
4917 | 1177.6161 | 0 | 0 | 0 | 0 | 0 | 0 | 1177.616 | 0 | 0
4918 | 1352.3591 | 0 | 0 | 0 | 0 | 0 | 0 | 1046.485 | 0 | 317.7434
4919 | 1335.092 | 0 | 0 | 0 | 0 | 0 | 0 | 743.092 | 0 | 614.9724
4920 | 1360.6473 | 0 | 0 | 0 | 0 | 0 | 0 | 1360.647 | 0 | 0
4921 | 1288.1255 | 0 | 0 | 0 | 0 | 0 | 0 | 1288.125 | 0 | 0
4922 | 1518.8139 | 0 | 0 | 0 | 0 | 0 | 0 | 1518.814 | 0 | 0
4923 | 1469.7754 | 0 | 0 | 0 | 0 | 0 | 0 | 1469.775 | 0 | 0
4924 | 1038.0979 | 0 | 0 | 0 | 0 | 0 | 0 | 1038.098 | 0 | 0
4925 | 1302.6298 | 0 | 0 | 0 | 0 | 0 | 0 | 1302.63 | 0 | 0
4926 | 1125.8148 | 0 | 0 | 0 | 0 | 0 | 0 | 1125.815 | 0 | 0
4927 | 1215.6037 | 6.85 | 4.0804 | 4.0804 | 0 | 0 | 0 | 1211.675 | 0 | 0
4928 | 1164.5561 | 17.63 | 51.0676 | 51.0676 | 0 | 0 | 0 | 1115.396 | 0 | 0
4929 | 1265.2017 | 138.91 | 605.2274 | 605.2274 | 0 | 0 | 0 | 682.583 | 0 | 0
4930 | 1521.9772 | 485.18 | 2167.2386 | 1581.0369 | -586.2017 | 0 | 0 | 0 | 0 | 0
4931 | 1459.9884 | 750.17 | 3298.5572 | 1516.6435 | -451.8094 | 0 | 1330.1043 | 0 | 0 | 0
4932 | 1450.6684 | 807.57 | 3524.8567 | 1506.9618 | 0 | 0 | 2017.8948 | 0 | 0 | 0
4933 | 1401.7369 | 755.13 | 3302.7498 | 1456.1311 | 0 | 0 | 1846.6188 | 0 | 0 | 0
4934 | 1375.3968 | 845.43 | 3754.4315 | 1428.7679 | 0 | 0 | 2325.6636 | 0 | 0 | 0
4935 | 1381.8306 | 709.37 | 3193.9922 | 1435.4526 | 0 | 0 | 1758.5396 | 0 | 0 | 0
4936 | 1788.7211 | 435.37 | 1966.0502 | 1858.1319 | 0 | 0 | 107.9183 | 0 | 0 | 0
4937 | 1525.3581 | 303.27 | 1345.329 | 1345.329 | 0 | 0 | 0 | 230.285 | 0 | 0
4938 | 1702.6602 | 95.1 | 336.6839 | 336.6839 | 0 | 0 | 0 | 1378.553 | 0 | 0
4939 | 1469.7754 | 0 | 0 | 0 | 0 | 0 | 0 | 1469.775 | 0 | 0
4940 | 1623.7979 | 0 | 0 | 0 | 0 | 0 | 0 | 1623.798 | 0 | 0
4941 | 1571.3059 | 0 | 0 | 0 | 0 | 0 | 0 | 1571.306 | 0 | 0
4942 | 1333.0199 | 0 | 0 | 0 | 0 | 0 | 0 | 1027.146 | 0 | 317.7434
4943 | 1336.4734 | 0 | 0 | 0 | 0 | 0 | 0 | 744.473 | 0 | 614.9724
4944 | 1509.1443 | 0 | 0 | 0 | 0 | 0 | 0 | 1509.144 | 0 | 0
4945 | 1440.7666 | 0 | 0 | 0 | 0 | 0 | 0 | 1440.767 | 0 | 0
4946 | 1415.902 | 0 | 0 | 0 | 0 | 0 | 0 | 1415.902 | 0 | 0
4947 | 1212.8409 | 0 | 0 | 0 | 0 | 0 | 0 | 1212.841 | 0 | 0
4948 | 1147.9167 | 0 | 0 | 0 | 0 | 0 | 0 | 1147.917 | 0 | 0
4949 | 1229.4174 | 0 | 0 | 0 | 0 | 0 | 0 | 1229.417 | 0 | 0
4950 | 988.3687 | 0 | 0 | 0 | 0 | 0 | 0 | 988.369 | 0 | 0
4951 | 1297.7951 | 98.75 | 323.3238 | 323.3238 | 0 | 0 | 0 | 986.549 | 0 | 0
4952 | 1047.8219 | 319.17 | 1413.4933 | 1088.4825 | -325.0108 | 0 | 0 | 0 | 0 | 0
4953 | 1384.7712 | 543.83 | 2481.6858 | 1438.5067 | -614.9724 | 0 | 428.2067 | 0 | 0 | 0
4954 | 1349.7673 | 733.06 | 3258.9393 | 1402.1444 | -98.0278 | 0 | 1758.7671 | 0 | 0 | 0
4955 | 1301.2096 | 865.37 | 3776.2609 | 1351.7031 | 0 | 0 | 2424.5578 | 0 | 0 | 0
4956 | 1364.7042 | 933.3 | 4047.3526 | 1417.661 | 0 | 0 | 2629.6916 | 0 | 0 | 0
4957 | 1493.1455 | 932.37 | 4050.1377 | 1551.0861 | 0 | 0 | 2499.0515 | 0 | 0 | 0
4958 | 1284.4951 | 847.15 | 3717.8479 | 1334.3395 | 0 | 0 | 2383.5084 | 0 | 0 | 0
4959 | 1168.1969 | 710.99 | 3174.606 | 1213.5286 | 0 | 0 | 1961.0774 | 0 | 0 | 0
4960 | 1479.6564 | 523.31 | 2382.7324 | 1537.0737 | 0 | 0 | 845.6587 | 0 | 0 | 0
4961 | 1510.8356 | 188.46 | 837.0024 | 837.0024 | 0 | 0 | 0 | 705.1 | 0 | 0
4962 | 1394.1765 | 92.01 | 354.5389 | 354.5389 | 0 | 0 | 0 | 1052.882 | 0 | 0
4963 | 1384.1314 | 0 | 0 | 0 | 0 | 0 | 0 | 1384.131 | 0 | 0
4964 | 1029.119 | 0 | 0 | 0 | 0 | 0 | 0 | 1029.119 | 0 | 0
4965 | 1141.7005 | 0 | 0 | 0 | 0 | 0 | 0 | 1141.7 | 0 | 0
4966 | 1211.4596 | 0 | 0 | 0 | 0 | 0 | 0 | 905.586 | 0 | 317.7434
4967 | 1361.338 | 0 | 0 | 0 | 0 | 0 | 0 | 769.338 | 0 | 614.9724
4968 | 1071.2507 | 0 | 0 | 0 | 0 | 0 | 0 | 1071.251 | 0 | 0
4969 | 1274.3118 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.312 | 0 | 0
4970 | 875.7872 | 0 | 0 | 0 | 0 | 0 | 0 | 875.787 | 0 | 0
4971 | 1036.7165 | 0 | 0 | 0 | 0 | 0 | 0 | 1036.717 | 0 | 0
4972 | 911.7028 | 0 | 0 | 0 | 0 | 0 | 0 | 911.703 | 0 | 0
4973 | 1306.0833 | 0 | 0 | 0 | 0 | 0 | 0 | 1306.083 | 0 | 0
4974 | 1031.1911 | 0 | 0 | 0 | 0 | 0 | 0 | 1031.191 | 0 | 0
4975 | 1167.9465 | 34.3 | 125.3297 | 125.3297 | 0 | 0 | 0 | 1047.299 | 0 | 0
4976 | 1102.0699 | 108 | 466.8337 | 466.8337 | 0 | 0 | 0 | 652.675 | 0 | 0
4977 | 1017.1236 | 280.13 | 1253.0935 | 1056.5922 | -196.5013 | 0 | 0 | 0 | 0 | 0
4978 | 1192.6799 | 333.51 | 1474.6207 | 1238.9616 | -235.6591 | 0 | 0 | 0 | 0 | 0
4979 | 1048.5359 | 687.02 | 2991.4429 | 1089.2231 | -605.8517 | 0 | 1296.3681 | 0 | 0 | 0
4980 | 1037.4685 | 750.19 | 3242.8357 | 1077.7277 | 0 | 0 | 2165.108 | 0 | 0 | 0
4981 | 1077.8269 | 717.87 | 3109.3151 | 1119.6518 | 0 | 0 | 1989.6632 | 0 | 0 | 0
4982 | 1076.3005 | 715.23 | 3114.3418 | 1118.0656 | 0 | 0 | 1996.2763 | 0 | 0 | 0
4983 | 852.6441 | 276.8 | 1217.7815 | 885.7306 | 0 | 0 | 332.0508 | 0 | 0 | 0
4984 | 422.9472 | 303.69 | 1354.7437 | 439.3594 | 0 | 0 | 915.3844 | 0 | 0 | 0
4985 | 167.4831 | 91.7 | 387.8751 | 173.9821 | 0 | 0 | 213.893 | 0 | 0 | 0
4986 | 147.3263 | 71.04 | 283.1979 | 153.0429 | 0 | 0 | 130.155 | 0 | 0 | 0
4987 | 102.2212 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.1877
4988 | 109.8187 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.0805
4989 | 87.0262 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.403
4990 | 81.5007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.6636
4991 | 81.5007 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.6636
4992 | 85.6448 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.9684
4993 | 80.1193 | 0 | 0 | 0 | 0 | 0 | 0 | 80.119 | 0 | 0
4994 | 78.738 | 0 | 0 | 0 | 0 | 0 | 0 | 41.456 | 0 | 38.7287
4995 | 73.9032 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76.7708
4996 | 80.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9458
4997 | 77.3566 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.3588
4998 | 80.81 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83.9458
4999 | 70.4498 | 37.24 | 139.2331 | 73.1838 | -66.0493 | 0 | 0 | 0 | 0 | 0
5000 | 82.0705 | 116.12 | 506.0724 | 85.2547 | -420.8177 | 0 | 0 | 0 | 0 | 0
5001 | 531.2024 | 368.2 | 1654.0452 | 551.8152 | -551.1441 | 0 | 551.0859 | 0 | 0 | 0
5002 | 1284.5469 | 509.29 | 2257.4443 | 1334.3925 | 0 | 0 | 923.0518 | 0 | 0 | 0
5003 | 1356.1138 | 367.36 | 1618.4609 | 1408.7377 | 0 | 0 | 209.7233 | 0 | 0 | 0
5004 | 1186.715 | 624.2 | 2727.1409 | 1232.7652 | 0 | 0 | 1494.3757 | 0 | 0 | 0
5005 | 1505.9819 | 459.35 | 2016.1652 | 1564.4213 | 0 | 0 | 451.744 | 0 | 0 | 0
5006 | 1112.084 | 119.23 | 500.4608 | 500.4608 | 0 | 0 | 0 | 630.318 | 0 | 0
5007 | 1330.2779 | 79.42 | 322.632 | 322.632 | 0 | 0 | 0 | 1019.698 | 0 | 0
5008 | 1190.5629 | 225.5 | 1000.6193 | 1000.6193 | 0 | 0 | 0 | 227.322 | 0 | 0
5009 | 1041.9355 | 87.83 | 370.8793 | 370.8793 | 0 | 0 | 0 | 684.911 | 0 | 0
5010 | 1168.6743 | 48.75 | 189.5258 | 189.5258 | 0 | 0 | 0 | 986.228 | 0 | 0
5011 | 1443.5337 | 0 | 0 | 0 | 0 | 0 | 0 | 1443.534 | 0 | 0
5012 | 1038.0979 | 0 | 0 | 0 | 0 | 0 | 0 | 1038.098 | 0 | 0
5013 | 1286.7441 | 0 | 0 | 0 | 0 | 0 | 0 | 1286.744 | 0 | 0
5014 | 712.7858 | 0 | 0 | 0 | 0 | 0 | 0 | 406.912 | 0 | 317.7434
5015 | 1145.8446 | 0 | 0 | 0 | 0 | 0 | 0 | 553.845 | 0 | 614.9724
5016 | 1181.7602 | 0 | 0 | 0 | 0 | 0 | 0 | 1181.76 | 0 | 0
5017 | 911.7028 | 0 | 0 | 0 | 0 | 0 | 0 | 911.703 | 0 | 0
5018 | 1009.0892 | 0 | 0 | 0 | 0 | 0 | 0 | 1009.089 | 0 | 0
5019 | 973.8643 | 0 | 0 | 0 | 0 | 0 | 0 | 973.864 | 0 | 0
5020 | 848.1598 | 0 | 0 | 0 | 0 | 0 | 0 | 848.16 | 0 | 0
5021 | 780.4728 | 0 | 0 | 0 | 0 | 0 | 0 | 780.473 | 0 | 0
5022 | 770.8032 | 0 | 0 | 0 | 0 | 0 | 0 | 770.803 | 0 | 0
5023 | 969.0295 | 46.87 | 183.2753 | 183.2753 | 0 | 0 | 0 | 792.601 | 0 | 0
5024 | 708.5433 | 158.44 | 707.7938 | 707.7938 | 0 | 0 | 0 | 27.19 | 0 | 0
5025 | 1101.8299 | 441.37 | 2011.4397 | 1144.5862 | -614.9724 | 0 | 251.8811 | 0 | 0 | 0
5026 | 952.1242 | 573.48 | 2574.9321 | 989.0709 | -423.0387 | 0 | 1162.8225 | 0 | 0 | 0
5027 | 1203.6531 | 717.55 | 3182.4833 | 1250.3605 | 0 | 0 | 1932.1228 | 0 | 0 | 0
5028 | 1159.54 | 742.37 | 3275.9061 | 1204.5357 | 0 | 0 | 2071.3704 | 0 | 0 | 0
5029 | 964.4063 | 671.6 | 2967.8704 | 1001.8306 | 0 | 0 | 1966.0398 | 0 | 0 | 0
5030 | 1140.2509 | 243.02 | 1069.0319 | 1069.0319 | 0 | 0 | 0 | 0 | 0 | 115.4652
5031 | 833.8618 | 511.18 | 2289.2795 | 866.2188 | -128.5012 | 0 | 1294.5595 | 0 | 0 | 0
5032 | 1036.9885 | 541.06 | 2496.7194 | 1077.2291 | 0 | 0 | 1419.4903 | 0 | 0 | 0
5033 | 1019.831 | 233.16 | 1051.3556 | 1051.3556 | 0 | 0 | 0 | 7.749 | 0 | 0
5034 | 933.7278 | 86.59 | 340.4693 | 340.4693 | 0 | 0 | 0 | 605.977 | 0 | 0
5035 | 870.2617 | 0 | 0 | 0 | 0 | 0 | 0 | 870.262 | 0 | 0
5036 | 1061.5812 | 0 | 0 | 0 | 0 | 0 | 0 | 1061.581 | 0 | 0
5037 | 730.0529 | 0 | 0 | 0 | 0 | 0 | 0 | 730.053 | 0 | 0
5038 | 1020.8308 | 0 | 0 | 0 | 0 | 0 | 0 | 714.957 | 0 | 317.7434
5039 | 954.5252 | 0 | 0 | 0 | 0 | 0 | 0 | 362.525 | 0 | 614.9724
5040 | 756.9896 | 0 | 0 | 0 | 0 | 0 | 0 | 756.99 | 0 | 0
5041 | 995.2755 | 0 | 0 | 0 | 0 | 0 | 0 | 995.276 | 0 | 0
5042 | 975.9364 | 0 | 0 | 0 | 0 | 0 | 0 | 975.936 | 0 | 0
5043 | 974.555 | 0 | 0 | 0 | 0 | 0 | 0 | 974.555 | 0 | 0
5044 | 919.3003 | 0 | 0 | 0 | 0 | 0 | 0 | 919.3 | 0 | 0
5045 | 1018.0681 | 0 | 0 | 0 | 0 | 0 | 0 | 1018.068 | 0 | 0
5046 | 664.4379 | 0 | 0 | 0 | 0 | 0 | 0 | 664.438 | 0 | 0
5047 | 891.6729 | 58.4 | 234.3003 | 234.3003 | 0 | 0 | 0 | 666.124 | 0 | 0
5048 | 882.8417 | 195.94 | 882.3389 | 882.3389 | 0 | 0 | 0 | 33.462 | 0 | 0
5049 | 1164.6709 | 546.64 | 2528.6367 | 1209.8647 | -614.9724 | 0 | 703.7996 | 0 | 0 | 0
5050 | 1275.9643 | 738.34 | 3342.7999 | 1325.4785 | -423.0387 | 0 | 1594.2827 | 0 | 0 | 0
5051 | 1281.6469 | 446.69 | 1975.039 | 1331.38 | 0 | 0 | 643.659 | 0 | 0 | 0
5052 | 1165.2105 | 941.41 | 4149.2739 | 1210.4257 | 0 | 0 | 2938.8482 | 0 | 0 | 0
5053 | 1262.2861 | 490.79 | 2157.5985 | 1311.2687 | 0 | 0 | 846.3298 | 0 | 0 | 0
5054 | 1118.1698 | 580.28 | 2554.2505 | 1161.5603 | 0 | 0 | 1392.6902 | 0 | 0 | 0
5055 | 1150.1519 | 593.1 | 2632.085 | 1194.7834 | 0 | 0 | 1437.3017 | 0 | 0 | 0
5056 | 1238.5577 | 374.02 | 1683.2366 | 1286.6199 | 0 | 0 | 396.6167 | 0 | 0 | 0
5057 | 954.5088 | 129.05 | 564.0949 | 564.0949 | 0 | 0 | 0 | 411.486 | 0 | 0
5058 | 1051.3962 | 42.1 | 159.5178 | 159.5178 | 0 | 0 | 0 | 897.837 | 0 | 0
5059 | 866.1271 | 0 | 0 | 0 | 0 | 0 | 0 | 866.127 | 0 | 0
5060 | 1031.8818 | 0 | 0 | 0 | 0 | 0 | 0 | 1031.882 | 0 | 0
5061 | 910.3214 | 0 | 0 | 0 | 0 | 0 | 0 | 910.321 | 0 | 0
5062 | 1085.7551 | 0 | 0 | 0 | 0 | 0 | 0 | 779.881 | 0 | 317.7434
5063 | 1110.6197 | 0 | 0 | 0 | 0 | 0 | 0 | 518.62 | 0 | 614.9724
5064 | 991.1314 | 0 | 0 | 0 | 0 | 0 | 0 | 991.131 | 0 | 0
5065 | 1030.5004 | 0 | 0 | 0 | 0 | 0 | 0 | 1030.5 | 0 | 0
5066 | 809.4815 | 0 | 0 | 0 | 0 | 0 | 0 | 809.482 | 0 | 0
5067 | 1055.365 | 0 | 0 | 0 | 0 | 0 | 0 | 1055.365 | 0 | 0
5068 | 926.8978 | 0 | 0 | 0 | 0 | 0 | 0 | 926.898 | 0 | 0
5069 | 813.6256 | 0 | 0 | 0 | 0 | 0 | 0 | 813.626 | 0 | 0
5070 | 907.5587 | 0 | 0 | 0 | 0 | 0 | 0 | 907.559 | 0 | 0
5071 | 821.2232 | 80 | 319.6226 | 319.6226 | 0 | 0 | 0 | 513.541 | 0 | 0
5072 | 962.443 | 257.14 | 1163.077 | 999.7904 | -163.2866 | 0 | 0 | 0 | 0 | 0
5073 | 1008.2725 | 538.38 | 2480.1006 | 1047.3977 | -614.9724 | 0 | 817.7305 | 0 | 0 | 0
5074 | 1436.7719 | 730.72 | 3299.0714 | 1492.5256 | -259.7521 | 0 | 1546.7938 | 0 | 0 | 0
5075 | 1155.7145 | 864.71 | 3843.1891 | 1200.5612 | 0 | 0 | 2642.6279 | 0 | 0 | 0
5076 | 1137.1705 | 75.73 | 301.0404 | 301.0404 | 0 | 0 | 0 | 255.376 | 0 | 614.9724
5077 | 1170.2102 | 365.14 | 1604.5451 | 1215.6197 | -388.9254 | 0 | 0 | 0 | 0 | 0
5078 | 1059.333 | 729.51 | 3214.8503 | 1100.4402 | -295.4724 | 0 | 1818.9378 | 0 | 0 | 0
5079 | 1086.2248 | 553.92 | 2471.0225 | 1128.3746 | 0 | 0 | 1342.6479 | 0 | 0 | 0
5080 | 1050.3472 | 67.64 | 273.0966 | 273.0966 | 0 | 0 | 0 | 787.452 | 0 | 0
5081 | 1100.0177 | 115.16 | 499.6152 | 499.6152 | 0 | 0 | 0 | 619.066 | 0 | 0
5082 | 961.4501 | 67.58 | 269.8908 | 269.8908 | 0 | 0 | 0 | 701.641 | 0 | 0
5083 | 1004.2544 | 0 | 0 | 0 | 0 | 0 | 0 | 1004.254 | 0 | 0
5084 | 918.6096 | 0 | 0 | 0 | 0 | 0 | 0 | 918.61 | 0 | 0
5085 | 1251.5192 | 0 | 0 | 0 | 0 | 0 | 0 | 1251.519 | 0 | 0
5086 | 1076.0855 | 0 | 0 | 0 | 0 | 0 | 0 | 770.212 | 0 | 317.7434
5087 | 1287.4348 | 0 | 0 | 0 | 0 | 0 | 0 | 695.435 | 0 | 614.9724
5088 | 1154.1328 | 0 | 0 | 0 | 0 | 0 | 0 | 1154.133 | 0 | 0
5089 | 1704.5439 | 0 | 0 | 0 | 0 | 0 | 0 | 1704.544 | 0 | 0
5090 | 1118.0342 | 0 | 0 | 0 | 0 | 0 | 0 | 1118.034 | 0 | 0
5091 | 1386.5855 | 0 | 0 | 0 | 0 | 0 | 0 | 1386.586 | 0 | 0
5092 | 1257.4896 | 0 | 0 | 0 | 0 | 0 | 0 | 1257.49 | 0 | 0
5093 | 1113.2529 | 0 | 0 | 0 | 0 | 0 | 0 | 1113.253 | 0 | 0
5094 | 1508.5094 | 0 | 0 | 0 | 0 | 0 | 0 | 1508.509 | 0 | 0
5095 | 1345.1473 | 41.16 | 156.7089 | 156.7089 | 0 | 0 | 0 | 1194.292 | 0 | 0
5096 | 1347.8468 | 208.34 | 942.3663 | 942.3663 | 0 | 0 | 0 | 440.683 | 0 | 0
5097 | 1439.8057 | 394.94 | 1795.9282 | 1495.6773 | -300.2509 | 0 | 0 | 0 | 0 | 0
5098 | 1331.5524 | 512.84 | 2296.9916 | 1383.2225 | -614.9724 | 0 | 298.7966 | 0 | 0 | 0
5099 | 1361.5313 | 571.36 | 2528.7967 | 1414.3649 | -122.7878 | 0 | 991.6441 | 0 | 0 | 0
5100 | 1417.9132 | 757.82 | 3313.7092 | 1472.9358 | 0 | 0 | 1840.7734 | 0 | 0 | 0
5101 | 1620.5808 | 790.48 | 3449.4945 | 1683.4672 | 0 | 0 | 1766.0273 | 0 | 0 | 0
5102 | 1546.263 | 706.79 | 3105.3759 | 1606.2653 | 0 | 0 | 1499.1106 | 0 | 0 | 0
5103 | 1367.5967 | 563.35 | 2506.3595 | 1420.6663 | 0 | 0 | 1085.6933 | 0 | 0 | 0
5104 | 1582.1499 | 343.02 | 1542.3944 | 1542.3944 | 0 | 0 | 0 | 97.371 | 0 | 0
5105 | 1603.4885 | 133.9 | 587.4732 | 587.4732 | 0 | 0 | 0 | 1037.961 | 0 | 0
5106 | 1628.2678 | 62.77 | 249.8253 | 249.8253 | 0 | 0 | 0 | 1387.775 | 0 | 0
5107 | 1753.1561 | 0 | 0 | 0 | 0 | 0 | 0 | 1753.156 | 0 | 0
5108 | 1494.1654 | 0 | 0 | 0 | 0 | 0 | 0 | 1494.165 | 0 | 0
5109 | 1494.1654 | 0 | 0 | 0 | 0 | 0 | 0 | 1494.165 | 0 | 0
5110 | 1460.6961 | 0 | 0 | 0 | 0 | 0 | 0 | 1154.822 | 0 | 317.7434
5111 | 1675.8559 | 0 | 0 | 0 | 0 | 0 | 0 | 1083.856 | 0 | 614.9724
5112 | 1392.1637 | 0 | 0 | 0 | 0 | 0 | 0 | 1392.164 | 0 | 0
5113 | 1467.0712 | 0 | 0 | 0 | 0 | 0 | 0 | 1467.071 | 0 | 0
5114 | 1345.1473 | 0 | 0 | 0 | 0 | 0 | 0 | 1345.147 | 0 | 0
5115 | 1282.1932 | 0 | 0 | 0 | 0 | 0 | 0 | 1282.193 | 0 | 0
5116 | 1174.6132 | 0 | 0 | 0 | 0 | 0 | 0 | 1174.613 | 0 | 0
5117 | 1106.8777 | 0 | 0 | 0 | 0 | 0 | 0 | 1106.878 | 0 | 0
5118 | 1184.9728 | 0 | 0 | 0 | 0 | 0 | 0 | 1184.973 | 0 | 0
5119 | 1051.8925 | 74.92 | 301.0581 | 301.0581 | 0 | 0 | 0 | 762.08 | 0 | 0
5120 | 1003.1398 | 237.13 | 1074.9344 | 1042.0666 | -32.8678 | 0 | 0 | 0 | 0 | 0
5121 | 1520.4757 | 270.6 | 1218.9875 | 1218.9875 | 0 | 0 | 0 | 318.593 | 0 | 29.5343
5122 | 1744.6384 | 451.91 | 2026.9054 | 1812.3393 | -214.5662 | 0 | 0 | 0 | 0 | 0
5123 | 1595.175 | 645.35 | 2862.7901 | 1657.0754 | -614.9724 | 0 | 590.7423 | 0 | 0 | 0
5124 | 1462.4025 | 703.61 | 3103.6494 | 1519.1501 | -208.4725 | 0 | 1376.0267 | 0 | 0 | 0
5125 | 1607.6891 | 727.57 | 3204.7968 | 1670.075 | 0 | 0 | 1534.7218 | 0 | 0 | 0
5126 | 1637.0923 | 609.12 | 2702.1722 | 1700.62 | 0 | 0 | 1001.5522 | 0 | 0 | 0
5127 | 1664.4276 | 404.93 | 1813.2919 | 1729.0157 | 0 | 0 | 84.2762 | 0 | 0 | 0
5128 | 1619.2759 | 157.28 | 692.033 | 692.033 | 0 | 0 | 0 | 953.094 | 0 | 0
5129 | 1609.6674 | 164.04 | 732.5786 | 732.5786 | 0 | 0 | 0 | 904.454 | 0 | 0
5130 | 1842.5401 | 65.25 | 260.9259 | 260.9259 | 0 | 0 | 0 | 1591.361 | 0 | 0
5131 | 1522.0625 | 0 | 0 | 0 | 0 | 0 | 0 | 1522.062 | 0 | 0
5132 | 1333.194 | 0 | 0 | 0 | 0 | 0 | 0 | 1333.194 | 0 | 0
5133 | 1353.1162 | 0 | 0 | 0 | 0 | 0 | 0 | 1353.116 | 0 | 0
5134 | 1412.8828 | 0 | 0 | 0 | 0 | 0 | 0 | 1107.009 | 0 | 317.7434
5135 | 1341.9598 | 0 | 0 | 0 | 0 | 0 | 0 | 749.96 | 0 | 614.9724
5136 | 1469.4619 | 0 | 0 | 0 | 0 | 0 | 0 | 1469.462 | 0 | 0
5137 | 1242.3487 | 0 | 0 | 0 | 0 | 0 | 0 | 1242.349 | 0 | 0
5138 | 1430.4144 | 0 | 0 | 0 | 0 | 0 | 0 | 1430.414 | 0 | 0
5139 | 1263.8647 | 0 | 0 | 0 | 0 | 0 | 0 | 1263.865 | 0 | 0
5140 | 1263.8647 | 0 | 0 | 0 | 0 | 0 | 0 | 1263.865 | 0 | 0
5141 | 1340.366 | 0 | 0 | 0 | 0 | 0 | 0 | 1340.366 | 0 | 0
5142 | 1114.0497 | 0 | 0 | 0 | 0 | 0 | 0 | 1114.05 | 0 | 0
5143 | 1307.6936 | 47.82 | 187.2259 | 187.2259 | 0 | 0 | 0 | 1127.462 | 0 | 0
5144 | 1075.8529 | 154.39 | 686.7985 | 686.7985 | 0 | 0 | 0 | 414.71 | 0 | 0
5145 | 1014.0104 | 334.3 | 1508.5606 | 1053.3584 | -455.2022 | 0 | 0 | 0 | 0 | 0
5146 | 1160.599 | 502.89 | 2242.9612 | 1205.6358 | -582.8089 | 0 | 454.5166 | 0 | 0 | 0
5147 | 1335.6922 | 593.48 | 2614.71 | 1387.5242 | 0 | 0 | 1227.1858 | 0 | 0 | 0
5148 | 1416.1869 | 727.01 | 3171.2995 | 1471.1418 | 0 | 0 | 1700.1577 | 0 | 0 | 0
5149 | 1072.5339 | 668.25 | 2922.3084 | 1114.1534 | 0 | 0 | 1808.155 | 0 | 0 | 0
5150 | 1228.6313 | 130.93 | 555.3242 | 555.3242 | 0 | 0 | 0 | 694.051 | 0 | 0
5151 | 962.4338 | 52.03 | 199.7632 | 199.7632 | 0 | 0 | 0 | 770.133 | 0 | 0
5152 | 1200.7083 | 76.88 | 317.3102 | 317.3102 | 0 | 0 | 0 | 895.252 | 0 | 0
5153 | 1232.7184 | 138.16 | 608.8819 | 608.8819 | 0 | 0 | 0 | 646.581 | 0 | 0
5154 | 856.2803 | 45.89 | 176.9053 | 176.9053 | 0 | 0 | 0 | 685.983 | 0 | 0
5155 | 1170.6288 | 0 | 0 | 0 | 0 | 0 | 0 | 1170.629 | 0 | 0
5156 | 1184.9728 | 0 | 0 | 0 | 0 | 0 | 0 | 1184.973 | 0 | 0
5157 | 1341.1629 | 0 | 0 | 0 | 0 | 0 | 0 | 1341.163 | 0 | 0
5158 | 1157.0817 | 0 | 0 | 0 | 0 | 0 | 0 | 987.476 | 0 | 176.1875
5159 | 1082.1742 | 0 | 0 | 0 | 0 | 0 | 0 | 490.174 | 0 | 614.9724
5160 | 136.2679 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 141.5558
5161 | 105.9861 | 0 | 0 | 0 | 0 | 0 | 0 | 105.986 | 0 | 0
5162 | 87.6577 | 0 | 0 | 0 | 0 | 0 | 0 | 87.658 | 0 | 0
5163 | 91.6421 | 0 | 0 | 0 | 0 | 0 | 0 | 91.642 | 0 | 0
5164 | 87.6577 | 0 | 0 | 0 | 0 | 0 | 0 | 87.658 | 0 | 0
5165 | 91.6421 | 0 | 0 | 0 | 0 | 0 | 0 | 91.642 | 0 | 0
5166 | 84.4702 | 0 | 0 | 0 | 0 | 0 | 0 | 84.47 | 0 | 0
5167 | 82.0795 | 80.53 | 320.5388 | 85.2641 | -235.2747 | 0 | 0 | 0 | 0 | 0
5168 | 81.0455 | 257.82 | 1161.5395 | 84.191 | -614.9724 | 0 | 462.3761 | 0 | 0 | 0
5169 | 801.8299 | 342.58 | 1535.209 | 832.9438 | -187.765 | 0 | 514.5003 | 0 | 0 | 0
5170 | 967.4233 | 509.29 | 2241.8674 | 1004.9636 | 0 | 0 | 1236.9038 | 0 | 0 | 0
5171 | 1373.2187 | 573.92 | 2494.3125 | 1426.5064 | 0 | 0 | 1067.8061 | 0 | 0 | 0
5172 | 1296.8011 | 713.9 | 3058.5788 | 1347.123 | 0 | 0 | 1711.4558 | 0 | 0 | 0
5173 | 1405.7098 | 651.13 | 2793.7563 | 1460.2582 | 0 | 0 | 1333.4981 | 0 | 0 | 0
5174 | 1424.881 | 509.1 | 2203.6394 | 1480.1731 | 0 | 0 | 723.4662 | 0 | 0 | 0
5175 | 1143.2188 | 726.93 | 3181.0404 | 1187.5813 | 0 | 0 | 1993.459 | 0 | 0 | 0
5176 | 1188.5309 | 533.35 | 2391.6454 | 1234.6516 | 0 | 0 | 1156.9937 | 0 | 0 | 0
5177 | 1249.3245 | 308.69 | 1346.5642 | 1297.8037 | 0 | 0 | 48.7605 | 0 | 0 | 0
5178 | 1404.2924 | 5.87 | 0 | 0 | 0 | 0 | 0 | 1404.292 | 0 | 0
5179 | 1160.2693 | 0 | 0 | 0 | 0 | 0 | 0 | 1160.269 | 0 | 0
5180 | 1162.6599 | 0 | 0 | 0 | 0 | 0 | 0 | 1162.66 | 0 | 0
5181 | 1369.8509 | 0 | 0 | 0 | 0 | 0 | 0 | 1369.851 | 0 | 0
5182 | 1357.1007 | 0 | 0 | 0 | 0 | 0 | 0 | 1051.227 | 0 | 317.7434
5183 | 1209.6763 | 0 | 0 | 0 | 0 | 0 | 0 | 617.676 | 0 | 614.9724
5184 | 945.9063 | 0 | 0 | 0 | 0 | 0 | 0 | 945.906 | 0 | 0
5185 | 1825.6709 | 0 | 0 | 0 | 0 | 0 | 0 | 1825.671 | 0 | 0
5186 | 1777.8576 | 0 | 0 | 0 | 0 | 0 | 0 | 1777.858 | 0 | 0
5187 | 1880.6562 | 0 | 0 | 0 | 0 | 0 | 0 | 1880.656 | 0 | 0
5188 | 2020.9085 | 0 | 0 | 0 | 0 | 0 | 0 | 2020.909 | 0 | 0
5189 | 2148.4107 | 0 | 0 | 0 | 0 | 0 | 0 | 2148.411 | 0 | 0
5190 | 2121.3165 | 0 | 0 | 0 | 0 | 0 | 0 | 2121.316 | 0 | 0
5191 | 1969.1108 | 80.87 | 322.2009 | 322.2009 | 0 | 0 | 0 | 1658.946 | 0 | 0
5192 | 1123.1632 | 260.07 | 1171.7884 | 1166.7471 | -5.0413 | 0 | 0 | 0 | 0 | 0
5193 | 1632.0301 | 373.01 | 1671.1958 | 1671.1958 | 0 | 0 | 0 | 18.902 | 0 | 4.5292
5194 | 1933.3126 | 525.17 | 2310.0971 | 2008.3347 | -301.7624 | 0 | 0 | 0 | 0 | 0
5195 | 2180.0402 | 667.52 | 2886.2504 | 2264.6359 | -614.9724 | 0 | 6.6421 | 0 | 0 | 0
5196 | 2017.7698 | 804.21 | 3423.0943 | 2096.0691 | -121.2763 | 0 | 1205.749 | 0 | 0 | 0
5197 | 1936.1236 | 781.9 | 3328.9911 | 2011.2548 | 0 | 0 | 1317.7363 | 0 | 0 | 0
5198 | 2326.1845 | 742.66 | 3179.4437 | 2416.452 | 0 | 0 | 762.9917 | 0 | 0 | 0
5199 | 2160.3092 | 540.14 | 2353.5295 | 2244.1392 | 0 | 0 | 109.3903 | 0 | 0 | 0
5200 | 1965.9362 | 64.92 | 259.0156 | 259.0156 | 0 | 0 | 0 | 1716.596 | 0 | 0
5201 | 2270.9292 | 88.89 | 373.5874 | 373.5874 | 0 | 0 | 0 | 1911.297 | 0 | 0
5202 | 1602.9128 | 27.43 | 92.678 | 92.678 | 0 | 0 | 0 | 1513.697 | 0 | 0
5203 | 2148.4226 | 0 | 0 | 0 | 0 | 0 | 0 | 2148.423 | 0 | 0
5204 | 2164.3484 | 0 | 0 | 0 | 0 | 0 | 0 | 2164.348 | 0 | 0
5205 | 1992.2206 | 0 | 0 | 0 | 0 | 0 | 0 | 1992.221 | 0 | 0
5206 | 1660.7151 | 0 | 0 | 0 | 0 | 0 | 0 | 1354.841 | 0 | 317.7434
5207 | 2342.8514 | 0 | 0 | 0 | 0 | 0 | 0 | 1750.851 | 0 | 614.9724
5208 | 2067.1281 | 0 | 0 | 0 | 0 | 0 | 0 | 2067.128 | 0 | 0
5209 | 1512.4939 | 0 | 0 | 0 | 0 | 0 | 0 | 1512.494 | 0 | 0
5210 | 1488.5872 | 0 | 0 | 0 | 0 | 0 | 0 | 1488.587 | 0 | 0
5211 | 1255.099 | 0 | 0 | 0 | 0 | 0 | 0 | 1255.099 | 0 | 0
5212 | 1229.5985 | 0 | 0 | 0 | 0 | 0 | 0 | 1229.599 | 0 | 0
5213 | 1267.0523 | 0 | 0 | 0 | 0 | 0 | 0 | 1267.052 | 0 | 0
5214 | 1408.8984 | 0 | 0 | 0 | 0 | 0 | 0 | 1408.898 | 0 | 0
5215 | 1368.2571 | 5.87 | 0 | 0 | 0 | 0 | 0 | 1368.257 | 0 | 0
5216 | 992.7355 | 14.69 | 38.1813 | 38.1813 | 0 | 0 | 0 | 955.981 | 0 | 0
5217 | 1172.2624 | 116.61 | 502.4293 | 502.4293 | 0 | 0 | 0 | 688.601 | 0 | 0
5218 | 1292.8316 | 276.61 | 1225.4572 | 1225.4572 | 0 | 0 | 0 | 113.151 | 0 | 0
5219 | 1352.5624 | 623.44 | 2730.571 | 1405.0489 | -614.9724 | 0 | 710.5497 | 0 | 0 | 0
5220 | 1429.4651 | 727.18 | 3149.5957 | 1484.9361 | -423.0387 | 0 | 1241.621 | 0 | 0 | 0
5221 | 1429.4511 | 796.74 | 3434.5794 | 1484.9205 | 0 | 0 | 1949.6589 | 0 | 0 | 0
5222 | 1083.6514 | 667.64 | 2909.5165 | 1125.7018 | 0 | 0 | 1783.8147 | 0 | 0 | 0
5223 | 1206.68 | 458.88 | 2031.6362 | 1253.5049 | 0 | 0 | 778.1312 | 0 | 0 | 0
5224 | 1434.9975 | 174.01 | 763.8227 | 763.8227 | 0 | 0 | 0 | 699.708 | 0 | 0
5225 | 1270.9311 | 156.66 | 692.7664 | 692.7664 | 0 | 0 | 0 | 604.044 | 0 | 0
5226 | 1239.3475 | 70.29 | 277.9229 | 277.9229 | 0 | 0 | 0 | 971.807 | 0 | 0
5227 | 795.2945 | 0 | 0 | 0 | 0 | 0 | 0 | 795.294 | 0 | 0
5228 | 1205.6919 | 0 | 0 | 0 | 0 | 0 | 0 | 1205.692 | 0 | 0
5229 | 1452.7272 | 0 | 0 | 0 | 0 | 0 | 0 | 1452.727 | 0 | 0
5230 | 1126.8 | 0 | 0 | 0 | 0 | 0 | 0 | 820.926 | 0 | 317.7434
5231 | 1046.3142 | 0 | 0 | 0 | 0 | 0 | 0 | 454.314 | 0 | 614.9724
5232 | 945.9063 | 0 | 0 | 0 | 0 | 0 | 0 | 945.906 | 0 | 0
5233 | 1189.7541 | 0 | 0 | 0 | 0 | 0 | 0 | 1189.754 | 0 | 0
5234 | 1080.5804 | 0 | 0 | 0 | 0 | 0 | 0 | 1080.58 | 0 | 0
5235 | 1216.8483 | 0 | 0 | 0 | 0 | 0 | 0 | 1216.848 | 0 | 0
5236 | 1073.4084 | 0 | 0 | 0 | 0 | 0 | 0 | 1073.408 | 0 | 0
5237 | 1196.1292 | 0 | 0 | 0 | 0 | 0 | 0 | 1196.129 | 0 | 0
5238 | 1135.5657 | 0 | 0 | 0 | 0 | 0 | 0 | 1135.566 | 0 | 0
5239 | 1033.564 | 41.15 | 156.2009 | 156.2009 | 0 | 0 | 0 | 883.198 | 0 | 0
5240 | 863.52 | 320.18 | 1423.6829 | 897.0287 | -526.6543 | 0 | 0 | 0 | 0 | 0
5241 | 1062.6763 | 547.08 | 2492.6151 | 1103.9139 | -511.3568 | 0 | 877.3444 | 0 | 0 | 0
5242 | 1360.7414 | 740.38 | 3280.8976 | 1413.5442 | 0 | 0 | 1867.3533 | 0 | 0 | 0
5243 | 1568.4882 | 878 | 3818.5694 | 1629.3528 | 0 | 0 | 2189.2166 | 0 | 0 | 0
5244 | 1509.8552 | 752.62 | 3242.4098 | 1568.4445 | 0 | 0 | 1673.9653 | 0 | 0 | 0
5245 | 1563.935 | 654.92 | 2840.0984 | 1624.6231 | 0 | 0 | 1215.4753 | 0 | 0 | 0
5246 | 1577.8526 | 873.63 | 3828.1555 | 1639.0801 | 0 | 0 | 2189.0753 | 0 | 0 | 0
5247 | 1437.9908 | 217.34 | 949.4634 | 949.4634 | 0 | 0 | 0 | 523.995 | 0 | 0
5248 | 1849.9352 | 34.32 | 122.1541 | 122.1541 | 0 | 0 | 0 | 1732.345 | 0 | 0
5249 | 2043.3748 | 16.65 | 46.1053 | 46.1053 | 0 | 0 | 0 | 1998.992 | 0 | 0
5250 | 1857.415 | 45.87 | 175.5746 | 175.5746 | 0 | 0 | 0 | 1688.399 | 0 | 0
5251 | 1680.6373 | 0 | 0 | 0 | 0 | 0 | 0 | 1680.637 | 0 | 0
5252 | 1432.0081 | 0 | 0 | 0 | 0 | 0 | 0 | 1432.008 | 0 | 0
5253 | 1791.4047 | 0 | 0 | 0 | 0 | 0 | 0 | 1791.405 | 0 | 0
5254 | 1433.6019 | 0 | 0 | 0 | 0 | 0 | 0 | 1127.728 | 0 | 317.7434
5255 | 1313.2718 | 0 | 0 | 0 | 0 | 0 | 0 | 721.272 | 0 | 614.9724
5256 | 1328.4127 | 0 | 0 | 0 | 0 | 0 | 0 | 1328.413 | 0 | 0
5257 | 1421.6486 | 0 | 0 | 0 | 0 | 0 | 0 | 1421.649 | 0 | 0
5258 | 1459.1023 | 0 | 0 | 0 | 0 | 0 | 0 | 1459.102 | 0 | 0
5259 | 1105.284 | 0 | 0 | 0 | 0 | 0 | 0 | 1105.284 | 0 | 0
5260 | 1154.691 | 0 | 0 | 0 | 0 | 0 | 0 | 1154.691 | 0 | 0
5261 | 1428.0237 | 0 | 0 | 0 | 0 | 0 | 0 | 1428.024 | 0 | 0
5262 | 1184.9728 | 0 | 0 | 0 | 0 | 0 | 0 | 1184.973 | 0 | 0
5263 | 1434.3988 | 83.8 | 331.2374 | 331.2374 | 0 | 0 | 0 | 1115.535 | 0 | 0
5264 | 1038.439 | 260.69 | 1175.4013 | 1078.7354 | -96.666 | 0 | 0 | 0 | 0 | 0
5265 | 1255.5094 | 383.54 | 1723.1205 | 1304.2287 | -418.8918 | 0 | 0 | 0 | 0 | 0
5266 | 1522.3454 | 530.42 | 2341.2872 | 1581.4192 | -522.4533 | 0 | 237.4147 | 0 | 0 | 0
5267 | 1627.697 | 682.48 | 2963.0202 | 1690.8594 | 0 | 0 | 1272.1608 | 0 | 0 | 0
5268 | 1740.9657 | 754.96 | 3244.905 | 1808.5227 | 0 | 0 | 1436.3823 | 0 | 0 | 0
5269 | 1456.1419 | 745.2 | 3198.6699 | 1512.6472 | 0 | 0 | 1686.0227 | 0 | 0 | 0
5270 | 1415.659 | 378.85 | 1654.79 | 1470.5933 | 0 | 0 | 184.1967 | 0 | 0 | 0
5271 | 1574.2258 | 270.78 | 1186.2953 | 1186.2953 | 0 | 0 | 0 | 432.245 | 0 | 0
5272 | 1456.6718 | 31.38 | 108.9239 | 108.9239 | 0 | 0 | 0 | 1351.817 | 0 | 0
5273 | 1710.5644 | 144.38 | 631.9351 | 631.9351 | 0 | 0 | 0 | 1102.236 | 0 | 0
5274 | 1605.2895 | 41.11 | 153.6039 | 153.6039 | 0 | 0 | 0 | 1457.423 | 0 | 0
5275 | 1610.0698 | 0 | 0 | 0 | 0 | 0 | 0 | 1610.07 | 0 | 0
5276 | 1475.0401 | 0 | 0 | 0 | 0 | 0 | 0 | 1475.04 | 0 | 0
5277 | 1838.4211 | 0 | 0 | 0 | 0 | 0 | 0 | 1838.421 | 0 | 0
5278 | 1491.7748 | 0 | 0 | 0 | 0 | 0 | 0 | 1185.901 | 0 | 317.7434
5279 | 1526.041 | 0 | 0 | 0 | 0 | 0 | 0 | 934.041 | 0 | 614.9724
5280 | 1497.353 | 0 | 0 | 0 | 0 | 0 | 0 | 1497.353 | 0 | 0
5281 | 1734.0288 | 0 | 0 | 0 | 0 | 0 | 0 | 1734.029 | 0 | 0
5282 | 1447.9459 | 0 | 0 | 0 | 0 | 0 | 0 | 1447.946 | 0 | 0
5283 | 1251.1145 | 0 | 0 | 0 | 0 | 0 | 0 | 1251.115 | 0 | 0
5284 | 1269.4429 | 0 | 0 | 0 | 0 | 0 | 0 | 1269.443 | 0 | 0
5285 | 1431.2113 | 0 | 0 | 0 | 0 | 0 | 0 | 1431.211 | 0 | 0
5286 | 1506.9156 | 0 | 0 | 0 | 0 | 0 | 0 | 1506.916 | 0 | 0
5287 | 1356.3038 | 79.91 | 317.4992 | 317.4992 | 0 | 0 | 0 | 1050.665 | 0 | 0
5288 | 1302.3903 | 253.36 | 1138.77 | 1138.77 | 0 | 0 | 0 | 206.159 | 0 | 0
5289 | 1113.0576 | 409.38 | 1830.135 | 1156.2499 | -614.9724 | 0 | 58.9127 | 0 | 0 | 0
5290 | 1552.2695 | 546.97 | 2392.8867 | 1612.5044 | -423.0387 | 0 | 357.3436 | 0 | 0 | 0
5291 | 1629.2201 | 586.66 | 2527.413 | 1692.4415 | 0 | 0 | 834.9715 | 0 | 0 | 0
5292 | 1607.9571 | 958.05 | 4042.1544 | 1670.3544 | 0 | 0 | 2371.8 | 0 | 0 | 0
5293 | 1593.6599 | 754.25 | 3174.6351 | 1655.5016 | 0 | 0 | 1519.1335 | 0 | 0 | 0
5294 | 1528.3529 | 516.47 | 2218.0455 | 1587.6604 | 0 | 0 | 630.3852 | 0 | 0 | 0
5295 | 1862.026 | 609.51 | 2630.6297 | 1934.2815 | 0 | 0 | 696.3482 | 0 | 0 | 0
5296 | 1724.6753 | 244.02 | 1072.1545 | 1072.1545 | 0 | 0 | 0 | 692.571 | 0 | 0
5297 | 1844.8819 | 207.55 | 920.7861 | 920.7861 | 0 | 0 | 0 | 958.492 | 0 | 0
5298 | 1817.6831 | 5.87 | 0 | 0 | 0 | 0 | 0 | 1817.683 | 0 | 0
5299 | 1765.9551 | 0 | 0 | 0 | 0 | 0 | 0 | 1765.955 | 0 | 0
5300 | 1718.8879 | 0 | 0 | 0 | 0 | 0 | 0 | 1718.888 | 0 | 0
5301 | 1542.7756 | 0 | 0 | 0 | 0 | 0 | 0 | 1542.776 | 0 | 0
5302 | 1653.5431 | 0 | 0 | 0 | 0 | 0 | 0 | 1347.669 | 0 | 317.7434
5303 | 1906.9535 | 0 | 0 | 0 | 0 | 0 | 0 | 1314.954 | 0 | 614.9724
5304 | 1835.2336 | 0 | 0 | 0 | 0 | 0 | 0 | 1835.234 | 0 | 0
5305 | 1701.3564 | 0 | 0 | 0 | 0 | 0 | 0 | 1701.356 | 0 | 0
5306 | 1351.5224 | 0 | 0 | 0 | 0 | 0 | 0 | 1351.522 | 0 | 0
5307 | 1069.424 | 0 | 0 | 0 | 0 | 0 | 0 | 1069.424 | 0 | 0
5308 | 1283.7869 | 0 | 0 | 0 | 0 | 0 | 0 | 1283.787 | 0 | 0
5309 | 1391.3668 | 0 | 0 | 0 | 0 | 0 | 0 | 1391.367 | 0 | 0
5310 | 1366.6633 | 0 | 0 | 0 | 0 | 0 | 0 | 1366.663 | 0 | 0
5311 | 1409.6953 | 51.77 | 204.6715 | 204.6715 | 0 | 0 | 0 | 1212.669 | 0 | 0
5312 | 1126.6764 | 169.7 | 758.0688 | 758.0688 | 0 | 0 | 0 | 396.926 | 0 | 0
5313 | 1236.8333 | 332.23 | 1492.1786 | 1284.828 | -207.3506 | 0 | 0 | 0 | 0 | 0
5314 | 853.2232 | 573.23 | 2524.7817 | 886.3331 | -614.9724 | 0 | 1023.4761 | 0 | 0 | 0
5315 | 1279.1002 | 624.73 | 2714.5142 | 1328.7352 | -215.6881 | 0 | 1170.091 | 0 | 0 | 0
5316 | 1487.5921 | 779.12 | 3328.3398 | 1545.3176 | 0 | 0 | 1783.0221 | 0 | 0 | 0
5317 | 1377.6534 | 734.39 | 3150.2637 | 1431.1125 | 0 | 0 | 1719.1512 | 0 | 0 | 0
5318 | 1389.6814 | 711 | 3074.3281 | 1443.6083 | 0 | 0 | 1630.7198 | 0 | 0 | 0
5319 | 1142.5534 | 360.51 | 1593.2792 | 1186.8905 | 0 | 0 | 406.3887 | 0 | 0 | 0
5320 | 1250.1114 | 246 | 1094.0016 | 1094.0016 | 0 | 0 | 0 | 196.977 | 0 | 0
5321 | 1587.4332 | 67.43 | 277.4315 | 277.4315 | 0 | 0 | 0 | 1320.365 | 0 | 0
5322 | 1534.0547 | 43.01 | 163.1017 | 163.1017 | 0 | 0 | 0 | 1377.045 | 0 | 0
5323 | 1588.2052 | 0 | 0 | 0 | 0 | 0 | 0 | 1588.205 | 0 | 0
5324 | 1595.3702 | 0 | 0 | 0 | 0 | 0 | 0 | 1595.37 | 0 | 0
5325 | 1622.4644 | 0 | 0 | 0 | 0 | 0 | 0 | 1622.464 | 0 | 0
5326 | 1469.4619 | 0 | 0 | 0 | 0 | 0 | 0 | 1469.462 | 0 | 0
5327 | 1749.1697 | 0 | 0 | 0 | 0 | 0 | 0 | 1749.17 | 0 | 0
5328 | 1341.9598 | 0 | 0 | 0 | 0 | 0 | 0 | 1036.086 | 0 | 317.7434
5329 | 1458.3055 | 0 | 0 | 0 | 0 | 0 | 0 | 1458.305 | 0 | 0
5330 | 1478.2277 | 0 | 0 | 0 | 0 | 0 | 0 | 1478.228 | 0 | 0
5331 | 1371.4446 | 0 | 0 | 0 | 0 | 0 | 0 | 1371.445 | 0 | 0
5332 | 1293.3496 | 0 | 0 | 0 | 0 | 0 | 0 | 1293.35 | 0 | 0
5333 | 1466.2743 | 0 | 0 | 0 | 0 | 0 | 0 | 1466.274 | 0 | 0
5334 | 1534.8067 | 0 | 0 | 0 | 0 | 0 | 0 | 1534.807 | 0 | 0
5335 | 1117.2373 | 76.38 | 306.4162 | 306.4162 | 0 | 0 | 0 | 230.267 | 0 | 614.9724
5336 | 1320.5663 | 328.19 | 1469.2678 | 1371.8102 | -97.4575 | 0 | 0 | 0 | 0 | 0
5337 | 1426.2447 | 414.22 | 1873.0823 | 1481.5901 | -391.4923 | 0 | 0 | 0 | 0 | 0
5338 | 1743.702 | 435.2 | 1937.1953 | 1811.3659 | -125.8294 | 0 | 0 | 0 | 0 | 0
5339 | 1773.4518 | 719.47 | 3148.4718 | 1842.2693 | -423.2319 | 0 | 882.9705 | 0 | 0 | 0
5340 | 1551.0702 | 734.95 | 3202.3244 | 1611.2589 | 0 | 0 | 1591.0656 | 0 | 0 | 0
5341 | 1468.154 | 758.93 | 3304.7963 | 1525.1253 | 0 | 0 | 1779.6709 | 0 | 0 | 0
5342 | 1368.2013 | 353.5 | 1558.7587 | 1421.2937 | 0 | 0 | 137.465 | 0 | 0 | 0
5343 | 1425.388 | 115.06 | 485.5872 | 485.5872 | 0 | 0 | 0 | 957.94 | 0 | 0
5344 | 1789.557 | 272.52 | 1219.2773 | 1219.2773 | 0 | 0 | 0 | 615.826 | 0 | 0
5345 | 1671.8207 | 15.67 | 42.0311 | 42.0311 | 0 | 0 | 0 | 1631.36 | 0 | 0
5346 | 1623.3211 | 5.87 | 0 | 0 | 0 | 0 | 0 | 1623.321 | 0 | 0
5347 | 1399.3357 | 0 | 0 | 0 | 0 | 0 | 0 | 1399.336 | 0 | 0
5348 | 1383.398 | 0 | 0 | 0 | 0 | 0 | 0 | 1383.398 | 0 | 0
5349 | 1339.5691 | 0 | 0 | 0 | 0 | 0 | 0 | 1339.569 | 0 | 0
5350 | 1674.2622 | 0 | 0 | 0 | 0 | 0 | 0 | 1368.389 | 0 | 317.7434
5351 | 1441.5708 | 0 | 0 | 0 | 0 | 0 | 0 | 849.571 | 0 | 614.9724
5352 | 1500.5405 | 0 | 0 | 0 | 0 | 0 | 0 | 1500.541 | 0 | 0
5353 | 1355.5069 | 0 | 0 | 0 | 0 | 0 | 0 | 1355.507 | 0 | 0
5354 | 1402.5233 | 0 | 0 | 0 | 0 | 0 | 0 | 1402.523 | 0 | 0
5355 | 1098.9089 | 0 | 0 | 0 | 0 | 0 | 0 | 1098.909 | 0 | 0
5356 | 1362.6789 | 0 | 0 | 0 | 0 | 0 | 0 | 1362.679 | 0 | 0
5357 | 1237.5674 | 0 | 0 | 0 | 0 | 0 | 0 | 1237.567 | 0 | 0
5358 | 1263.8647 | 0 | 0 | 0 | 0 | 0 | 0 | 1263.865 | 0 | 0
5359 | 1380.2104 | 58.55 | 234.5902 | 234.5902 | 0 | 0 | 0 | 1154.383 | 0 | 0
5360 | 1386.2658 | 26.45 | 90.8092 | 90.8092 | 0 | 0 | 0 | 1298.848 | 0 | 0
5361 | 1418.5776 | 124.29 | 537.6064 | 537.6064 | 0 | 0 | 0 | 901.054 | 0 | 0
5362 | 1606.5008 | 506.45 | 2247.6868 | 1668.8409 | -578.8459 | 0 | 0 | 0 | 0 | 0
5363 | 1395.5694 | 234.15 | 1021.3123 | 1021.3123 | 0 | 0 | 0 | 0 | 0 | 428.4114
5364 | 1749.1418 | 657.52 | 2852.6243 | 1817.017 | -614.9724 | 0 | 420.6349 | 0 | 0 | 0
5365 | 1070.1512 | 391.87 | 1713.4929 | 1111.6779 | -320.9689 | 0 | 280.8461 | 0 | 0 | 0
5366 | 1155.2987 | 223.16 | 968.1401 | 968.1401 | 0 | 0 | 0 | 223.324 | 0 | 0
5367 | 1561.8691 | 61.21 | 239.3874 | 239.3874 | 0 | 0 | 0 | 952.883 | 0 | 393.2312
5368 | 1337.3169 | 408.01 | 1826.8348 | 1389.2112 | -437.6235 | 0 | 0 | 0 | 0 | 0
5369 | 1556.0846 | 225.36 | 1006.929 | 1006.929 | 0 | 0 | 0 | 586.769 | 0 | 0
5370 | 1554.3395 | 47.74 | 183.5288 | 183.5288 | 0 | 0 | 0 | 1377.666 | 0 | 0
5371 | 914.8386 | 0 | 0 | 0 | 0 | 0 | 0 | 914.839 | 0 | 0
5372 | 1265.4585 | 0 | 0 | 0 | 0 | 0 | 0 | 1265.459 | 0 | 0
5373 | 1199.3168 | 0 | 0 | 0 | 0 | 0 | 0 | 1199.317 | 0 | 0
5374 | 1364.2726 | 0 | 0 | 0 | 0 | 0 | 0 | 1058.399 | 0 | 317.7434
5375 | 1340.366 | 0 | 0 | 0 | 0 | 0 | 0 | 748.366 | 0 | 614.9724
5376 | 1275.0212 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.021 | 0 | 0
5377 | 2321.3354 | 0 | 0 | 0 | 0 | 0 | 0 | 2321.335 | 0 | 0
5378 | 2049.5965 | 0 | 0 | 0 | 0 | 0 | 0 | 2049.597 | 0 | 0
5379 | 2418.5558 | 0 | 0 | 0 | 0 | 0 | 0 | 2418.556 | 0 | 0
5380 | 2200.2084 | 0 | 0 | 0 | 0 | 0 | 0 | 2200.208 | 0 | 0
5381 | 1996.205 | 0 | 0 | 0 | 0 | 0 | 0 | 1996.205 | 0 | 0
5382 | 2369.9456 | 0 | 0 | 0 | 0 | 0 | 0 | 2369.946 | 0 | 0
5383 | 2032.8619 | 38.23 | 143.2906 | 143.2906 | 0 | 0 | 0 | 1894.924 | 0 | 0
5384 | 1717.081 | 125.59 | 552.3616 | 552.3616 | 0 | 0 | 0 | 1185.353 | 0 | 0
5385 | 1818.1981 | 359.33 | 1626.4919 | 1626.4919 | 0 | 0 | 0 | 252.464 | 0 | 0
5386 | 2087.6529 | 504.96 | 2252.4237 | 2168.6638 | -83.7599 | 0 | 0 | 0 | 0 | 0
5387 | 2288.3681 | 703.06 | 3088.5867 | 2377.1675 | -614.9724 | 0 | 96.4468 | 0 | 0 | 0
5388 | 2277.5584 | 798.67 | 3478.6797 | 2365.9381 | -339.2788 | 0 | 773.4629 | 0 | 0 | 0
5389 | 2252.5022 | 694.75 | 3037.838 | 2339.9098 | 0 | 0 | 697.9282 | 0 | 0 | 0
5390 | 2381.0831 | 585.55 | 2577.9062 | 2473.4803 | 0 | 0 | 104.4258 | 0 | 0 | 0
5391 | 2172.9459 | 267.19 | 1183.7585 | 1183.7585 | 0 | 0 | 0 | 1033.407 | 0 | 0
5392 | 1845.8412 | 42.17 | 158.7439 | 158.7439 | 0 | 0 | 0 | 1693.027 | 0 | 0
5393 | 2378.556 | 14.69 | 38.0452 | 38.0452 | 0 | 0 | 0 | 2341.932 | 0 | 0
5394 | 2247.4788 | 10.77 | 20.2671 | 20.2671 | 0 | 0 | 0 | 2227.969 | 0 | 0
5395 | 2405.0087 | 0 | 0 | 0 | 0 | 0 | 0 | 2405.009 | 0 | 0
5396 | 1889.422 | 0 | 0 | 0 | 0 | 0 | 0 | 1889.422 | 0 | 0
5397 | 2380.3051 | 0 | 0 | 0 | 0 | 0 | 0 | 2380.305 | 0 | 0
5398 | 2206.5835 | 0 | 0 | 0 | 0 | 0 | 0 | 1900.71 | 0 | 317.7434
5399 | 2286.2723 | 0 | 0 | 0 | 0 | 0 | 0 | 1694.272 | 0 | 614.9724
5400 | 1948.3917 | 0 | 0 | 0 | 0 | 0 | 0 | 1948.392 | 0 | 0
5401 | 1804.9518 | 0 | 0 | 0 | 0 | 0 | 0 | 1804.952 | 0 | 0
5402 | 1843.2025 | 0 | 0 | 0 | 0 | 0 | 0 | 1843.202 | 0 | 0
5403 | 1243.9425 | 0 | 0 | 0 | 0 | 0 | 0 | 1243.943 | 0 | 0
5404 | 1298.1309 | 0 | 0 | 0 | 0 | 0 | 0 | 1298.131 | 0 | 0
5405 | 1563.4947 | 0 | 0 | 0 | 0 | 0 | 0 | 1563.495 | 0 | 0
5406 | 1161.0661 | 0 | 0 | 0 | 0 | 0 | 0 | 1161.066 | 0 | 0
5407 | 1122.8155 | 68.38 | 275.303 | 275.303 | 0 | 0 | 0 | 857.797 | 0 | 0
5408 | 842.0808 | 327.46 | 1463.8982 | 874.7577 | -589.1405 | 0 | 0 | 0 | 0 | 0
5409 | 1173.7765 | 414.83 | 1863.4599 | 1219.3241 | -448.8706 | 0 | 195.2652 | 0 | 0 | 0
5410 | 1566.0129 | 574.26 | 2525.7987 | 1626.7817 | 0 | 0 | 899.0169 | 0 | 0 | 0
5411 | 1402.9586 | 574.75 | 2502.3259 | 1457.4005 | 0 | 0 | 1044.9254 | 0 | 0 | 0
5412 | 1433.2991 | 661.1 | 2857.1068 | 1488.9178 | 0 | 0 | 1368.189 | 0 | 0 | 0
5413 | 1510.4219 | 797.89 | 3429.1267 | 1569.0335 | 0 | 0 | 1860.0931 | 0 | 0 | 0
5414 | 1372.2356 | 738.5 | 3207.641 | 1425.4842 | 0 | 0 | 1782.1568 | 0 | 0 | 0
5415 | 1544.9103 | 581.99 | 2569.8336 | 1604.8598 | 0 | 0 | 964.9738 | 0 | 0 | 0
5416 | 1537.5301 | 446.43 | 2006.3361 | 1597.1935 | 0 | 0 | 409.1426 | 0 | 0 | 0
5417 | 1196.4679 | 312.36 | 1394.6099 | 1242.8966 | 0 | 0 | 151.7133 | 0 | 0 | 0
5418 | 1288.0652 | 91.04 | 329.9711 | 329.9711 | 0 | 0 | 0 | 970.42 | 0 | 0
5419 | 1408.1115 | 0 | 0 | 0 | 0 | 0 | 0 | 1408.111 | 0 | 0
5420 | 1260.6772 | 0 | 0 | 0 | 0 | 0 | 0 | 1260.677 | 0 | 0
5421 | 1176.207 | 0 | 0 | 0 | 0 | 0 | 0 | 1176.207 | 0 | 0
5422 | 1688.6062 | 0 | 0 | 0 | 0 | 0 | 0 | 1382.732 | 0 | 317.7434
5423 | 1341.1629 | 0 | 0 | 0 | 0 | 0 | 0 | 749.163 | 0 | 614.9724
5424 | 1206.4888 | 0 | 0 | 0 | 0 | 0 | 0 | 1206.489 | 0 | 0
5425 | 1402.5233 | 0 | 0 | 0 | 0 | 0 | 0 | 1402.523 | 0 | 0
5426 | 1134.7688 | 0 | 0 | 0 | 0 | 0 | 0 | 1134.769 | 0 | 0
5427 | 1440.7739 | 0 | 0 | 0 | 0 | 0 | 0 | 1440.774 | 0 | 0
5428 | 1137.9564 | 0 | 0 | 0 | 0 | 0 | 0 | 1137.956 | 0 | 0
5429 | 876.5771 | 0 | 0 | 0 | 0 | 0 | 0 | 876.577 | 0 | 0
5430 | 1141.1439 | 0 | 0 | 0 | 0 | 0 | 0 | 1141.144 | 0 | 0
5431 | 939.5312 | 80.72 | 321.2483 | 321.2483 | 0 | 0 | 0 | 630.283 | 0 | 0
5432 | 1269.4808 | 257.76 | 1161.7577 | 1161.7577 | 0 | 0 | 0 | 151.121 | 0 | 0
5433 | 1423.8829 | 448.88 | 2015.6978 | 1479.1354 | -536.5624 | 0 | 0 | 0 | 0 | 0
5434 | 1541.5026 | 630.62 | 2770.5193 | 1601.3196 | -501.4498 | 0 | 667.7499 | 0 | 0 | 0
5435 | 1400.2571 | 875.05 | 3804.772 | 1454.5936 | 0 | 0 | 2350.1784 | 0 | 0 | 0
5436 | 1426.2825 | 779.67 | 3342.3626 | 1481.6296 | 0 | 0 | 1860.733 | 0 | 0 | 0
5437 | 1362.2406 | 685.67 | 2957.4262 | 1415.1024 | 0 | 0 | 1542.3238 | 0 | 0 | 0
5438 | 1667.2764 | 704.59 | 3050.1749 | 1731.9742 | 0 | 0 | 1318.2006 | 0 | 0 | 0
5439 | 1636.4498 | 561.77 | 2468.492 | 1699.952 | 0 | 0 | 768.54 | 0 | 0 | 0
5440 | 1895.057 | 397.35 | 1774.8623 | 1774.8623 | 0 | 0 | 0 | 186.495 | 0 | 0
5441 | 1891.8794 | 87.49 | 368.2584 | 368.2584 | 0 | 0 | 0 | 1537.377 | 0 | 0
5442 | 1615.2725 | 17.62 | 49.2632 | 49.2632 | 0 | 0 | 0 | 1567.849 | 0 | 0
5443 | 1799.3766 | 0 | 0 | 0 | 0 | 0 | 0 | 1799.377 | 0 | 0
5444 | 1355.5069 | 0 | 0 | 0 | 0 | 0 | 0 | 1355.507 | 0 | 0
5445 | 1471.8526 | 0 | 0 | 0 | 0 | 0 | 0 | 1471.853 | 0 | 0
5446 | 1823.2803 | 0 | 0 | 0 | 0 | 0 | 0 | 1517.407 | 0 | 317.7434
5447 | 1494.9623 | 0 | 0 | 0 | 0 | 0 | 0 | 902.962 | 0 | 614.9724
5448 | 1516.4783 | 0 | 0 | 0 | 0 | 0 | 0 | 1516.478 | 0 | 0
5449 | 1078.9867 | 0 | 0 | 0 | 0 | 0 | 0 | 1078.987 | 0 | 0
5450 | 1199.3168 | 0 | 0 | 0 | 0 | 0 | 0 | 1199.317 | 0 | 0
5451 | 1483.009 | 0 | 0 | 0 | 0 | 0 | 0 | 1483.009 | 0 | 0
5452 | 1071.8147 | 0 | 0 | 0 | 0 | 0 | 0 | 1071.815 | 0 | 0
5453 | 1069.424 | 0 | 0 | 0 | 0 | 0 | 0 | 1069.424 | 0 | 0
5454 | 908.4526 | 0 | 0 | 0 | 0 | 0 | 0 | 908.453 | 0 | 0
5455 | 961.0472 | 80.56 | 321.0831 | 321.0831 | 0 | 0 | 0 | 651.958 | 0 | 0
5456 | 1232.0808 | 257.24 | 1163.4499 | 1163.4499 | 0 | 0 | 0 | 112.092 | 0 | 0
5457 | 898.5931 | 444.41 | 2005.7803 | 933.4627 | -614.9724 | 0 | 457.3452 | 0 | 0 | 0
5458 | 1637.5824 | 581.82 | 2579.3969 | 1701.128 | -423.0387 | 0 | 455.2302 | 0 | 0 | 0
5459 | 1399.4642 | 639.05 | 2799.8946 | 1453.7698 | 0 | 0 | 1346.1247 | 0 | 0 | 0
5460 | 1253.0838 | 962.85 | 4203.0269 | 1301.7096 | 0 | 0 | 2901.3173 | 0 | 0 | 0
5461 | 1139.5362 | 758.09 | 3288.326 | 1183.7554 | 0 | 0 | 2104.5706 | 0 | 0 | 0
5462 | 1059.7836 | 883.33 | 3883.6588 | 1100.9087 | 0 | 0 | 2782.7502 | 0 | 0 | 0
5463 | 1558.9445 | 738.23 | 3293.3767 | 1619.4395 | 0 | 0 | 1673.9372 | 0 | 0 | 0
5464 | 1523.5696 | 461.71 | 2069.3385 | 1582.6918 | 0 | 0 | 486.6468 | 0 | 0 | 0
5465 | 1542.7437 | 307.27 | 1351.1598 | 1351.1598 | 0 | 0 | 0 | 242.057 | 0 | 0
5466 | 951.0801 | 71.57 | 273.6409 | 273.6409 | 0 | 0 | 0 | 687.661 | 0 | 0
5467 | 976.1213 | 0 | 0 | 0 | 0 | 0 | 0 | 976.121 | 0 | 0
5468 | 1243.9425 | 0 | 0 | 0 | 0 | 0 | 0 | 1243.943 | 0 | 0
5469 | 1221.6297 | 0 | 0 | 0 | 0 | 0 | 0 | 1221.63 | 0 | 0
5470 | 1326.8189 | 0 | 0 | 0 | 0 | 0 | 0 | 1020.945 | 0 | 317.7434
5471 | 1231.9892 | 0 | 0 | 0 | 0 | 0 | 0 | 639.989 | 0 | 614.9724
5472 | 1280.5994 | 0 | 0 | 0 | 0 | 0 | 0 | 1280.599 | 0 | 0
5473 | 1526.8378 | 0 | 0 | 0 | 0 | 0 | 0 | 1526.838 | 0 | 0
5474 | 1339.5691 | 0 | 0 | 0 | 0 | 0 | 0 | 1339.569 | 0 | 0
5475 | 1200.1137 | 0 | 0 | 0 | 0 | 0 | 0 | 1200.114 | 0 | 0
5476 | 1116.4404 | 0 | 0 | 0 | 0 | 0 | 0 | 1116.44 | 0 | 0
5477 | 1081.3773 | 0 | 0 | 0 | 0 | 0 | 0 | 1081.377 | 0 | 0
5478 | 1066.2364 | 0 | 0 | 0 | 0 | 0 | 0 | 1066.236 | 0 | 0
5479 | 1336.3816 | 46.91 | 182.411 | 182.411 | 0 | 0 | 0 | 1160.784 | 0 | 0
5480 | 911.6949 | 260.37 | 1175.4606 | 947.0731 | -228.3875 | 0 | 0 | 0 | 0 | 0
5481 | 1039.4979 | 562.21 | 2565.1206 | 1079.8355 | -614.9724 | 0 | 870.3127 | 0 | 0 | 0
5482 | 1131.3791 | 647.47 | 2845.3018 | 1175.2819 | -194.6512 | 0 | 1475.3687 | 0 | 0 | 0
5483 | 1048.2088 | 890.17 | 3874.3615 | 1088.8834 | 0 | 0 | 2785.4781 | 0 | 0 | 0
5484 | 1006.9788 | 960.1 | 4144.5962 | 1046.0546 | 0 | 0 | 3098.5416 | 0 | 0 | 0
5485 | 904.3835 | 957.1 | 4144.0643 | 939.4784 | 0 | 0 | 3204.5859 | 0 | 0 | 0
5486 | 1037.6411 | 875.17 | 3834.8443 | 1077.9064 | 0 | 0 | 2756.9379 | 0 | 0 | 0
5487 | 1025.9707 | 729.64 | 3257.9223 | 1065.7835 | 0 | 0 | 2192.1388 | 0 | 0 | 0
5488 | 1029.466 | 531.49 | 2424.8819 | 1069.4142 | 0 | 0 | 1355.4678 | 0 | 0 | 0
5489 | 1371.0223 | 302.36 | 1340.0768 | 1340.0768 | 0 | 0 | 0 | 81.004 | 0 | 0
5490 | 1163.9011 | 83.43 | 286.1606 | 286.1606 | 0 | 0 | 0 | 888.43 | 0 | 0
5491 | 1193.7386 | 0 | 0 | 0 | 0 | 0 | 0 | 1193.739 | 0 | 0
5492 | 1105.284 | 0 | 0 | 0 | 0 | 0 | 0 | 1105.284 | 0 | 0
5493 | 1094.1275 | 0 | 0 | 0 | 0 | 0 | 0 | 1094.128 | 0 | 0
5494 | 1174.6132 | 0 | 0 | 0 | 0 | 0 | 0 | 1174.613 | 0 | 0
5495 | 1165.0506 | 0 | 0 | 0 | 0 | 0 | 0 | 954.9 | 0 | 218.3048
5496 | 495.6645 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 514.8981
5497 | 368.1624 | 0 | 0 | 0 | 0 | 0 | 0 | 368.162 | 0 | 0
5498 | 341.0682 | 0 | 0 | 0 | 0 | 0 | 0 | 341.068 | 0 | 0
5499 | 376.9281 | 0 | 0 | 0 | 0 | 0 | 0 | 376.928 | 0 | 0
5500 | 385.6939 | 0 | 0 | 0 | 0 | 0 | 0 | 385.694 | 0 | 0
5501 | 367.3655 | 0 | 0 | 0 | 0 | 0 | 0 | 367.365 | 0 | 0
5502 | 324.3335 | 0 | 0 | 0 | 0 | 0 | 0 | 324.334 | 0 | 0
5503 | 333.8962 | 39.21 | 147.3409 | 147.3409 | 0 | 0 | 0 | 0 | 0 | 199.5118
5504 | 280.1859 | 325.45 | 1464.3127 | 291.0585 | -614.9724 | 0 | 558.2817 | 0 | 0 | 0
5505 | 809.242 | 556.88 | 2560.9279 | 840.6455 | -423.0387 | 0 | 1297.2438 | 0 | 0 | 0
5506 | 1188.3885 | 754.33 | 3390.4489 | 1234.5031 | 0 | 0 | 2155.9458 | 0 | 0 | 0
5507 | 993.5084 | 902.56 | 3983.9014 | 1032.0619 | 0 | 0 | 2951.8395 | 0 | 0 | 0
5508 | 1233.7922 | 834.24 | 3606.3333 | 1281.669 | 0 | 0 | 2324.6643 | 0 | 0 | 0
5509 | 1154.0047 | 606.22 | 2644.3855 | 1198.7848 | 0 | 0 | 1445.6007 | 0 | 0 | 0
5510 | 1230.0597 | 690.96 | 3017.8847 | 1277.7922 | 0 | 0 | 1740.0925 | 0 | 0 | 0
5511 | 1043.0311 | 587.05 | 2593.0935 | 1083.5056 | 0 | 0 | 1509.5879 | 0 | 0 | 0
5512 | 1276.6757 | 437.07 | 1962.7385 | 1326.2171 | 0 | 0 | 636.5214 | 0 | 0 | 0
5513 | 1051.0647 | 307.68 | 1359.463 | 1091.8513 | 0 | 0 | 267.6117 | 0 | 0 | 0
5514 | 1040.0298 | 83.95 | 277.686 | 277.686 | 0 | 0 | 0 | 772.717 | 0 | 0
5515 | 1084.0897 | 0 | 0 | 0 | 0 | 0 | 0 | 1084.09 | 0 | 0
5516 | 894.9055 | 0 | 0 | 0 | 0 | 0 | 0 | 451.258 | 0 | 460.8626
5517 | 269.3482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 279.8
5518 | 90.8453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.3702
5519 | 94.0328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.6819
5520 | 90.8453 | 0 | 0 | 0 | 0 | 0 | 0 | 90.845 | 0 | 0
5521 | 95.6266 | 0 | 0 | 0 | 0 | 0 | 0 | 95.627 | 0 | 0
5522 | 87.6577 | 0 | 0 | 0 | 0 | 0 | 0 | 87.658 | 0 | 0
5523 | 94.0328 | 0 | 0 | 0 | 0 | 0 | 0 | 94.033 | 0 | 0
5524 | 85.267 | 0 | 0 | 0 | 0 | 0 | 0 | 85.267 | 0 | 0
5525 | 94.8297 | 0 | 0 | 0 | 0 | 0 | 0 | 94.83 | 0 | 0
5526 | 87.6577 | 0 | 0 | 0 | 0 | 0 | 0 | 87.658 | 0 | 0
5527 | 93.2359 | 101.54 | 355.6442 | 96.854 | -258.7902 | 0 | 0 | 0 | 0 | 0
5528 | 76.7762 | 330.45 | 1485.5375 | 79.7553 | -614.9724 | 0 | 790.8099 | 0 | 0 | 0
5529 | 83.0716 | 562.97 | 2581.7747 | 86.2956 | -164.2485 | 0 | 2331.2306 | 0 | 0 | 0
5530 | 78.5941 | 758.69 | 3393.5185 | 81.6438 | 0 | 0 | 3311.8747 | 0 | 0 | 0
5531 | 85.6854 | 898.37 | 3939.0552 | 89.01 | 0 | 0 | 3850.0452 | 0 | 0 | 0
5532 | 80.162 | 969.29 | 4192.2513 | 83.2727 | 0 | 0 | 4108.9787 | 0 | 0 | 0
5533 | 88.2653 | 964.85 | 4164.0655 | 91.6911 | 0 | 0 | 4072.3743 | 0 | 0 | 0
5534 | 80.4469 | 889.47 | 3871.9255 | 83.5687 | 0 | 0 | 3788.3568 | 0 | 0 | 0
5535 | 94.9911 | 602.56 | 2640.9855 | 98.6771 | 0 | 0 | 2542.3084 | 0 | 0 | 0
5536 | 84.2281 | 539.03 | 2445.4804 | 87.4964 | 0 | 0 | 2357.9839 | 0 | 0 | 0
5537 | 89.7426 | 304.16 | 1339.1014 | 93.2255 | 0 | 0 | 1245.8759 | 0 | 0 | 0
5538 | 80.4598 | 74.48 | 277.8512 | 83.5812 | 0 | 0 | 194.27 | 0 | 0 | 0
5539 | 96.4285 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.1699
5540 | 86.0639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4037
5541 | 93.2359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.854
5542 | 86.8608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2316
5543 | 92.439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.0261
5544 | 86.8608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2316
5545 | 93.2359 | 0 | 0 | 0 | 0 | 0 | 0 | 93.236 | 0 | 0
5546 | 87.6577 | 0 | 0 | 0 | 0 | 0 | 0 | 87.085 | 0 | 0.59524
5547 | 92.439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.0261
5548 | 86.8608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2316
5549 | 93.2359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.854
5550 | 82.8764 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.092
5551 | 84.4702 | 99.86 | 362.7288 | 87.7478 | -274.981 | 0 | 0 | 0 | 0 | 0
5552 | 79.4856 | 325.77 | 1467.2515 | 82.5704 | -614.9724 | 0 | 769.7086 | 0 | 0 | 0
5553 | 83.7151 | 556.99 | 2558.0297 | 86.9635 | -148.0577 | 0 | 2323.0084 | 0 | 0 | 0
5554 | 80.1929 | 753.53 | 3383.1336 | 83.3049 | 0 | 0 | 3299.8287 | 0 | 0 | 0
5555 | 80.8682 | 906.94 | 4000.3779 | 84.0071 | 0 | 0 | 3916.3708 | 0 | 0 | 0
5556 | 79.7665 | 973.35 | 4251.0363 | 82.8613 | 0 | 0 | 4168.175 | 0 | 0 | 0
5557 | 81.1979 | 967.79 | 4218.6983 | 84.3489 | 0 | 0 | 4134.3494 | 0 | 0 | 0
5558 | 74.3586 | 882.58 | 3881.3994 | 77.2434 | 0 | 0 | 3804.156 | 0 | 0 | 0
5559 | 87.9635 | 565.25 | 2496.95 | 91.3774 | 0 | 0 | 2405.5726 | 0 | 0 | 0
5560 | 78.7595 | 470.46 | 2116.5616 | 81.8163 | 0 | 0 | 2034.7453 | 0 | 0 | 0
5561 | 83.995 | 272.65 | 1220.9155 | 87.2544 | 0 | 0 | 1133.6611 | 0 | 0 | 0
5562 | 78.9318 | 81.19 | 280.1407 | 81.9949 | 0 | 0 | 198.1458 | 0 | 0 | 0
5563 | 94.8446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 98.5254
5564 | 89.2515 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.7144
5565 | 93.2359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.854
5566 | 86.8608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2316
5567 | 96.4235 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.1647
5568 | 86.8608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2316
5569 | 93.2359 | 0 | 0 | 0 | 0 | 0 | 0 | 93.236 | 0 | 0
5570 | 88.4546 | 0 | 0 | 0 | 0 | 0 | 0 | 88.455 | 0 | 0
5571 | 86.8608 | 0 | 0 | 0 | 0 | 0 | 0 | 0.234 | 0 | 89.9885
5572 | 86.8608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2316
5573 | 93.2359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.854
5574 | 83.6733 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.9199
5575 | 86.8608 | 90.61 | 358.7315 | 90.2316 | -268.4999 | 0 | 0 | 0 | 0 | 0
5576 | 75.7243 | 330.8 | 1491.3808 | 78.6625 | -614.9724 | 0 | 797.746 | 0 | 0 | 0
5577 | 84.1783 | 563.33 | 2586.1626 | 87.4445 | -154.5388 | 0 | 2344.1793 | 0 | 0 | 0
5578 | 72.4879 | 760.79 | 3416.6008 | 75.3009 | 0 | 0 | 3341.2999 | 0 | 0 | 0
5579 | 80.7865 | 753.93 | 3295.902 | 83.9219 | 0 | 0 | 3211.9801 | 0 | 0 | 0
5580 | 74.8706 | 834.66 | 3608.8586 | 77.7753 | 0 | 0 | 3531.0833 | 0 | 0 | 0
5581 | 86.2801 | 964.77 | 4214.5347 | 89.6281 | 0 | 0 | 4124.9067 | 0 | 0 | 0
5582 | 78.115 | 560.62 | 2456.2497 | 81.1462 | 0 | 0 | 2375.1034 | 0 | 0 | 0
5583 | 78.5463 | 609.23 | 2696.465 | 81.595 | 0 | 0 | 2614.87 | 0 | 0 | 0
5584 | 79.3432 | 532.43 | 2432.7592 | 82.4219 | 0 | 0 | 2350.3373 | 0 | 0 | 0
5585 | 88.3072 | 298.37 | 1319.8212 | 91.7337 | 0 | 0 | 1228.0874 | 0 | 0 | 0
5586 | 82.3435 | 78.67 | 271.394 | 85.5393 | 0 | 0 | 185.8546 | 0 | 0 | 0
5587 | 97.2562 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 101.03
5588 | 88.4546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.8875
5589 | 94.0328 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.6819
5590 | 86.8608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2316
5591 | 90.8453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.3702
5592 | 84.4702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87.7478
5593 | 93.2359 | 0 | 0 | 0 | 0 | 0 | 0 | 93.236 | 0 | 0
5594 | 81.2826 | 0 | 0 | 0 | 0 | 0 | 0 | 67.194 | 0 | 14.6357
5595 | 92.439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.0261
5596 | 79.6888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.7813
5597 | 90.0484 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 93.5423
5598 | 79.6888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.7813
5599 | 86.0639 | 80.59 | 323.0755 | 89.4037 | -233.6719 | 0 | 0 | 0 | 0 | 0
5600 | 75.1595 | 257.01 | 1166.6193 | 78.0755 | -614.9724 | 0 | 473.5713 | 0 | 0 | 0
5601 | 85.1346 | 455.96 | 2069.8174 | 88.4386 | -189.3668 | 0 | 1792.0119 | 0 | 0 | 0
5602 | 74.1644 | 598.89 | 2674.6002 | 77.0419 | 0 | 0 | 2597.5583 | 0 | 0 | 0
5603 | 80.2656 | 733.19 | 3233.1541 | 83.3797 | 0 | 0 | 3149.7744 | 0 | 0 | 0
5604 | 72.995 | 741.51 | 3252.3387 | 75.8265 | 0 | 0 | 3176.5122 | 0 | 0 | 0
5605 | 82.3325 | 783.36 | 3428.6114 | 85.5269 | 0 | 0 | 3343.0846 | 0 | 0 | 0
5606 | 74.6694 | 667.2 | 2942.5287 | 77.5676 | 0 | 0 | 2864.9612 | 0 | 0 | 0
5607 | 86.4494 | 607.72 | 2707.4524 | 89.8036 | 0 | 0 | 2617.6488 | 0 | 0 | 0
5608 | 80.9369 | 457.67 | 2070.9051 | 84.0777 | 0 | 0 | 1986.8273 | 0 | 0 | 0
5609 | 86.7502 | 269.65 | 1212.3464 | 90.1163 | 0 | 0 | 1122.2301 | 0 | 0 | 0
5610 | 79.3501 | 76.82 | 269.3766 | 82.4292 | 0 | 0 | 186.9475 | 0 | 0 | 0
5611 | 96.4444 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.1865
5612 | 87.6577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.0595
5613 | 90.8453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.3702
5614 | 86.0639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4037
5615 | 92.439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.0261
5616 | 87.6577 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.0595
5617 | 94.0328 | 0 | 0 | 0 | 0 | 0 | 0 | 94.033 | 0 | 0
5618 | 86.8608 | 0 | 0 | 0 | 0 | 0 | 0 | 77.538 | 0 | 9.6837
5619 | 93.2359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.854
5620 | 79.6888 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.7813
5621 | 88.4546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.8875
5622 | 86.0639 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.4037
5623 | 88.4546 | 94.48 | 370.8668 | 91.8864 | -278.9804 | 0 | 0 | 0 | 0 | 0
5624 | 78.9726 | 285.56 | 1295.6274 | 82.0375 | -614.9724 | 0 | 598.6175 | 0 | 0 | 0
5625 | 84.4114 | 451.44 | 2040.8742 | 87.6865 | -144.0594 | 0 | 1809.1283 | 0 | 0 | 0
5626 | 75.3169 | 617.48 | 2740.3763 | 78.2397 | 0 | 0 | 2662.1366 | 0 | 0 | 0
5627 | 86.3179 | 719.78 | 3150.0923 | 89.6675 | 0 | 0 | 3060.4247 | 0 | 0 | 0
5628 | 74.6116 | 781.18 | 3394.7661 | 77.5073 | 0 | 0 | 3317.2588 | 0 | 0 | 0
5629 | 87.3011 | 736.47 | 3205.7078 | 90.6897 | 0 | 0 | 3115.0181 | 0 | 0 | 0
5630 | 82.3166 | 277.28 | 1214.0376 | 85.5103 | 0 | 0 | 1128.5274 | 0 | 0 | 0
5631 | 88.9845 | 405.72 | 1800.6122 | 92.438 | 0 | 0 | 1708.1742 | 0 | 0 | 0
5632 | 81.1182 | 347.19 | 1559.8412 | 84.2658 | 0 | 0 | 1475.5754 | 0 | 0 | 0
5633 | 82.9302 | 125.32 | 546.1111 | 86.1491 | 0 | 0 | 459.962 | 0 | 0 | 0
5634 | 82.6104 | 41.96 | 155.9755 | 85.8157 | 0 | 0 | 70.1598 | 0 | 0 | 0
5635 | 95.6336 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.3451
5636 | 90.8453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.3702
5637 | 93.2359 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.854
5638 | 88.4546 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.8875
5639 | 97.2204 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 100.9926
5640 | 90.0484 | 0 | 0 | 0 | 0 | 0 | 0 | 90.048 | 0 | 0
5641 | 92.439 | 0 | 0 | 0 | 0 | 0 | 0 | 92.439 | 0 | 0
5642 | 86.0639 | 0 | 0 | 0 | 0 | 0 | 0 | 8.992 | 0 | 80.0628
5643 | 90.8453 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.3702
5644 | 86.8608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.2316
5645 | 92.439 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.0261
5646 | 85.267 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 88.5758
5647 | 76.5013 | 70.27 | 283.0857 | 79.4706 | -203.6151 | 0 | 0 | 0 | 0 | 0
5648 | 82.453 | 254.6 | 1153.7745 | 85.6526 | -614.9724 | 0 | 453.1495 | 0 | 0 | 0
5649 | 644.2323 | 465.2 | 2106.5018 | 669.2313 | -219.4236 | 0 | 1217.8469 | 0 | 0 | 0
5650 | 550.7832 | 607.23 | 2702.195 | 572.156 | 0 | 0 | 2130.039 | 0 | 0 | 0
5651 | 872.9741 | 670.53 | 2946.9644 | 906.8506 | 0 | 0 | 2040.1138 | 0 | 0 | 0
5652 | 946.1464 | 481.86 | 2115.6329 | 982.861 | 0 | 0 | 1132.7719 | 0 | 0 | 0
5653 | 1239.5337 | 244.98 | 1063.5979 | 1063.5979 | 0 | 0 | 0 | 136.814 | 0 | 81.9129
5654 | 1165.2976 | 297.22 | 1301.6774 | 1210.5171 | -91.1603 | 0 | 0 | 0 | 0 | 0
5655 | 1376.3664 | 51.05 | 193.4826 | 193.4826 | 0 | 0 | 0 | 1190.112 | 0 | 0
5656 | 885.9086 | 31.38 | 109.0246 | 109.0246 | 0 | 0 | 0 | 780.957 | 0 | 0
5657 | 1355.6593 | 12.73 | 29.02 | 29.02 | 0 | 0 | 0 | 1327.723 | 0 | 0
5658 | 1090.8972 | 21.55 | 65.7698 | 65.7698 | 0 | 0 | 0 | 1027.584 | 0 | 0
5659 | 1122.6312 | 0 | 0 | 0 | 0 | 0 | 0 | 1122.631 | 0 | 0
5660 | 1206.4888 | 0 | 0 | 0 | 0 | 0 | 0 | 1206.489 | 0 | 0
5661 | 1114.0497 | 0 | 0 | 0 | 0 | 0 | 0 | 1114.05 | 0 | 0
5662 | 1332.3971 | 0 | 0 | 0 | 0 | 0 | 0 | 1189.089 | 0 | 148.869
5663 | 1107.6746 | 0 | 0 | 0 | 0 | 0 | 0 | 515.675 | 0 | 614.9724
5664 | 162.5652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 168.8733
5665 | 108.3768 | 0 | 0 | 0 | 0 | 0 | 0 | 108.377 | 0 | 0
5666 | 94.0328 | 0 | 0 | 0 | 0 | 0 | 0 | 94.033 | 0 | 0
5667 | 105.1892 | 0 | 0 | 0 | 0 | 0 | 0 | 105.189 | 0 | 0
5668 | 101.2048 | 0 | 0 | 0 | 0 | 0 | 0 | 101.205 | 0 | 0
5669 | 105.1892 | 0 | 0 | 0 | 0 | 0 | 0 | 105.189 | 0 | 0
5670 | 94.8297 | 0 | 0 | 0 | 0 | 0 | 0 | 94.83 | 0 | 0
5671 | 86.8608 | 41.16 | 156.2425 | 90.2316 | -66.0108 | 0 | 0 | 0 | 0 | 0
5672 | 82.0825 | 338.39 | 1519.9635 | 85.2682 | -614.9724 | 0 | 819.7229 | 0 | 0 | 0
5673 | 832.2691 | 574.99 | 2623.9647 | 864.565 | -357.0278 | 0 | 1402.3719 | 0 | 0 | 0
5674 | 1035.63 | 773.15 | 3450.0503 | 1075.8174 | 0 | 0 | 2374.2329 | 0 | 0 | 0
5675 | 888.0562 | 905.16 | 3967.614 | 922.5168 | 0 | 0 | 3045.0972 | 0 | 0 | 0
5676 | 1347.1615 | 975.26 | 4236.8254 | 1399.4383 | 0 | 0 | 2837.3871 | 0 | 0 | 0
5677 | 1336.4483 | 968.49 | 4209.9515 | 1388.3085 | 0 | 0 | 2821.643 | 0 | 0 | 0
5678 | 1189.8149 | 886.98 | 3892.7899 | 1235.9855 | 0 | 0 | 2656.8044 | 0 | 0 | 0
5679 | 1475.6089 | 539.89 | 2387.1982 | 1532.8696 | 0 | 0 | 854.3286 | 0 | 0 | 0
5680 | 1639.9322 | 532.94 | 2431.0265 | 1703.5691 | 0 | 0 | 727.4573 | 0 | 0 | 0
5681 | 1706.823 | 220.52 | 986.3191 | 986.3191 | 0 | 0 | 0 | 757.348 | 0 | 0
5682 | 1428.5228 | 34.29 | 121.5859 | 121.5859 | 0 | 0 | 0 | 1311.479 | 0 | 0
5683 | 1533.5207 | 0 | 0 | 0 | 0 | 0 | 0 | 1533.521 | 0 | 0
5684 | 1655.1368 | 0 | 0 | 0 | 0 | 0 | 0 | 1655.137 | 0 | 0
5685 | 1609.7142 | 0 | 0 | 0 | 0 | 0 | 0 | 1609.714 | 0 | 0
5686 | 1722.0755 | 0 | 0 | 0 | 0 | 0 | 0 | 1416.202 | 0 | 317.7434
5687 | 1463.8837 | 0 | 0 | 0 | 0 | 0 | 0 | 871.884 | 0 | 614.9724
5688 | 1754.7479 | 0 | 0 | 0 | 0 | 0 | 0 | 1754.748 | 0 | 0
5689 | 1349.1318 | 0 | 0 | 0 | 0 | 0 | 0 | 1349.132 | 0 | 0
5690 | 1326.022 | 0 | 0 | 0 | 0 | 0 | 0 | 1326.022 | 0 | 0
5691 | 1411.2891 | 0 | 0 | 0 | 0 | 0 | 0 | 1411.289 | 0 | 0
5692 | 1294.1465 | 0 | 0 | 0 | 0 | 0 | 0 | 1294.146 | 0 | 0
5693 | 1482.2121 | 0 | 0 | 0 | 0 | 0 | 0 | 1482.212 | 0 | 0
5694 | 1483.009 | 0 | 0 | 0 | 0 | 0 | 0 | 1483.009 | 0 | 0
5695 | 1287.7714 | 77.24 | 310.479 | 310.479 | 0 | 0 | 0 | 988.89 | 0 | 0
5696 | 1284.4902 | 249.61 | 1126.4394 | 1126.4394 | 0 | 0 | 0 | 200.129 | 0 | 0
5697 | 1520.7915 | 414.87 | 1860.9231 | 1579.806 | -281.1172 | 0 | 0 | 0 | 0 | 0
5698 | 1079.7616 | 549.34 | 2425.3193 | 1121.6609 | -614.9724 | 0 | 688.686 | 0 | 0 | 0
5699 | 1397.4561 | 670.39 | 2923.5799 | 1451.6839 | -141.9215 | 0 | 1329.9744 | 0 | 0 | 0
5700 | 1300.2516 | 816.77 | 3521.1243 | 1350.7069 | 0 | 0 | 2170.4174 | 0 | 0 | 0
5701 | 1512.0147 | 760.19 | 3287.3381 | 1570.6884 | 0 | 0 | 1716.6498 | 0 | 0 | 0
5702 | 1330.6818 | 654.22 | 2852.5765 | 1382.3188 | 0 | 0 | 1470.2578 | 0 | 0 | 0
5703 | 1355.5716 | 577.62 | 2543.6526 | 1408.1736 | 0 | 0 | 1135.479 | 0 | 0 | 0
5704 | 1598.3855 | 255.92 | 1136.8783 | 1136.8783 | 0 | 0 | 0 | 503.976 | 0 | 0
5705 | 1495.9604 | 125.31 | 545.5719 | 545.5719 | 0 | 0 | 0 | 970.768 | 0 | 0
5706 | 1298.7306 | 45.02 | 168.7092 | 168.7092 | 0 | 0 | 0 | 1136.324 | 0 | 0
5707 | 1402.2623 | 0 | 0 | 0 | 0 | 0 | 0 | 1402.262 | 0 | 0
5708 | 1392.1637 | 0 | 0 | 0 | 0 | 0 | 0 | 1392.164 | 0 | 0
5709 | 1202.5043 | 0 | 0 | 0 | 0 | 0 | 0 | 1202.504 | 0 | 0
5710 | 1352.3193 | 0 | 0 | 0 | 0 | 0 | 0 | 1046.446 | 0 | 317.7434
5711 | 1295.7403 | 0 | 0 | 0 | 0 | 0 | 0 | 703.74 | 0 | 614.9724
5712 | 1243.9425 | 0 | 0 | 0 | 0 | 0 | 0 | 1243.943 | 0 | 0
5713 | 1173.8164 | 0 | 0 | 0 | 0 | 0 | 0 | 1173.816 | 0 | 0
5714 | 1220.8328 | 0 | 0 | 0 | 0 | 0 | 0 | 1220.833 | 0 | 0
5715 | 1220.0359 | 0 | 0 | 0 | 0 | 0 | 0 | 1220.036 | 0 | 0
5716 | 899.6868 | 0 | 0 | 0 | 0 | 0 | 0 | 899.687 | 0 | 0
5717 | 1117.2373 | 0 | 0 | 0 | 0 | 0 | 0 | 1117.237 | 0 | 0
5718 | 1305.3029 | 0 | 0 | 0 | 0 | 0 | 0 | 1305.303 | 0 | 0
5719 | 1147.519 | 97.42 | 382.3518 | 382.3518 | 0 | 0 | 0 | 779.45 | 0 | 0
5720 | 929.5402 | 298.44 | 1356.1575 | 965.6116 | -390.5459 | 0 | 0 | 0 | 0 | 0
5721 | 1210.9693 | 393.85 | 1776.4122 | 1257.9614 | -518.4508 | 0 | 0 | 0 | 0 | 0
5722 | 1135.0278 | 559.41 | 2481.7565 | 1179.0725 | -129.0133 | 0 | 1173.6707 | 0 | 0 | 0
5723 | 1545.1075 | 916.28 | 4023.4892 | 1605.0645 | 0 | 0 | 2418.4247 | 0 | 0 | 0
5724 | 1332.948 | 386.41 | 1686.9275 | 1384.6727 | 0 | 0 | 302.2548 | 0 | 0 | 0
5725 | 1136.3975 | 981.7 | 4243.7148 | 1180.4946 | 0 | 0 | 3063.2202 | 0 | 0 | 0
5726 | 1310.148 | 610.95 | 2653.9903 | 1360.988 | 0 | 0 | 1293.0023 | 0 | 0 | 0
5727 | 1355.743 | 738.32 | 3267.4492 | 1408.3523 | 0 | 0 | 1859.0969 | 0 | 0 | 0
5728 | 1265.597 | 471.25 | 2106.5132 | 1314.7082 | 0 | 0 | 791.805 | 0 | 0 | 0
5729 | 1372.3541 | 20.57 | 63.1199 | 63.1199 | 0 | 0 | 0 | 1311.592 | 0 | 0
5730 | 1424.6399 | 57.39 | 213.0516 | 213.0516 | 0 | 0 | 0 | 1219.547 | 0 | 0
5731 | 1131.4817 | 0 | 0 | 0 | 0 | 0 | 0 | 1131.482 | 0 | 0
5732 | 1318.85 | 0 | 0 | 0 | 0 | 0 | 0 | 1318.85 | 0 | 0
5733 | 1212.067 | 0 | 0 | 0 | 0 | 0 | 0 | 1212.067 | 0 | 0
5734 | 1363.4758 | 0 | 0 | 0 | 0 | 0 | 0 | 1057.602 | 0 | 317.7434
5735 | 1298.9278 | 0 | 0 | 0 | 0 | 0 | 0 | 706.928 | 0 | 614.9724
5736 | 502.0396 | 0 | 0 | 0 | 0 | 0 | 0 | 502.04 | 0 | 0
5737 | 307.5989 | 0 | 0 | 0 | 0 | 0 | 0 | 307.599 | 0 | 0
5738 | 222.3318 | 0 | 0 | 0 | 0 | 0 | 0 | 222.332 | 0 | 0
5739 | 304.4113 | 0 | 0 | 0 | 0 | 0 | 0 | 304.411 | 0 | 0
5740 | 233.4883 | 0 | 0 | 0 | 0 | 0 | 0 | 233.488 | 0 | 0
5741 | 283.6922 | 0 | 0 | 0 | 0 | 0 | 0 | 283.692 | 0 | 0
5742 | 279.7078 | 0 | 0 | 0 | 0 | 0 | 0 | 279.708 | 0 | 0
5743 | 278.114 | 105.44 | 377.993 | 288.9061 | -89.0869 | 0 | 0 | 0 | 0 | 0
5744 | 207.0754 | 338.97 | 1527.0305 | 215.1115 | -614.9724 | 0 | 696.9466 | 0 | 0 | 0
5745 | 1378.0269 | 364.27 | 1627.0362 | 1431.501 | -195.5353 | 0 | 0 | 0 | 0 | 0
5746 | 1300.4519 | 774.36 | 3399.0128 | 1350.9157 | -138.4166 | 0 | 1909.6805 | 0 | 0 | 0
5747 | 1608.7589 | 915.67 | 3930.297 | 1671.1865 | 0 | 0 | 2259.1105 | 0 | 0 | 0
5748 | 1772.0822 | 984.34 | 4178.483 | 1840.8472 | 0 | 0 | 2337.6358 | 0 | 0 | 0
5749 | 1617.9401 | 836.25 | 3532.521 | 1680.7238 | 0 | 0 | 1851.7972 | 0 | 0 | 0
5750 | 1533.0237 | 554.44 | 2394.5436 | 1592.5126 | 0 | 0 | 802.031 | 0 | 0 | 0
5751 | 1780.7354 | 582.69 | 2539.1172 | 1849.837 | 0 | 0 | 689.2802 | 0 | 0 | 0
5752 | 1349.0361 | 73.47 | 297.2851 | 297.2851 | 0 | 0 | 0 | 1062.856 | 0 | 0
5753 | 1613.9387 | 90.32 | 380.0987 | 380.0987 | 0 | 0 | 0 | 1248.039 | 0 | 0
5754 | 1295.9295 | 23.51 | 73.2918 | 73.2918 | 0 | 0 | 0 | 1225.375 | 0 | 0
5755 | 1388.6465 | 0 | 0 | 0 | 0 | 0 | 0 | 1388.646 | 0 | 0
5756 | 1267.0523 | 0 | 0 | 0 | 0 | 0 | 0 | 1267.052 | 0 | 0
5757 | 1465.4775 | 0 | 0 | 0 | 0 | 0 | 0 | 1465.477 | 0 | 0
5758 | 1438.3833 | 0 | 0 | 0 | 0 | 0 | 0 | 1132.51 | 0 | 317.7434
5759 | 1352.3193 | 0 | 0 | 0 | 0 | 0 | 0 | 760.319 | 0 | 614.9724
5760 | 574.5564 | 0 | 0 | 0 | 0 | 0 | 0 | 574.556 | 0 | 0
5761 | 496.4614 | 0 | 0 | 0 | 0 | 0 | 0 | 496.461 | 0 | 0
5762 | 496.4614 | 0 | 0 | 0 | 0 | 0 | 0 | 496.461 | 0 | 0
5763 | 502.0396 | 0 | 0 | 0 | 0 | 0 | 0 | 502.04 | 0 | 0
5764 | 419.9601 | 0 | 0 | 0 | 0 | 0 | 0 | 419.96 | 0 | 0
5765 | 483.7112 | 0 | 0 | 0 | 0 | 0 | 0 | 483.711 | 0 | 0
5766 | 465.3827 | 0 | 0 | 0 | 0 | 0 | 0 | 465.383 | 0 | 0
5767 | 470.1641 | 78.53 | 315.4881 | 315.4881 | 0 | 0 | 0 | 166.461 | 0 | 0
5768 | 384.0224 | 250.94 | 1131.8744 | 398.9239 | -614.9724 | 0 | 117.9781 | 0 | 0 | 0
5769 | 1040.75 | 397.61 | 1785.2119 | 1081.136 | -423.0387 | 0 | 281.0372 | 0 | 0 | 0
5770 | 1686.0651 | 512.75 | 2268.5574 | 1751.4923 | 0 | 0 | 517.0651 | 0 | 0 | 0
5771 | 1865.857 | 713.26 | 3109.0252 | 1938.2611 | 0 | 0 | 1170.7641 | 0 | 0 | 0
5772 | 1807.6941 | 610.58 | 2661.4417 | 1877.8411 | 0 | 0 | 783.6005 | 0 | 0 | 0
5773 | 1599.518 | 980.3 | 4264.8815 | 1661.5869 | 0 | 0 | 2603.2946 | 0 | 0 | 0
5774 | 1650.484 | 502.31 | 2207.1931 | 1714.5306 | 0 | 0 | 492.6625 | 0 | 0 | 0
5775 | 1952.3423 | 490.41 | 2174.933 | 2028.1032 | 0 | 0 | 146.8299 | 0 | 0 | 0
5776 | 1917.6398 | 186.47 | 821.5252 | 821.5252 | 0 | 0 | 0 | 1126.802 | 0 | 0
5777 | 1638.3992 | 32.34 | 116.3285 | 116.3285 | 0 | 0 | 0 | 1526.416 | 0 | 0
5778 | 1789.8428 | 34.26 | 120.5336 | 120.5336 | 0 | 0 | 0 | 1673.812 | 0 | 0
5779 | 1557.9215 | 0 | 0 | 0 | 0 | 0 | 0 | 1557.921 | 0 | 0
5780 | 1417.6642 | 0 | 0 | 0 | 0 | 0 | 0 | 1417.664 | 0 | 0
5781 | 1755.5448 | 0 | 0 | 0 | 0 | 0 | 0 | 1755.545 | 0 | 0
5782 | 1519.6659 | 0 | 0 | 0 | 0 | 0 | 0 | 1213.792 | 0 | 317.7434
5783 | 1699.7626 | 0 | 0 | 0 | 0 | 0 | 0 | 1107.763 | 0 | 614.9724
5784 | 524.3525 | 0 | 0 | 0 | 0 | 0 | 0 | 524.352 | 0 | 0
5785 | 475.7423 | 0 | 0 | 0 | 0 | 0 | 0 | 475.742 | 0 | 0
5786 | 485.3049 | 0 | 0 | 0 | 0 | 0 | 0 | 485.305 | 0 | 0
5787 | 448.6481 | 0 | 0 | 0 | 0 | 0 | 0 | 448.648 | 0 | 0
5788 | 408.8037 | 0 | 0 | 0 | 0 | 0 | 0 | 408.804 | 0 | 0
5789 | 496.4614 | 0 | 0 | 0 | 0 | 0 | 0 | 496.461 | 0 | 0
5790 | 478.9298 | 0 | 0 | 0 | 0 | 0 | 0 | 478.93 | 0 | 0
5791 | 400.8348 | 64.89 | 260.8314 | 260.8314 | 0 | 0 | 0 | 149.747 | 0 | 0
5792 | 182.8679 | 212.8 | 952.0594 | 189.9641 | -614.9724 | 0 | 147.1228 | 0 | 0 | 0
5793 | 1356.1404 | 390.21 | 1736.4452 | 1408.7657 | -327.6795 | 0 | 0 | 0 | 0 | 0
5794 | 1493.0687 | 563.25 | 2450.4542 | 1551.0072 | -95.3592 | 0 | 804.0879 | 0 | 0 | 0
5795 | 1601.832 | 690.08 | 2944.9533 | 1663.9907 | 0 | 0 | 1280.9626 | 0 | 0 | 0
5796 | 1394.3631 | 739.92 | 3131.6047 | 1448.4709 | 0 | 0 | 1683.1338 | 0 | 0 | 0
5797 | 1717.3001 | 726.27 | 3084.1334 | 1783.9394 | 0 | 0 | 1300.194 | 0 | 0 | 0
5798 | 1250.3824 | 747.47 | 3192.8329 | 1298.9038 | 0 | 0 | 1893.9291 | 0 | 0 | 0
5799 | 1121.1221 | 612.04 | 2668.8348 | 1164.6279 | 0 | 0 | 1504.2069 | 0 | 0 | 0
5800 | 1607.7798 | 257.03 | 1137.2679 | 1137.2679 | 0 | 0 | 0 | 512.995 | 0 | 0
5801 | 1448.2039 | 70.27 | 288.4023 | 288.4023 | 0 | 0 | 0 | 1170.575 | 0 | 0
5802 | 1364.7797 | 18.61 | 52.0909 | 52.0909 | 0 | 0 | 0 | 1314.635 | 0 | 0
5803 | 1446.5205 | 0 | 0 | 0 | 0 | 0 | 0 | 1446.52 | 0 | 0
5804 | 1027.9858 | 0 | 0 | 0 | 0 | 0 | 0 | 1027.986 | 0 | 0
5805 | 1208.0826 | 0 | 0 | 0 | 0 | 0 | 0 | 1208.083 | 0 | 0
5806 | 1391.3668 | 0 | 0 | 0 | 0 | 0 | 0 | 1085.493 | 0 | 317.7434
5807 | 960.2503 | 0 | 0 | 0 | 0 | 0 | 0 | 368.25 | 0 | 614.9724
5808 | 1379.4135 | 0 | 0 | 0 | 0 | 0 | 0 | 1379.414 | 0 | 0
5809 | 1115.6435 | 0 | 0 | 0 | 0 | 0 | 0 | 1115.644 | 0 | 0
5810 | 1562.6978 | 0 | 0 | 0 | 0 | 0 | 0 | 1562.698 | 0 | 0
5811 | 1405.7108 | 0 | 0 | 0 | 0 | 0 | 0 | 1405.711 | 0 | 0
5812 | 1476.6339 | 0 | 0 | 0 | 0 | 0 | 0 | 1476.634 | 0 | 0
5813 | 1177.8008 | 0 | 0 | 0 | 0 | 0 | 0 | 1177.801 | 0 | 0
5814 | 1127.5968 | 0 | 0 | 0 | 0 | 0 | 0 | 1127.597 | 0 | 0
5815 | 1133.1751 | 82.89 | 331.9469 | 331.9469 | 0 | 0 | 0 | 813.628 | 0 | 0
5816 | 181.302 | 350.1 | 1565.5421 | 188.3374 | -614.9724 | 0 | 762.2323 | 0 | 0 | 0
5817 | 479.2755 | 390.48 | 1733.0504 | 497.8742 | -423.0387 | 0 | 812.1376 | 0 | 0 | 0
5818 | 453.9145 | 789.12 | 3412.5848 | 471.528 | 0 | 0 | 2941.0567 | 0 | 0 | 0
5819 | 496.7951 | 927.72 | 3904.1565 | 516.073 | 0 | 0 | 3388.0835 | 0 | 0 | 0
5820 | 414.3719 | 997.29 | 4143.2717 | 430.4516 | 0 | 0 | 3712.8201 | 0 | 0 | 0
5821 | 318.7732 | 989.49 | 4120.8688 | 331.1429 | 0 | 0 | 3789.7259 | 0 | 0 | 0
5822 | 334.3604 | 898.49 | 3801.4956 | 347.3348 | 0 | 0 | 3454.1608 | 0 | 0 | 0
5823 | 406.4429 | 746.79 | 3239.0566 | 422.2149 | 0 | 0 | 2816.8417 | 0 | 0 | 0
5824 | 328.2074 | 537.32 | 2405.6204 | 340.944 | 0 | 0 | 2064.6764 | 0 | 0 | 0
5825 | 412.0002 | 295.9 | 1284.5153 | 427.9886 | 0 | 0 | 856.5267 | 0 | 0 | 0
5826 | 284.013 | 69.31 | 211.5495 | 211.5495 | 0 | 0 | 0 | 80.366 | 0 | 0
5827 | 303.3544 | 0 | 0 | 0 | 0 | 0 | 0 | 303.354 | 0 | 0
5828 | 260.5825 | 0 | 0 | 0 | 0 | 0 | 0 | 260.582 | 0 | 0
5829 | 203.2065 | 0 | 0 | 0 | 0 | 0 | 0 | 203.206 | 0 | 0
5830 | 329.9117 | 0 | 0 | 0 | 0 | 0 | 0 | 51.103 | 0 | 289.6281
5831 | 295.6455 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 307.1185
5832 | 301.2237 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 312.9129
5833 | 332.0389 | 0 | 0 | 0 | 0 | 0 | 0 | 332.039 | 0 | 0
5834 | 303.4149 | 0 | 0 | 0 | 0 | 0 | 0 | 303.415 | 0 | 0
5835 | 303.4149 | 0 | 0 | 0 | 0 | 0 | 0 | 303.415 | 0 | 0
5836 | 323.0428 | 0 | 0 | 0 | 0 | 0 | 0 | 323.043 | 0 | 0
5837 | 232.2637 | 0 | 0 | 0 | 0 | 0 | 0 | 232.264 | 0 | 0
5838 | 282.1513 | 0 | 0 | 0 | 0 | 0 | 0 | 282.151 | 0 | 0
5839 | 262.5234 | 62.41 | 249.6539 | 249.6539 | 0 | 0 | 0 | 0 | 0 | 23.0573
5840 | 251.6319 | 238.53 | 1078.8912 | 261.3965 | -614.9724 | 0 | 202.5223 | 0 | 0 | 0
5841 | 470.5752 | 383.66 | 1726.8529 | 488.8366 | -423.0387 | 0 | 814.9776 | 0 | 0 | 0
5842 | 1198.9713 | 453.8 | 2011.9072 | 1245.4968 | 0 | 0 | 766.4104 | 0 | 0 | 0
5843 | 1601.2271 | 624.73 | 2733.3031 | 1663.3622 | 0 | 0 | 1069.9408 | 0 | 0 | 0
5844 | 1241.291 | 706.99 | 3070.8803 | 1289.459 | 0 | 0 | 1781.4213 | 0 | 0 | 0
5845 | 1602.0439 | 762.51 | 3306.6121 | 1664.2109 | 0 | 0 | 1642.4012 | 0 | 0 | 0
5846 | 1542.9506 | 735.07 | 3206.9253 | 1602.8238 | 0 | 0 | 1604.1015 | 0 | 0 | 0
5847 | 1640.668 | 511.13 | 2266.192 | 1704.3337 | 0 | 0 | 561.8583 | 0 | 0 | 0
5848 | 1242.7375 | 449.53 | 2025.929 | 1290.9611 | 0 | 0 | 734.9679 | 0 | 0 | 0
5849 | 1329.2874 | 250.85 | 1122.8139 | 1122.8139 | 0 | 0 | 0 | 248.416 | 0 | 0
5850 | 1176.7039 | 61.02 | 215.2819 | 215.2819 | 0 | 0 | 0 | 969.464 | 0 | 0
5851 | 1489.1425 | 0 | 0 | 0 | 0 | 0 | 0 | 1489.142 | 0 | 0
5852 | 1527.7062 | 0 | 0 | 0 | 0 | 0 | 0 | 1527.706 | 0 | 0
5853 | 1849.1134 | 0 | 0 | 0 | 0 | 0 | 0 | 1849.113 | 0 | 0
5854 | 1687.1831 | 0 | 0 | 0 | 0 | 0 | 0 | 1381.309 | 0 | 317.7434
5855 | 1236.5588 | 0 | 0 | 0 | 0 | 0 | 0 | 644.559 | 0 | 614.9724
5856 | 1050.9114 | 0 | 0 | 0 | 0 | 0 | 0 | 1050.911 | 0 | 0
5857 | 1364.9581 | 0 | 0 | 0 | 0 | 0 | 0 | 1364.958 | 0 | 0
5858 | 1355.1441 | 0 | 0 | 0 | 0 | 0 | 0 | 1355.144 | 0 | 0
5859 | 1388.6752 | 0 | 0 | 0 | 0 | 0 | 0 | 1388.675 | 0 | 0
5860 | 1544.0628 | 0 | 0 | 0 | 0 | 0 | 0 | 1544.063 | 0 | 0
5861 | 1248.0084 | 0 | 0 | 0 | 0 | 0 | 0 | 1248.008 | 0 | 0
5862 | 1493.3574 | 0 | 0 | 0 | 0 | 0 | 0 | 1493.357 | 0 | 0
5863 | 1527.7062 | 108.62 | 396.3861 | 396.3861 | 0 | 0 | 0 | 1146.127 | 0 | 0
5864 | 1240.9649 | 345.18 | 1565.4414 | 1289.1203 | -276.321 | 0 | 0 | 0 | 0 | 0
5865 | 1314.0022 | 463.38 | 2092.6628 | 1364.9915 | -614.9724 | 0 | 112.6989 | 0 | 0 | 0
5866 | 1895.8186 | 783.88 | 3511.4083 | 1969.3858 | -146.7177 | 0 | 1395.3049 | 0 | 0 | 0
5867 | 1738.3935 | 727.37 | 3183.3112 | 1805.8519 | 0 | 0 | 1377.4593 | 0 | 0 | 0
5868 | 1628.6735 | 832.62 | 3609.5743 | 1691.8732 | 0 | 0 | 1917.7011 | 0 | 0 | 0
5869 | 1331.8493 | 981.99 | 4286.8698 | 1383.5321 | 0 | 0 | 2903.3377 | 0 | 0 | 0
5870 | 1502.9147 | 879.52 | 3869.4293 | 1561.2342 | 0 | 0 | 2308.1951 | 0 | 0 | 0
5871 | 1067.9509 | 727.61 | 3254.7643 | 1109.3926 | 0 | 0 | 2145.3718 | 0 | 0 | 0
5872 | 1186.9605 | 519.07 | 2368.5922 | 1233.0197 | 0 | 0 | 1135.5725 | 0 | 0 | 0
5873 | 1465.9979 | 282.56 | 1245.2693 | 1245.2693 | 0 | 0 | 0 | 267.246 | 0 | 0
5874 | 1552.9578 | 63.25 | 211.2659 | 211.2659 | 0 | 0 | 0 | 1349.584 | 0 | 0
5875 | 1503.1713 | 0 | 0 | 0 | 0 | 0 | 0 | 1503.171 | 0 | 0
5876 | 1143.3262 | 0 | 0 | 0 | 0 | 0 | 0 | 1143.326 | 0 | 0
5877 | 1723.9854 | 0 | 0 | 0 | 0 | 0 | 0 | 1723.985 | 0 | 0
5878 | 1668.373 | 0 | 0 | 0 | 0 | 0 | 0 | 1362.499 | 0 | 317.7434
5879 | 1373.1364 | 0 | 0 | 0 | 0 | 0 | 0 | 781.136 | 0 | 614.9724
5880 | 1233.2875 | 0 | 0 | 0 | 0 | 0 | 0 | 1233.287 | 0 | 0
5881 | 1690.4544 | 0 | 0 | 0 | 0 | 0 | 0 | 1690.454 | 0 | 0
5882 | 1819.6715 | 0 | 0 | 0 | 0 | 0 | 0 | 1819.672 | 0 | 0
5883 | 1252.9154 | 0 | 0 | 0 | 0 | 0 | 0 | 1252.915 | 0 | 0
5884 | 1363.3224 | 0 | 0 | 0 | 0 | 0 | 0 | 1363.322 | 0 | 0
5885 | 1499.0822 | 0 | 0 | 0 | 0 | 0 | 0 | 1499.082 | 0 | 0
5886 | 1406.6674 | 0 | 0 | 0 | 0 | 0 | 0 | 1406.667 | 0 | 0
5887 | 1239.0123 | 111.44 | 403.2048 | 403.2048 | 0 | 0 | 0 | 850.869 | 0 | 0
5888 | 1144.3567 | 348.18 | 1576.2699 | 1188.7624 | -387.5074 | 0 | 0 | 0 | 0 | 0
5889 | 1160.5057 | 587.26 | 2677.8537 | 1205.5391 | -614.9724 | 0 | 857.3422 | 0 | 0 | 0
5890 | 1535.5758 | 783.72 | 3482.2813 | 1595.1636 | -35.5313 | 0 | 1851.5864 | 0 | 0 | 0
5891 | 1778.9231 | 921.05 | 4013.1282 | 1847.9537 | 0 | 0 | 2165.1745 | 0 | 0 | 0
5892 | 1434.3111 | 986.85 | 4252.1073 | 1489.9691 | 0 | 0 | 2762.1382 | 0 | 0 | 0
5893 | 1226.9442 | 977.6 | 4211.9512 | 1274.5563 | 0 | 0 | 2937.3949 | 0 | 0 | 0
5894 | 1067.315 | 893.36 | 3882.4289 | 1108.7319 | 0 | 0 | 2773.697 | 0 | 0 | 0
5895 | 1327.1212 | 737.88 | 3268.9045 | 1378.6196 | 0 | 0 | 1890.285 | 0 | 0 | 0
5896 | 1593.7705 | 528.93 | 2401.2315 | 1655.6158 | 0 | 0 | 745.6156 | 0 | 0 | 0
5897 | 1265.787 | 191.95 | 851.4625 | 851.4625 | 0 | 0 | 0 | 446.131 | 0 | 0
5898 | 1411.0786 | 44.37 | 159.3589 | 159.3589 | 0 | 0 | 0 | 1257.673 | 0 | 0
5899 | 906.1208 | 0 | 0 | 0 | 0 | 0 | 0 | 906.121 | 0 | 0
5900 | 1138.4192 | 0 | 0 | 0 | 0 | 0 | 0 | 1138.419 | 0 | 0
5901 | 1154.7758 | 0 | 0 | 0 | 0 | 0 | 0 | 1154.776 | 0 | 0
5902 | 1472.9116 | 0 | 0 | 0 | 0 | 0 | 0 | 1167.038 | 0 | 317.7434
5903 | 1362.5046 | 0 | 0 | 0 | 0 | 0 | 0 | 770.505 | 0 | 614.9724
5904 | 141.4846 | 0 | 0 | 0 | 0 | 0 | 0 | 141.485 | 0 | 0
5905 | 99.7752 | 0 | 0 | 0 | 0 | 0 | 0 | 99.775 | 0 | 0
5906 | 96.5039 | 0 | 0 | 0 | 0 | 0 | 0 | 96.504 | 0 | 0
5907 | 105.5001 | 0 | 0 | 0 | 0 | 0 | 0 | 105.5 | 0 | 0
5908 | 94.8683 | 0 | 0 | 0 | 0 | 0 | 0 | 94.868 | 0 | 0
5909 | 100.5931 | 0 | 0 | 0 | 0 | 0 | 0 | 100.593 | 0 | 0
5910 | 91.5969 | 0 | 0 | 0 | 0 | 0 | 0 | 91.597 | 0 | 0
5911 | 86.69 | 110.2 | 401.7494 | 90.054 | -311.6954 | 0 | 0 | 0 | 0 | 0
5912 | 88.3635 | 345.12 | 1559.9419 | 91.7929 | -614.9724 | 0 | 853.1766 | 0 | 0 | 0
5913 | 674.8497 | 581.8 | 2649.8798 | 701.0363 | -111.3432 | 0 | 1837.5002 | 0 | 0 | 0
5914 | 1069.3668 | 495.28 | 2191.93 | 1110.8635 | 0 | 0 | 1081.0664 | 0 | 0 | 0
5915 | 1034.0283 | 919.62 | 4012.0281 | 1074.1532 | 0 | 0 | 2937.8749 | 0 | 0 | 0
5916 | 1101.8888 | 984.29 | 4252.716 | 1144.6475 | 0 | 0 | 3108.0685 | 0 | 0 | 0
5917 | 1309.4418 | 972.92 | 4199.23 | 1360.2546 | 0 | 0 | 2838.9755 | 0 | 0 | 0
5918 | 1334.591 | 865.21 | 3764.6928 | 1386.3795 | 0 | 0 | 2378.3133 | 0 | 0 | 0
5919 | 1249.9334 | 625.86 | 2748.2598 | 1298.4374 | 0 | 0 | 1449.8224 | 0 | 0 | 0
5920 | 1409.4378 | 502.66 | 2275.1039 | 1464.1309 | 0 | 0 | 810.9731 | 0 | 0 | 0
5921 | 1475.0421 | 269.46 | 1187.6499 | 1187.6499 | 0 | 0 | 0 | 331.757 | 0 | 0
5922 | 1347.0834 | 44.76 | 159.6664 | 159.6664 | 0 | 0 | 0 | 1193.382 | 0 | 0
5923 | 1438.5628 | 0 | 0 | 0 | 0 | 0 | 0 | 1438.563 | 0 | 0
5924 | 1652.8342 | 0 | 0 | 0 | 0 | 0 | 0 | 1652.834 | 0 | 0
5925 | 1743.6133 | 0 | 0 | 0 | 0 | 0 | 0 | 1743.613 | 0 | 0
5926 | 1660.1947 | 0 | 0 | 0 | 0 | 0 | 0 | 1354.321 | 0 | 317.7434
5927 | 1413.2101 | 0 | 0 | 0 | 0 | 0 | 0 | 821.21 | 0 | 614.9724
5928 | 139.8489 | 0 | 0 | 0 | 0 | 0 | 0 | 139.849 | 0 | 0
5929 | 107.1357 | 0 | 0 | 0 | 0 | 0 | 0 | 107.136 | 0 | 0
5930 | 98.9574 | 0 | 0 | 0 | 0 | 0 | 0 | 98.957 | 0 | 0
5931 | 102.2287 | 0 | 0 | 0 | 0 | 0 | 0 | 102.229 | 0 | 0
5932 | 100.5931 | 0 | 0 | 0 | 0 | 0 | 0 | 100.593 | 0 | 0
5933 | 103.8644 | 0 | 0 | 0 | 0 | 0 | 0 | 103.864 | 0 | 0
5934 | 97.3218 | 0 | 0 | 0 | 0 | 0 | 0 | 97.322 | 0 | 0
5935 | 94.8683 | 8.81 | 12.2652 | 12.2652 | 0 | 0 | 0 | 83.061 | 0 | 0
5936 | 87.886 | 273.56 | 1235.8307 | 91.2964 | -614.9724 | 0 | 529.5619 | 0 | 0 | 0
5937 | 953.4016 | 244.18 | 1085.5852 | 990.3975 | -95.1878 | 0 | 0 | 0 | 0 | 0
5938 | 1414.2467 | 781.05 | 3450.5593 | 1469.1265 | -327.8509 | 0 | 1653.5819 | 0 | 0 | 0
5939 | 1289.2178 | 917.33 | 3980.8909 | 1339.2458 | 0 | 0 | 2641.6452 | 0 | 0 | 0
5940 | 1489.7845 | 797.3 | 3428.4525 | 1547.5957 | 0 | 0 | 1880.8568 | 0 | 0 | 0
5941 | 1378.1088 | 713.49 | 3087.7588 | 1431.5862 | 0 | 0 | 1656.1726 | 0 | 0 | 0
5942 | 1448.9237 | 797.91 | 3437.4236 | 1505.1481 | 0 | 0 | 1932.2755 | 0 | 0 | 0
5943 | 1588.6233 | 522.79 | 2310.5293 | 1650.2702 | 0 | 0 | 660.2591 | 0 | 0 | 0
5944 | 1511.5071 | 195.94 | 865.3192 | 865.3192 | 0 | 0 | 0 | 678.512 | 0 | 0
5945 | 1311.4301 | 106.6 | 459.1984 | 459.1984 | 0 | 0 | 0 | 869.385 | 0 | 0
5946 | 1754.8452 | 24.5 | 76.3501 | 76.3501 | 0 | 0 | 0 | 1681.348 | 0 | 0
5947 | 1257.345 | 0 | 0 | 0 | 0 | 0 | 0 | 1257.345 | 0 | 0
5948 | 847.2718 | 0 | 0 | 0 | 0 | 0 | 0 | 847.272 | 0 | 0
5949 | 1282.3573 | 0 | 0 | 0 | 0 | 0 | 0 | 1282.357 | 0 | 0
5950 | 1299.5317 | 0 | 0 | 0 | 0 | 0 | 0 | 993.658 | 0 | 317.7434
5951 | 1363.3224 | 0 | 0 | 0 | 0 | 0 | 0 | 771.322 | 0 | 614.9724
5952 | 1331.4271 | 0 | 0 | 0 | 0 | 0 | 0 | 1331.427 | 0 | 0
5953 | 1392.7643 | 0 | 0 | 0 | 0 | 0 | 0 | 1392.764 | 0 | 0
5954 | 954.4075 | 0 | 0 | 0 | 0 | 0 | 0 | 954.407 | 0 | 0
5955 | 1391.9465 | 0 | 0 | 0 | 0 | 0 | 0 | 1391.946 | 0 | 0
5956 | 1367.4116 | 0 | 0 | 0 | 0 | 0 | 0 | 1367.412 | 0 | 0
5957 | 1018.1982 | 0 | 0 | 0 | 0 | 0 | 0 | 1018.198 | 0 | 0
5958 | 1299.5317 | 0 | 0 | 0 | 0 | 0 | 0 | 1299.532 | 0 | 0
5959 | 1066.4502 | 78.34 | 316.8957 | 316.8957 | 0 | 0 | 0 | 761.392 | 0 | 0
5960 | 879.7304 | 354.39 | 1597.1935 | 913.8677 | -614.9724 | 0 | 68.3534 | 0 | 0 | 0
5961 | 1118.7892 | 593.73 | 2691.1006 | 1162.2033 | -423.0387 | 0 | 1105.8586 | 0 | 0 | 0
5962 | 1147.7987 | 791.72 | 3497.4686 | 1192.3391 | 0 | 0 | 2305.1296 | 0 | 0 | 0
5963 | 1167.7466 | 922.28 | 3995.6991 | 1213.0601 | 0 | 0 | 2782.639 | 0 | 0 | 0
5964 | 1009.8492 | 987.45 | 4241.7161 | 1049.0359 | 0 | 0 | 3192.6802 | 0 | 0 | 0
5965 | 1123.4907 | 977.24 | 4201.9382 | 1167.0878 | 0 | 0 | 3034.8504 | 0 | 0 | 0
5966 | 1352.7826 | 601.79 | 2617.0992 | 1405.2774 | 0 | 0 | 1211.8218 | 0 | 0 | 0
5967 | 1227.347 | 111.46 | 467.165 | 467.165 | 0 | 0 | 0 | 777.633 | 0 | 0
5968 | 1201.4218 | 36.28 | 131.0369 | 131.0369 | 0 | 0 | 0 | 1075.28 | 0 | 0
5969 | 1209.5909 | 13.71 | 33.3487 | 33.3487 | 0 | 0 | 0 | 1177.488 | 0 | 0
5970 | 1315.1216 | 4.89 | 0 | 0 | 0 | 0 | 0 | 1315.122 | 0 | 0
5971 | 1232.4093 | 0 | 0 | 0 | 0 | 0 | 0 | 1232.409 | 0 | 0
5972 | 1067.268 | 0 | 0 | 0 | 0 | 0 | 0 | 1067.268 | 0 | 0
5973 | 1498.2644 | 0 | 0 | 0 | 0 | 0 | 0 | 1498.264 | 0 | 0
5974 | 1077.8998 | 0 | 0 | 0 | 0 | 0 | 0 | 772.026 | 0 | 317.7434
5975 | 1290.5356 | 0 | 0 | 0 | 0 | 0 | 0 | 698.536 | 0 | 614.9724
5976 | 956.861 | 0 | 0 | 0 | 0 | 0 | 0 | 956.861 | 0 | 0
5977 | 1195.6673 | 0 | 0 | 0 | 0 | 0 | 0 | 1195.667 | 0 | 0
5978 | 1304.4387 | 0 | 0 | 0 | 0 | 0 | 0 | 1304.439 | 0 | 0
5979 | 1028.83 | 0 | 0 | 0 | 0 | 0 | 0 | 1028.83 | 0 | 0
5980 | 1461.462 | 0 | 0 | 0 | 0 | 0 | 0 | 1461.462 | 0 | 0
5981 | 1392.7643 | 0 | 0 | 0 | 0 | 0 | 0 | 1392.764 | 0 | 0
5982 | 1118.7913 | 0 | 0 | 0 | 0 | 0 | 0 | 1118.791 | 0 | 0
5983 | 1271.7255 | 43.12 | 165.438 | 165.438 | 0 | 0 | 0 | 1112.467 | 0 | 0
5984 | 186.0829 | 150 | 664.7509 | 193.3029 | -471.448 | 0 | 0 | 0 | 0 | 0
5985 | 155.6841 | 396.97 | 1783.4086 | 161.7253 | -566.5641 | 0 | 1055.1192 | 0 | 0 | 0
5986 | 185.2027 | 506.51 | 2236.0895 | 192.3898 | 0 | 0 | 2043.6998 | 0 | 0 | 0
5987 | 174.4073 | 686.72 | 2981.7145 | 181.1748 | 0 | 0 | 2800.5397 | 0 | 0 | 0
5988 | 189.5525 | 538.19 | 2342.6003 | 196.9075 | 0 | 0 | 2145.6928 | 0 | 0 | 0
5989 | 199.8194 | 263.85 | 1146.908 | 207.5729 | 0 | 0 | 939.335 | 0 | 0 | 0
5990 | 201.4499 | 546.76 | 2387.2336 | 209.2672 | 0 | 0 | 2177.9663 | 0 | 0 | 0
5991 | 132.424 | 401.76 | 1774.4717 | 137.5627 | 0 | 0 | 1636.909 | 0 | 0 | 0
5992 | 181.7586 | 55.68 | 218.8471 | 188.8111 | 0 | 0 | 30.036 | 0 | 0 | 0
5993 | 119.9634 | 144.99 | 637.3753 | 124.6181 | 0 | 0 | 512.7571 | 0 | 0 | 0
5994 | 101.4733 | 31.32 | 105.4408 | 105.4106 | 0 | 0 | 0.030125 | 0 | 0 | 0
5995 | 112.5998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 116.9694
5996 | 110.407 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 114.6913
5997 | 102.2287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.196
5998 | 93.2326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.8509
5999 | 102.2287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.196
6000 | 95.6861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.3991
6001 | 100.5931 | 0 | 0 | 0 | 0 | 0 | 0 | 100.593 | 0 | 0
6002 | 92.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 92.415 | 0 | 0
6003 | 98.9574 | 0 | 0 | 0 | 0 | 0 | 0 | 98.957 | 0 | 0
6004 | 93.2326 | 0 | 0 | 0 | 0 | 0 | 0 | 2.296 | 0 | 94.4647
6005 | 98.9574 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.797
6006 | 91.5969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.1514
6007 | 94.8683 | 78.23 | 318.5578 | 98.5493 | -220.0085 | 0 | 0 | 0 | 0 | 0
6008 | 88.6732 | 272.44 | 1241.2896 | 92.1139 | -614.9724 | 0 | 534.2033 | 0 | 0 | 0
6009 | 877.3751 | 601.38 | 2765.3273 | 911.4213 | -203.0313 | 0 | 1650.8747 | 0 | 0 | 0
6010 | 1234.046 | 335.97 | 1495.1423 | 1281.9328 | 0 | 0 | 213.2095 | 0 | 0 | 0
6011 | 1673.4272 | 652.41 | 2873.6248 | 1738.365 | 0 | 0 | 1135.2598 | 0 | 0 | 0
6012 | 1423.6773 | 470.67 | 2075.5475 | 1478.9224 | 0 | 0 | 596.625 | 0 | 0 | 0
6013 | 1772.2558 | 191.29 | 827.623 | 827.623 | 0 | 0 | 0 | 975.549 | 0 | 0
6014 | 1493.8665 | 150.52 | 645.105 | 645.105 | 0 | 0 | 0 | 872.859 | 0 | 0
6015 | 1557.6541 | 48.09 | 182.2936 | 182.2936 | 0 | 0 | 0 | 1382.171 | 0 | 0
6016 | 1584.9707 | 54.7 | 215.6185 | 215.6185 | 0 | 0 | 0 | 1377.407 | 0 | 0
6017 | 1772.4797 | 48.73 | 192.0927 | 192.0927 | 0 | 0 | 0 | 1587.563 | 0 | 0
6018 | 1755.7039 | 12.73 | 26.6246 | 26.6246 | 0 | 0 | 0 | 1730.074 | 0 | 0
6019 | 1611.083 | 0 | 0 | 0 | 0 | 0 | 0 | 1611.083 | 0 | 0
6020 | 1745.249 | 0 | 0 | 0 | 0 | 0 | 0 | 1745.249 | 0 | 0
6021 | 1431.2023 | 0 | 0 | 0 | 0 | 0 | 0 | 1431.202 | 0 | 0
6022 | 1315.8883 | 0 | 0 | 0 | 0 | 0 | 0 | 1010.015 | 0 | 317.7434
6023 | 1081.1711 | 0 | 0 | 0 | 0 | 0 | 0 | 489.171 | 0 | 614.9724
6024 | 1571.0512 | 0 | 0 | 0 | 0 | 0 | 0 | 1571.051 | 0 | 0
6025 | 1019.8339 | 0 | 0 | 0 | 0 | 0 | 0 | 1019.834 | 0 | 0
6026 | 1302.803 | 0 | 0 | 0 | 0 | 0 | 0 | 1302.803 | 0 | 0
6027 | 1215.2952 | 0 | 0 | 0 | 0 | 0 | 0 | 1215.295 | 0 | 0
6028 | 1135.9657 | 0 | 0 | 0 | 0 | 0 | 0 | 1135.966 | 0 | 0
6029 | 1096.7099 | 0 | 0 | 0 | 0 | 0 | 0 | 1096.71 | 0 | 0
6030 | 1092.6207 | 0 | 0 | 0 | 0 | 0 | 0 | 1092.621 | 0 | 0
6031 | 1315.8883 | 101.12 | 405.7592 | 405.7592 | 0 | 0 | 0 | 925.286 | 0 | 0
6032 | 1094.9209 | 192.44 | 868.5 | 868.5 | 0 | 0 | 0 | 258.863 | 0 | 0
6033 | 1387.202 | 313.48 | 1414.1083 | 1414.1083 | 0 | 0 | 0 | 25.918 | 0 | 0
6034 | 1405.6574 | 801.79 | 3594.5532 | 1460.2042 | -614.9724 | 0 | 1519.3766 | 0 | 0 | 0
6035 | 1365.2484 | 770.6 | 3371.6777 | 1418.2261 | -423.0387 | 0 | 1530.4129 | 0 | 0 | 0
6036 | 1221.3717 | 990.64 | 4317.4034 | 1268.767 | 0 | 0 | 3048.6364 | 0 | 0 | 0
6037 | 1267.0966 | 981.45 | 4285.1776 | 1316.2653 | 0 | 0 | 2968.9123 | 0 | 0 | 0
6038 | 1528.0967 | 896.97 | 3960.3278 | 1587.3944 | 0 | 0 | 2372.9334 | 0 | 0 | 0
6039 | 1700.6118 | 742.35 | 3344.5389 | 1766.6038 | 0 | 0 | 1577.9351 | 0 | 0 | 0
6040 | 1411.0387 | 385.22 | 1747.3028 | 1465.793 | 0 | 0 | 281.5099 | 0 | 0 | 0
6041 | 1480.8333 | 76.39 | 320.2375 | 320.2375 | 0 | 0 | 0 | 1172.559 | 0 | 0
6042 | 1727.6442 | 17.63 | 46.8148 | 46.8148 | 0 | 0 | 0 | 1682.578 | 0 | 0
6043 | 1863.8394 | 0 | 0 | 0 | 0 | 0 | 0 | 1863.839 | 0 | 0
6044 | 874.2602 | 0 | 0 | 0 | 0 | 0 | 0 | 874.26 | 0 | 0
6045 | 1106.5238 | 0 | 0 | 0 | 0 | 0 | 0 | 1106.524 | 0 | 0
6046 | 1191.5782 | 0 | 0 | 0 | 0 | 0 | 0 | 885.704 | 0 | 317.7434
6047 | 1427.931 | 0 | 0 | 0 | 0 | 0 | 0 | 835.931 | 0 | 614.9724
6048 | 771.2136 | 0 | 0 | 0 | 0 | 0 | 0 | 771.214 | 0 | 0
6049 | 615.8259 | 0 | 0 | 0 | 0 | 0 | 0 | 615.826 | 0 | 0
6050 | 593.7445 | 0 | 0 | 0 | 0 | 0 | 0 | 593.745 | 0 | 0
6051 | 716.419 | 0 | 0 | 0 | 0 | 0 | 0 | 716.419 | 0 | 0
6052 | 741.7717 | 0 | 0 | 0 | 0 | 0 | 0 | 741.772 | 0 | 0
6053 | 516.8685 | 0 | 0 | 0 | 0 | 0 | 0 | 516.868 | 0 | 0
6054 | 739.3182 | 0 | 0 | 0 | 0 | 0 | 0 | 739.318 | 0 | 0
6055 | 691.8841 | 54.02 | 215.8023 | 215.8023 | 0 | 0 | 0 | 484.144 | 0 | 0
6056 | 788.801 | 176.85 | 794.5932 | 794.5932 | 0 | 0 | 0 | 23.89 | 0 | 0
6057 | 672.9677 | 250.47 | 1123.6481 | 699.0824 | -424.5657 | 0 | 0 | 0 | 0 | 0
6058 | 848.4842 | 330.02 | 1473.0418 | 881.4102 | -591.6315 | 0 | 0 | 0 | 0 | 0
6059 | 583.859 | 630.74 | 2795.4828 | 606.5155 | -21.8128 | 0 | 2167.1545 | 0 | 0 | 0
6060 | 720.5879 | 570.5 | 2524.0535 | 748.5502 | 0 | 0 | 1775.5033 | 0 | 0 | 0
6061 | 820.5103 | 758.8 | 3339.2576 | 852.3507 | 0 | 0 | 2486.9069 | 0 | 0 | 0
6062 | 864.1732 | 653.25 | 2897.1205 | 897.707 | 0 | 0 | 1999.4135 | 0 | 0 | 0
6063 | 828.4586 | 734.79 | 3329.5115 | 860.6071 | 0 | 0 | 2468.9044 | 0 | 0 | 0
6064 | 969.7735 | 393.05 | 1787.5534 | 1007.4048 | 0 | 0 | 780.1486 | 0 | 0 | 0
6065 | 882.8525 | 277.37 | 1224.4225 | 917.1108 | 0 | 0 | 307.3117 | 0 | 0 | 0
6066 | 889.7008 | 56.34 | 176.012 | 176.012 | 0 | 0 | 0 | 720.263 | 0 | 0
6067 | 815.3764 | 0 | 0 | 0 | 0 | 0 | 0 | 815.376 | 0 | 0
6068 | 857.0857 | 0 | 0 | 0 | 0 | 0 | 0 | 857.086 | 0 | 0
6069 | 776.1206 | 0 | 0 | 0 | 0 | 0 | 0 | 776.121 | 0 | 0
6070 | 704.9694 | 0 | 0 | 0 | 0 | 0 | 0 | 370.581 | 0 | 347.3649
6071 | 563.4848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 585.3509
6072 | 704.9694 | 0 | 0 | 0 | 0 | 0 | 0 | 704.969 | 0 | 0
6073 | 1049.2758 | 0 | 0 | 0 | 0 | 0 | 0 | 1049.276 | 0 | 0
6074 | 1127.7874 | 0 | 0 | 0 | 0 | 0 | 0 | 1127.787 | 0 | 0
6075 | 815.3764 | 0 | 0 | 0 | 0 | 0 | 0 | 815.376 | 0 | 0
6076 | 836.64 | 0 | 0 | 0 | 0 | 0 | 0 | 836.64 | 0 | 0
6077 | 796.5663 | 0 | 0 | 0 | 0 | 0 | 0 | 796.566 | 0 | 0
6078 | 758.1283 | 0 | 0 | 0 | 0 | 0 | 0 | 758.128 | 0 | 0
6079 | 855.4501 | 50.94 | 201.6559 | 201.6559 | 0 | 0 | 0 | 661.327 | 0 | 0
6080 | 639.7638 | 168.22 | 753.6383 | 664.5888 | -89.0495 | 0 | 0 | 0 | 0 | 0
6081 | 302.7034 | 386.95 | 1755.0741 | 314.4493 | -614.9724 | 0 | 825.6524 | 0 | 0 | 0
6082 | 287.4345 | 437.19 | 1958.2851 | 298.5878 | -333.9903 | 0 | 1325.707 | 0 | 0 | 0
6083 | 226.1197 | 651.52 | 2887.7827 | 234.8945 | 0 | 0 | 2652.8881 | 0 | 0 | 0
6084 | 306.2691 | 608.57 | 2688.1078 | 318.1537 | 0 | 0 | 2369.9541 | 0 | 0 | 0
6085 | 908.0488 | 739.28 | 3252.3979 | 943.2846 | 0 | 0 | 2309.1134 | 0 | 0 | 0
6086 | 1146.5832 | 676.06 | 2993.5247 | 1191.0759 | 0 | 0 | 1802.4488 | 0 | 0 | 0
6087 | 858.2665 | 48.09 | 182.6894 | 182.6894 | 0 | 0 | 0 | 682.401 | 0 | 0
6088 | 1394.3683 | 27.45 | 93.0863 | 93.0863 | 0 | 0 | 0 | 1304.759 | 0 | 0
6089 | 1415.3466 | 14.69 | 38.1397 | 38.1397 | 0 | 0 | 0 | 1378.632 | 0 | 0
6090 | 1274.8271 | 4.89 | 0 | 0 | 0 | 0 | 0 | 1274.827 | 0 | 0
6091 | 1217.7058 | 0 | 0 | 0 | 0 | 0 | 0 | 1217.706 | 0 | 0
6092 | 1113.8843 | 0 | 0 | 0 | 0 | 0 | 0 | 1113.884 | 0 | 0
6093 | 1204.6634 | 0 | 0 | 0 | 0 | 0 | 0 | 1204.663 | 0 | 0
6094 | 1071.3572 | 0 | 0 | 0 | 0 | 0 | 0 | 765.483 | 0 | 317.7434
6095 | 1266.8185 | 0 | 0 | 0 | 0 | 0 | 0 | 674.819 | 0 | 614.9724
6096 | 1126.9696 | 0 | 0 | 0 | 0 | 0 | 0 | 1126.97 | 0 | 0
6097 | 1026.3765 | 0 | 0 | 0 | 0 | 0 | 0 | 1026.377 | 0 | 0
6098 | 914.3338 | 0 | 0 | 0 | 0 | 0 | 0 | 914.334 | 0 | 0
6099 | 758.1283 | 0 | 0 | 0 | 0 | 0 | 0 | 758.128 | 0 | 0
6100 | 830.0973 | 0 | 0 | 0 | 0 | 0 | 0 | 830.097 | 0 | 0
6101 | 926.6013 | 0 | 0 | 0 | 0 | 0 | 0 | 926.601 | 0 | 0
6102 | 1324.0666 | 0 | 0 | 0 | 0 | 0 | 0 | 1324.067 | 0 | 0
6103 | 1107.3417 | 80.18 | 326.6127 | 326.6127 | 0 | 0 | 0 | 792.93 | 0 | 0
6104 | 949.5925 | 253.2 | 1149.1435 | 986.4417 | -162.7018 | 0 | 0 | 0 | 0 | 0
6105 | 1070.4841 | 449.31 | 2025.5269 | 1112.0239 | -614.9724 | 0 | 298.5307 | 0 | 0 | 0
6106 | 1490.9918 | 517.2 | 2294.1764 | 1548.8485 | -260.3369 | 0 | 484.9909 | 0 | 0 | 0
6107 | 1371.7788 | 605.9 | 2658.2369 | 1425.0105 | 0 | 0 | 1233.2264 | 0 | 0 | 0
6108 | 1488.1212 | 842.13 | 3632.2307 | 1545.8672 | 0 | 0 | 2086.3635 | 0 | 0 | 0
6109 | 1658.559 | 441.86 | 1940.4187 | 1722.919 | 0 | 0 | 217.4997 | 0 | 0 | 0
6110 | 1466.1104 | 181.11 | 783.1497 | 783.1497 | 0 | 0 | 0 | 553.781 | 0 | 164.583
6111 | 1663.649 | 429.1 | 1911.3696 | 1728.2065 | -183.1631 | 0 | 0 | 0 | 0 | 0
6112 | 1239.8362 | 257.58 | 1155.182 | 1155.182 | 0 | 0 | 0 | 127.807 | 0 | 0
6113 | 1491.3363 | 194.71 | 870.5817 | 870.5817 | 0 | 0 | 0 | 653.275 | 0 | 0
6114 | 1536.6216 | 38.51 | 129.8059 | 129.8059 | 0 | 0 | 0 | 1411.664 | 0 | 0
6115 | 1553.0947 | 0 | 0 | 0 | 0 | 0 | 0 | 1553.095 | 0 | 0
6116 | 1250.4619 | 0 | 0 | 0 | 0 | 0 | 0 | 1250.462 | 0 | 0
6117 | 1401.7604 | 0 | 0 | 0 | 0 | 0 | 0 | 1401.76 | 0 | 0
6118 | 1464.7333 | 0 | 0 | 0 | 0 | 0 | 0 | 1158.86 | 0 | 317.7434
6119 | 1255.3689 | 0 | 0 | 0 | 0 | 0 | 0 | 663.369 | 0 | 614.9724
6120 | 1278.2681 | 0 | 0 | 0 | 0 | 0 | 0 | 1278.268 | 0 | 0
6121 | 1221.8379 | 0 | 0 | 0 | 0 | 0 | 0 | 1221.838 | 0 | 0
6122 | 1106.5238 | 0 | 0 | 0 | 0 | 0 | 0 | 1106.524 | 0 | 0
6123 | 1113.0665 | 0 | 0 | 0 | 0 | 0 | 0 | 1113.066 | 0 | 0
6124 | 1459.8264 | 0 | 0 | 0 | 0 | 0 | 0 | 1459.826 | 0 | 0
6125 | 963.4036 | 0 | 0 | 0 | 0 | 0 | 0 | 963.404 | 0 | 0
6126 | 978.9424 | 0 | 0 | 0 | 0 | 0 | 0 | 978.942 | 0 | 0
6127 | 1391.9465 | 123.59 | 444.65 | 444.65 | 0 | 0 | 0 | 963.906 | 0 | 0
6128 | 1243.5472 | 368.63 | 1660.3144 | 1291.8025 | -368.5118 | 0 | 0 | 0 | 0 | 0
6129 | 1089.836 | 609.39 | 2728.6305 | 1132.1268 | -614.9724 | 0 | 981.5313 | 0 | 0 | 0
6130 | 1125.3411 | 647.65 | 2802.5145 | 1169.0096 | -54.5279 | 0 | 1578.977 | 0 | 0 | 0
6131 | 1443.0721 | 786.1 | 3334.0407 | 1499.07 | 0 | 0 | 1834.9707 | 0 | 0 | 0
6132 | 1395.4795 | 988.97 | 4165.8335 | 1449.6313 | 0 | 0 | 2716.2023 | 0 | 0 | 0
6133 | 1267.3981 | 972.74 | 4119.882 | 1316.5791 | 0 | 0 | 2803.3029 | 0 | 0 | 0
6134 | 1171.6916 | 871.37 | 3740.4336 | 1217.1592 | 0 | 0 | 2523.2744 | 0 | 0 | 0
6135 | 1207.4389 | 709.32 | 3110.6697 | 1254.2934 | 0 | 0 | 1856.3763 | 0 | 0 | 0
6136 | 1296.1408 | 497.81 | 2239.1 | 1346.4374 | 0 | 0 | 892.6626 | 0 | 0 | 0
6137 | 1213.9294 | 257.33 | 1116.7047 | 1116.7047 | 0 | 0 | 0 | 138.939 | 0 | 0
6138 | 1030.8817 | 45.53 | 140.6168 | 140.6168 | 0 | 0 | 0 | 895.517 | 0 | 0
6139 | 1441.0183 | 0 | 0 | 0 | 0 | 0 | 0 | 1441.018 | 0 | 0
6140 | 967.4928 | 0 | 0 | 0 | 0 | 0 | 0 | 967.493 | 0 | 0
6141 | 1176.0394 | 0 | 0 | 0 | 0 | 0 | 0 | 1176.039 | 0 | 0
6142 | 1427.1132 | 0 | 0 | 0 | 0 | 0 | 0 | 1121.24 | 0 | 317.7434
6143 | 1197.303 | 0 | 0 | 0 | 0 | 0 | 0 | 605.303 | 0 | 614.9724
6144 | 1134.3301 | 0 | 0 | 0 | 0 | 0 | 0 | 1134.33 | 0 | 0
6145 | 1411.5744 | 0 | 0 | 0 | 0 | 0 | 0 | 1411.574 | 0 | 0
6146 | 1233.2875 | 0 | 0 | 0 | 0 | 0 | 0 | 1233.287 | 0 | 0
6147 | 1411.5744 | 0 | 0 | 0 | 0 | 0 | 0 | 1411.574 | 0 | 0
6148 | 1032.9192 | 0 | 0 | 0 | 0 | 0 | 0 | 1032.919 | 0 | 0
6149 | 981.3959 | 0 | 0 | 0 | 0 | 0 | 0 | 981.396 | 0 | 0
6150 | 1022.2874 | 0 | 0 | 0 | 0 | 0 | 0 | 1022.287 | 0 | 0
6151 | 1038.644 | 107.78 | 429.9125 | 429.9125 | 0 | 0 | 0 | 624.791 | 0 | 0
6152 | 236.2455 | 309.17 | 1402.884 | 245.4135 | -614.9724 | 0 | 542.4981 | 0 | 0 | 0
6153 | 185.3969 | 376.83 | 1686.8506 | 192.5913 | -423.0387 | 0 | 1071.2207 | 0 | 0 | 0
6154 | 160.3938 | 565.45 | 2489.7345 | 166.617 | 0 | 0 | 2323.1175 | 0 | 0 | 0
6155 | 207.2309 | 698.15 | 3028.3527 | 215.2725 | 0 | 0 | 2813.0801 | 0 | 0 | 0
6156 | 198.151 | 822.83 | 3529.363 | 205.8402 | 0 | 0 | 3323.5228 | 0 | 0 | 0
6157 | 199.0353 | 797.79 | 3428.3341 | 206.7585 | 0 | 0 | 3221.5756 | 0 | 0 | 0
6158 | 150.5308 | 751.51 | 3259.0754 | 156.3723 | 0 | 0 | 3102.7031 | 0 | 0 | 0
6159 | 152.6909 | 436.93 | 1930.8555 | 158.6151 | 0 | 0 | 1772.2404 | 0 | 0 | 0
6160 | 170.769 | 374.93 | 1682.6871 | 177.3956 | 0 | 0 | 1505.2914 | 0 | 0 | 0
6161 | 138.479 | 120.33 | 521.3429 | 143.8526 | 0 | 0 | 377.4902 | 0 | 0 | 0
6162 | 137.6387 | 23.52 | 70.0102 | 70.0102 | 0 | 0 | 0 | 0 | 0 | 72.9698
6163 | 108.4667 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.676
6164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6165 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6166 | 87.5078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 90.9037
6167 | 89.1435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.6022
6168 | 92.4148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.0011
6169 | 86.69 | 0 | 0 | 0 | 0 | 0 | 0 | 68.407 | 0 | 18.9925
6170 | 89.1435 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 92.6022
6171 | 82.6008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 85.8063
6172 | 88.3256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.7535
6173 | 83.4186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.6561
6174 | 88.3256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.7535
6175 | 70.3334 | 102.88 | 413.8972 | 73.0623 | -340.835 | 0 | 0 | 0 | 0 | 0
6176 | 96.5407 | 301.47 | 1367.8846 | 100.2872 | -614.9724 | 0 | 652.6249 | 0 | 0 | 0
6177 | 784.7098 | 447.78 | 2004.4911 | 815.1594 | -82.2048 | 0 | 1107.1269 | 0 | 0 | 0
6178 | 1340.7248 | 584.71 | 2564.837 | 1392.7515 | 0 | 0 | 1172.0855 | 0 | 0 | 0
6179 | 1486.7248 | 720.68 | 3111.3906 | 1544.416 | 0 | 0 | 1566.9746 | 0 | 0 | 0
6180 | 1306.7255 | 736.08 | 3166.521 | 1357.4321 | 0 | 0 | 1809.0889 | 0 | 0 | 0
6181 | 1510.7833 | 786.14 | 3375.2262 | 1569.4086 | 0 | 0 | 1805.8177 | 0 | 0 | 0
6182 | 1642.3118 | 712.09 | 3085.0621 | 1706.0415 | 0 | 0 | 1379.0206 | 0 | 0 | 0
6183 | 1547.9905 | 577.9 | 2539.8911 | 1608.0594 | 0 | 0 | 931.8318 | 0 | 0 | 0
6184 | 1693.5468 | 430.58 | 1929.3243 | 1759.2647 | 0 | 0 | 170.0596 | 0 | 0 | 0
6185 | 1585.4113 | 231.32 | 1024.275 | 1024.275 | 0 | 0 | 0 | 599.398 | 0 | 0
6186 | 1638.605 | 45.69 | 141.5278 | 141.5278 | 0 | 0 | 0 | 1502.364 | 0 | 0
6187 | 1627.7258 | 0 | 0 | 0 | 0 | 0 | 0 | 1627.726 | 0 | 0
6188 | 1555.5125 | 0 | 0 | 0 | 0 | 0 | 0 | 1555.512 | 0 | 0
6189 | 1476.183 | 0 | 0 | 0 | 0 | 0 | 0 | 1476.183 | 0 | 0
6190 | 1661.8303 | 0 | 0 | 0 | 0 | 0 | 0 | 1355.957 | 0 | 317.7434
6191 | 1613.5784 | 0 | 0 | 0 | 0 | 0 | 0 | 1021.578 | 0 | 614.9724
6192 | 1260.2759 | 0 | 0 | 0 | 0 | 0 | 0 | 1260.276 | 0 | 0
6193 | 1171.9502 | 0 | 0 | 0 | 0 | 0 | 0 | 1171.95 | 0 | 0
6194 | 1521.1636 | 0 | 0 | 0 | 0 | 0 | 0 | 1521.164 | 0 | 0
6195 | 1377.2255 | 0 | 0 | 0 | 0 | 0 | 0 | 1377.226 | 0 | 0
6196 | 1270.9077 | 0 | 0 | 0 | 0 | 0 | 0 | 1270.908 | 0 | 0
6197 | 1565.3264 | 0 | 0 | 0 | 0 | 0 | 0 | 1565.326 | 0 | 0
6198 | 1360.8689 | 0 | 0 | 0 | 0 | 0 | 0 | 1360.869 | 0 | 0
6199 | 1170.3146 | 73.81 | 300.4493 | 300.4493 | 0 | 0 | 0 | 881.089 | 0 | 0
6200 | 1033.4007 | 246.49 | 1115.3449 | 1073.5019 | -41.8431 | 0 | 0 | 0 | 0 | 0
6201 | 1230.7481 | 436.97 | 1960.4437 | 1278.5069 | -614.9724 | 0 | 66.9645 | 0 | 0 | 0
6202 | 1537.052 | 620.04 | 2720.292 | 1596.6969 | -381.1956 | 0 | 742.3995 | 0 | 0 | 0
6203 | 1548.9034 | 701.81 | 3030.2568 | 1609.0078 | 0 | 0 | 1421.249 | 0 | 0 | 0
6204 | 1590.8468 | 800.57 | 3426.6429 | 1652.5794 | 0 | 0 | 1774.0635 | 0 | 0 | 0
6205 | 1238.0554 | 792.8 | 3394.8544 | 1286.0974 | 0 | 0 | 2108.757 | 0 | 0 | 0
6206 | 1441.5264 | 708.6 | 3066.4976 | 1497.4641 | 0 | 0 | 1569.0335 | 0 | 0 | 0
6207 | 1346.8708 | 628.96 | 2763.8959 | 1399.136 | 0 | 0 | 1364.7599 | 0 | 0 | 0
6208 | 1554.022 | 394.32 | 1767.5346 | 1614.3254 | 0 | 0 | 153.2092 | 0 | 0 | 0
6209 | 1638.7226 | 141.81 | 620.6152 | 620.6152 | 0 | 0 | 0 | 1041.291 | 0 | 0
6210 | 1543.6519 | 25.48 | 78.0412 | 78.0412 | 0 | 0 | 0 | 1468.526 | 0 | 0
6211 | 1296.4209 | 0 | 0 | 0 | 0 | 0 | 0 | 1296.421 | 0 | 0
6212 | 1246.3728 | 0 | 0 | 0 | 0 | 0 | 0 | 1246.373 | 0 | 0
6213 | 1571.8691 | 0 | 0 | 0 | 0 | 0 | 0 | 1571.869 | 0 | 0
6214 | 1827.8498 | 0 | 0 | 0 | 0 | 0 | 0 | 1521.976 | 0 | 317.7434
6215 | 1962.7917 | 0 | 0 | 0 | 0 | 0 | 0 | 1370.792 | 0 | 614.9724
6216 | 1447.5589 | 0 | 0 | 0 | 0 | 0 | 0 | 1447.559 | 0 | 0
6217 | 1347.7837 | 0 | 0 | 0 | 0 | 0 | 0 | 1347.784 | 0 | 0
6218 | 1417.2992 | 0 | 0 | 0 | 0 | 0 | 0 | 1417.299 | 0 | 0
6219 | 1479.4543 | 0 | 0 | 0 | 0 | 0 | 0 | 1479.454 | 0 | 0
6220 | 1595.5861 | 0 | 0 | 0 | 0 | 0 | 0 | 1595.586 | 0 | 0
6221 | 1610.3071 | 0 | 0 | 0 | 0 | 0 | 0 | 1610.307 | 0 | 0
6222 | 1157.2293 | 0 | 0 | 0 | 0 | 0 | 0 | 1157.229 | 0 | 0
6223 | 1109.7952 | 57.6 | 231.2909 | 231.2909 | 0 | 0 | 0 | 887.144 | 0 | 0
6224 | 994.4167 | 188.66 | 848.5466 | 848.5466 | 0 | 0 | 0 | 177.568 | 0 | 0
6225 | 1024.9954 | 299.55 | 1346.2214 | 1064.7697 | -281.4517 | 0 | 0 | 0 | 0 | 0
6226 | 1252.2468 | 588.08 | 2609.6115 | 1300.8401 | -614.9724 | 0 | 693.799 | 0 | 0 | 0
6227 | 1666.1761 | 772.1 | 3366.7163 | 1730.8326 | -141.587 | 0 | 1494.2967 | 0 | 0 | 0
6228 | 1295.9036 | 831.2 | 3590.5133 | 1346.1902 | 0 | 0 | 2244.3231 | 0 | 0 | 0
6229 | 1418.6527 | 771.92 | 3345.585 | 1473.7024 | 0 | 0 | 1871.8825 | 0 | 0 | 0
6230 | 1542.1992 | 773.11 | 3365.4448 | 1602.0447 | 0 | 0 | 1763.4001 | 0 | 0 | 0
6231 | 1525.4623 | 605.58 | 2684.3764 | 1584.6572 | 0 | 0 | 1099.7192 | 0 | 0 | 0
6232 | 1140.3677 | 461.86 | 2088.7777 | 1184.6197 | 0 | 0 | 904.158 | 0 | 0 | 0
6233 | 1753.2821 | 266.24 | 1159.2323 | 1159.2323 | 0 | 0 | 0 | 637.353 | 0 | 0
6234 | 1615.8908 | 38.51 | 119.8822 | 119.8822 | 0 | 0 | 0 | 1500.486 | 0 | 0
6235 | 1178.4929 | 0 | 0 | 0 | 0 | 0 | 0 | 1178.493 | 0 | 0
6236 | 1647.9272 | 0 | 0 | 0 | 0 | 0 | 0 | 1647.927 | 0 | 0
6237 | 1432.0201 | 0 | 0 | 0 | 0 | 0 | 0 | 1432.02 | 0 | 0
6238 | 1643.0203 | 0 | 0 | 0 | 0 | 0 | 0 | 1337.147 | 0 | 317.7434
6239 | 1400.1248 | 0 | 0 | 0 | 0 | 0 | 0 | 808.125 | 0 | 614.9724
6240 | 1198.1208 | 0 | 0 | 0 | 0 | 0 | 0 | 1198.121 | 0 | 0
6241 | 1325.7023 | 0 | 0 | 0 | 0 | 0 | 0 | 1325.702 | 0 | 0
6242 | 1425.4775 | 0 | 0 | 0 | 0 | 0 | 0 | 1425.478 | 0 | 0
6243 | 1218.5665 | 0 | 0 | 0 | 0 | 0 | 0 | 1218.567 | 0 | 0
6244 | 1399.3069 | 0 | 0 | 0 | 0 | 0 | 0 | 1399.307 | 0 | 0
6245 | 1315.0705 | 0 | 0 | 0 | 0 | 0 | 0 | 1315.07 | 0 | 0
6246 | 733.5934 | 0 | 0 | 0 | 0 | 0 | 0 | 733.593 | 0 | 0
6247 | 983.0315 | 124.66 | 463.2197 | 463.2197 | 0 | 0 | 0 | 537.115 | 0 | 0
6248 | 877.8811 | 370.51 | 1692.0135 | 911.947 | -614.9724 | 0 | 165.0941 | 0 | 0 | 0
6249 | 945.2549 | 612.01 | 2793.7324 | 981.9354 | -423.0387 | 0 | 1388.7583 | 0 | 0 | 0
6250 | 1289.4335 | 487.83 | 2157.9652 | 1339.4691 | 0 | 0 | 818.4961 | 0 | 0 | 0
6251 | 942.1656 | 676.38 | 2944.3082 | 978.7255 | 0 | 0 | 1965.5827 | 0 | 0 | 0
6252 | 1192.4164 | 1003.58 | 4331.5675 | 1238.6884 | 0 | 0 | 3092.8791 | 0 | 0 | 0
6253 | 1457.5078 | 626.44 | 2719.4527 | 1514.0662 | 0 | 0 | 1205.3864 | 0 | 0 | 0
6254 | 1298.3816 | 413.29 | 1815.4734 | 1348.7643 | 0 | 0 | 466.709 | 0 | 0 | 0
6255 | 1441.2678 | 178.12 | 773.3974 | 773.3974 | 0 | 0 | 0 | 696.761 | 0 | 0
6256 | 1536.8077 | 28.43 | 96.6286 | 96.6286 | 0 | 0 | 0 | 1443.788 | 0 | 0
6257 | 1458.4473 | 10.77 | 20.6816 | 20.6816 | 0 | 0 | 0 | 1438.539 | 0 | 0
6258 | 1564.8337 | 3.91 | 0 | 0 | 0 | 0 | 0 | 1564.834 | 0 | 0
6259 | 1103.6522 | 0 | 0 | 0 | 0 | 0 | 0 | 1103.652 | 0 | 0
6260 | 1320.7953 | 0 | 0 | 0 | 0 | 0 | 0 | 1320.795 | 0 | 0
6261 | 1423.8418 | 0 | 0 | 0 | 0 | 0 | 0 | 1423.842 | 0 | 0
6262 | 1526.8884 | 0 | 0 | 0 | 0 | 0 | 0 | 1221.015 | 0 | 317.7434
6263 | 1557.9659 | 0 | 0 | 0 | 0 | 0 | 0 | 965.966 | 0 | 614.9724
6264 | 1416.4814 | 0 | 0 | 0 | 0 | 0 | 0 | 1416.481 | 0 | 0
6265 | 1565.3264 | 0 | 0 | 0 | 0 | 0 | 0 | 1565.326 | 0 | 0
6266 | 1530.9776 | 0 | 0 | 0 | 0 | 0 | 0 | 1530.978 | 0 | 0
6267 | 1518.7101 | 0 | 0 | 0 | 0 | 0 | 0 | 1518.71 | 0 | 0
6268 | 1445.1054 | 0 | 0 | 0 | 0 | 0 | 0 | 1445.105 | 0 | 0
6269 | 1521.9814 | 0 | 0 | 0 | 0 | 0 | 0 | 1521.981 | 0 | 0
6270 | 1328.1557 | 0 | 0 | 0 | 0 | 0 | 0 | 1328.156 | 0 | 0
6271 | 1128.6053 | 43.14 | 165.6748 | 165.6748 | 0 | 0 | 0 | 969.119 | 0 | 0
6272 | 1388.3388 | 140.37 | 620.0594 | 620.0594 | 0 | 0 | 0 | 791.442 | 0 | 0
6273 | 1708.9138 | 329.52 | 1481.5402 | 1481.5402 | 0 | 0 | 0 | 282.717 | 0 | 0
6274 | 1431.3986 | 587.96 | 2606.9262 | 1486.943 | -614.9724 | 0 | 505.0108 | 0 | 0 | 0
6275 | 1533.1581 | 669.84 | 2931.9662 | 1592.6518 | -423.0387 | 0 | 916.2757 | 0 | 0 | 0
6276 | 1365.5684 | 588.85 | 2575.8016 | 1418.5596 | 0 | 0 | 1157.242 | 0 | 0 | 0
6277 | 1628.745 | 755.61 | 3282.1337 | 1691.948 | 0 | 0 | 1590.1857 | 0 | 0 | 0
6278 | 1656.7966 | 67.55 | 266.8274 | 266.8274 | 0 | 0 | 0 | 1399.936 | 0 | 0
6279 | 1559.5597 | 45.14 | 169.0811 | 169.0811 | 0 | 0 | 0 | 1396.794 | 0 | 0
6280 | 1548.5916 | 23.53 | 75.5159 | 75.5159 | 0 | 0 | 0 | 1475.897 | 0 | 0
6281 | 1862.9184 | 37.24 | 139.553 | 139.553 | 0 | 0 | 0 | 1728.579 | 0 | 0
6282 | 1641.6575 | 8.81 | 9.6578 | 9.6578 | 0 | 0 | 0 | 1632.361 | 0 | 0
6283 | 1998.0095 | 0 | 0 | 0 | 0 | 0 | 0 | 1998.01 | 0 | 0
6284 | 1726.4389 | 0 | 0 | 0 | 0 | 0 | 0 | 1726.439 | 0 | 0
6285 | 1521.9814 | 0 | 0 | 0 | 0 | 0 | 0 | 1521.981 | 0 | 0
6286 | 1737.8885 | 0 | 0 | 0 | 0 | 0 | 0 | 1432.015 | 0 | 317.7434
6287 | 1565.3264 | 0 | 0 | 0 | 0 | 0 | 0 | 973.326 | 0 | 614.9724
6288 | 1698.6327 | 0 | 0 | 0 | 0 | 0 | 0 | 1698.633 | 0 | 0
6289 | 692.7019 | 0 | 0 | 0 | 0 | 0 | 0 | 692.702 | 0 | 0
6290 | 512.7793 | 0 | 0 | 0 | 0 | 0 | 0 | 512.779 | 0 | 0
6291 | 606.0119 | 0 | 0 | 0 | 0 | 0 | 0 | 606.012 | 0 | 0
6292 | 754.857 | 0 | 0 | 0 | 0 | 0 | 0 | 754.857 | 0 | 0
6293 | 802.2911 | 0 | 0 | 0 | 0 | 0 | 0 | 802.291 | 0 | 0
6294 | 671.4383 | 0 | 0 | 0 | 0 | 0 | 0 | 671.438 | 0 | 0
6295 | 609.2833 | 100.1 | 407.7527 | 407.7527 | 0 | 0 | 0 | 216.762 | 0 | 0
6296 | 469.188 | 83.1 | 351.9834 | 351.9834 | 0 | 0 | 0 | 130.353 | 0 | 0
6297 | 557.6649 | 334.29 | 1501.612 | 579.305 | -614.9724 | 0 | 307.3345 | 0 | 0 | 0
6298 | 672.0078 | 560.26 | 2477.7467 | 698.0841 | -423.0387 | 0 | 1356.6239 | 0 | 0 | 0
6299 | 802.2369 | 947.94 | 4128.0906 | 833.3676 | 0 | 0 | 3294.723 | 0 | 0 | 0
6300 | 773.4902 | 1009.26 | 4347.7895 | 803.5051 | 0 | 0 | 3544.2844 | 0 | 0 | 0
6301 | 936.0094 | 992.73 | 4280.4885 | 972.3316 | 0 | 0 | 3308.1568 | 0 | 0 | 0
6302 | 851.9365 | 889.39 | 3878.0638 | 884.9952 | 0 | 0 | 2993.0686 | 0 | 0 | 0
6303 | 657.248 | 609.34 | 2689.2494 | 682.7523 | 0 | 0 | 2006.4971 | 0 | 0 | 0
6304 | 682.6487 | 173.44 | 764.1832 | 709.139 | 0 | 0 | 55.0442 | 0 | 0 | 0
6305 | 686.5273 | 64.1 | 262.4571 | 262.4571 | 0 | 0 | 0 | 433.874 | 0 | 0
6306 | 776.4017 | 12.73 | 24.8451 | 24.8451 | 0 | 0 | 0 | 752.485 | 0 | 0
6307 | 785.1463 | 0 | 0 | 0 | 0 | 0 | 0 | 785.146 | 0 | 0
6308 | 546.3104 | 0 | 0 | 0 | 0 | 0 | 0 | 546.31 | 0 | 0
6309 | 724.5973 | 0 | 0 | 0 | 0 | 0 | 0 | 724.597 | 0 | 0
6310 | 823.5547 | 0 | 0 | 0 | 0 | 0 | 0 | 517.681 | 0 | 317.7434
6311 | 729.5043 | 0 | 0 | 0 | 0 | 0 | 0 | 137.504 | 0 | 614.9724
6312 | 745.043 | 0 | 0 | 0 | 0 | 0 | 0 | 745.043 | 0 | 0
6313 | 1741.9777 | 0 | 0 | 0 | 0 | 0 | 0 | 1741.978 | 0 | 0
6314 | 1703.5397 | 0 | 0 | 0 | 0 | 0 | 0 | 1703.54 | 0 | 0
6315 | 1585.7722 | 0 | 0 | 0 | 0 | 0 | 0 | 1585.772 | 0 | 0
6316 | 1660.1947 | 0 | 0 | 0 | 0 | 0 | 0 | 1660.195 | 0 | 0
6317 | 1616.0319 | 0 | 0 | 0 | 0 | 0 | 0 | 1616.032 | 0 | 0
6318 | 1492.5396 | 0 | 0 | 0 | 0 | 0 | 0 | 1492.54 | 0 | 0
6319 | 1496.6287 | 83.41 | 342.9645 | 342.9645 | 0 | 0 | 0 | 1166.476 | 0 | 0
6320 | 112.7164 | 258.86 | 1182.2616 | 117.0899 | -614.9724 | 0 | 450.1993 | 0 | 0 | 0
6321 | 91.689 | 318.84 | 1440.3433 | 95.248 | -423.0387 | 0 | 922.0566 | 0 | 0 | 0
6322 | 0 | 431.73 | 1928.7155 | 0 | 0 | 0 | 1928.7155 | 0 | 0 | 0
6323 | 0 | 584.74 | 2583.8855 | 0 | 0 | 0 | 2583.8855 | 0 | 0 | 0
6324 | 0 | 604.18 | 2659.0171 | 0 | 0 | 0 | 2659.0171 | 0 | 0 | 0
6325 | 0 | 242.61 | 1067.4415 | 0 | 0 | 0 | 1067.4415 | 0 | 0 | 0
6326 | 89.7711 | 117.39 | 498.805 | 93.2556 | 0 | 0 | 405.5494 | 0 | 0 | 0
6327 | 73.0251 | 141.03 | 612.365 | 75.8587 | 0 | 0 | 536.5063 | 0 | 0 | 0
6328 | 78.3215 | 108.58 | 468.4542 | 81.3613 | 0 | 0 | 387.0929 | 0 | 0 | 0
6329 | 73.0629 | 85.43 | 363.8466 | 75.8972 | 0 | 0 | 287.9494 | 0 | 0 | 0
6330 | 85.2782 | 15.67 | 36.3 | 36.3 | 0 | 0 | 0 | 0 | 0 | 52.2872
6331 | 79.3551 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 82.4344
6332 | 88.3256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.7535
6333 | 80.9652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.1068
6334 | 88.3256 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.7535
6335 | 80.9652 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.1068
6336 | 85.8721 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 89.2042
6337 | 76.876 | 0 | 0 | 0 | 0 | 0 | 0 | 76.876 | 0 | 0
6338 | 83.4186 | 0 | 0 | 0 | 0 | 0 | 0 | 61.095 | 0 | 23.1903
6339 | 77.6938 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 80.7089
6340 | 81.783 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 84.9566
6341 | 78.5117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.5586
6342 | 83.4186 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.6561
6343 | 68.6977 | 88.37 | 363.7468 | 71.3638 | -292.383 | 0 | 0 | 0 | 0 | 0
6344 | 80.819 | 271.57 | 1246.0328 | 83.9552 | -614.9724 | 0 | 547.1052 | 0 | 0 | 0
6345 | 556.7111 | 424.28 | 1933.8545 | 578.314 | -130.6557 | 0 | 1224.8848 | 0 | 0 | 0
6346 | 1538.6406 | 428.03 | 1920.8674 | 1598.3476 | 0 | 0 | 322.5198 | 0 | 0 | 0
6347 | 1710.5127 | 513.38 | 2283.4372 | 1776.889 | 0 | 0 | 506.5482 | 0 | 0 | 0
6348 | 1592.0899 | 698.1 | 3073.9728 | 1653.8707 | 0 | 0 | 1420.1022 | 0 | 0 | 0
6349 | 1586.6892 | 700.61 | 3085.1857 | 1648.2601 | 0 | 0 | 1436.9256 | 0 | 0 | 0
6350 | 1637.1595 | 738.18 | 3263.1797 | 1700.6896 | 0 | 0 | 1562.4901 | 0 | 0 | 0
6351 | 1737.0911 | 365.45 | 1639.0656 | 1639.0656 | 0 | 0 | 0 | 0 | 0 | 165.4338
6352 | 1235.9792 | 358.64 | 1633.9433 | 1283.9409 | -184.1094 | 0 | 165.893 | 0 | 0 | 0
6353 | 1637.9753 | 162.86 | 725.7599 | 725.7599 | 0 | 0 | 0 | 939.326 | 0 | 0
6354 | 1283.7711 | 21.56 | 59.1579 | 59.1579 | 0 | 0 | 0 | 1226.823 | 0 | 0
6355 | 1342.5199 | 0 | 0 | 0 | 0 | 0 | 0 | 1342.52 | 0 | 0
6356 | 1375.5899 | 0 | 0 | 0 | 0 | 0 | 0 | 1375.59 | 0 | 0
6357 | 1208.7526 | 0 | 0 | 0 | 0 | 0 | 0 | 1208.753 | 0 | 0
6358 | 1334.6984 | 0 | 0 | 0 | 0 | 0 | 0 | 1028.825 | 0 | 317.7434
6359 | 1426.2953 | 0 | 0 | 0 | 0 | 0 | 0 | 834.295 | 0 | 614.9724
6360 | 1445.9232 | 0 | 0 | 0 | 0 | 0 | 0 | 1445.923 | 0 | 0
6361 | 1568.5977 | 0 | 0 | 0 | 0 | 0 | 0 | 1568.598 | 0 | 0
6362 | 1526.8884 | 0 | 0 | 0 | 0 | 0 | 0 | 1526.888 | 0 | 0
6363 | 1723.1676 | 0 | 0 | 0 | 0 | 0 | 0 | 1723.168 | 0 | 0
6364 | 1466.369 | 0 | 0 | 0 | 0 | 0 | 0 | 1466.369 | 0 | 0
6365 | 1491.7217 | 0 | 0 | 0 | 0 | 0 | 0 | 1491.722 | 0 | 0
6366 | 1755.8808 | 0 | 0 | 0 | 0 | 0 | 0 | 1755.881 | 0 | 0
6367 | 1216.9309 | 27.43 | 95.2387 | 27.0058 | -68.2329 | 0 | 0 | 1190.934 | 0 | 0
6368 | 1615.258 | 87.59 | 374.995 | 374.995 | 0 | 0 | 0 | 1254.271 | 0 | 0
6369 | 1535.5124 | 249.44 | 1121.3357 | 1121.3357 | 0 | 0 | 0 | 456.064 | 0 | 0
6370 | 1473.9411 | 266.28 | 1184.4971 | 1184.4971 | 0 | 0 | 0 | 333.691 | 0 | 0
6371 | 1908.6882 | 474.67 | 2110.712 | 1982.7542 | -127.9579 | 0 | 0 | 0 | 0 | 0
6372 | 2013.4594 | 527.23 | 2338.3183 | 2091.5908 | -246.7276 | 0 | 0 | 0 | 0 | 0
6373 | 2035.7422 | 196.72 | 859.4229 | 859.4229 | 0 | 0 | 0 | 1208.424 | 0 | 0
6374 | 1841.9829 | 562.42 | 2508.5535 | 1913.4607 | -595.0928 | 0 | 0 | 0 | 0 | 0
6375 | 1628.7921 | 276.6 | 1238.4807 | 1238.4807 | 0 | 0 | 0 | 436.575 | 0 | 0
6376 | 1389.4705 | 298.9 | 1359.9003 | 1359.9003 | 0 | 0 | 0 | 80.369 | 0 | 0
6377 | 1931.9585 | 130.05 | 574.2201 | 574.2201 | 0 | 0 | 0 | 1379.189 | 0 | 0
6378 | 1367.8348 | 19.59 | 51.7117 | 51.7117 | 0 | 0 | 0 | 1318.055 | 0 | 0
6379 | 1384.0595 | 0 | 0 | 0 | 0 | 0 | 0 | 1384.06 | 0 | 0
6380 | 1184.2177 | 0 | 0 | 0 | 0 | 0 | 0 | 1184.218 | 0 | 0
6381 | 1696.1792 | 0 | 0 | 0 | 0 | 0 | 0 | 1696.179 | 0 | 0
6382 | 1602.9466 | 0 | 0 | 0 | 0 | 0 | 0 | 1297.073 | 0 | 317.7434
6383 | 1638.9311 | 0 | 0 | 0 | 0 | 0 | 0 | 1046.931 | 0 | 614.9724
6384 | 1551.4233 | 0 | 0 | 0 | 0 | 0 | 0 | 1551.423 | 0 | 0
6385 | 1701.0862 | 0 | 0 | 0 | 0 | 0 | 0 | 1701.086 | 0 | 0
6386 | 1653.652 | 0 | 0 | 0 | 0 | 0 | 0 | 1653.652 | 0 | 0
6387 | 1684.7296 | 0 | 0 | 0 | 0 | 0 | 0 | 1684.73 | 0 | 0
6388 | 1203.0278 | 0 | 0 | 0 | 0 | 0 | 0 | 1203.028 | 0 | 0
6389 | 1548.9698 | 0 | 0 | 0 | 0 | 0 | 0 | 1548.97 | 0 | 0
6390 | 1546.5163 | 0 | 0 | 0 | 0 | 0 | 0 | 1546.516 | 0 | 0
6391 | 1351.055 | 19.59 | 59.8383 | 0 | -59.8383 | 0 | 0 | 1351.055 | 0 | 0
6392 | 1371.2114 | 58.53 | 238.9438 | 118.6159 | -120.3279 | 0 | 0 | 1257.027 | 0 | 0
6393 | 1665.9839 | 192.06 | 856.0925 | 856.0925 | 0 | 0 | 0 | 841.871 | 0 | 0
6394 | 1480.4755 | 343.08 | 1535.8832 | 1535.8832 | 0 | 0 | 0 | 1.965 | 0 | 0
6395 | 1901.1918 | 462.82 | 2059.178 | 1974.9673 | -84.2107 | 0 | 0 | 0 | 0 | 0
6396 | 1801.945 | 516.31 | 2288.6998 | 1871.869 | -416.8308 | 0 | 0 | 0 | 0 | 0
6397 | 1608.8247 | 456.76 | 2028.0585 | 1671.255 | -356.8035 | 0 | 0 | 0 | 0 | 0
6398 | 1764.516 | 294.28 | 1305.9178 | 1305.9178 | 0 | 0 | 0 | 507.381 | 0 | 0
6399 | 1869.6654 | 212.05 | 939.3143 | 939.3143 | 0 | 0 | 0 | 965.439 | 0 | 0
6400 | 1735.3911 | 238.48 | 1074.7277 | 1074.7277 | 0 | 0 | 0 | 700.81 | 0 | 0
6401 | 1870.3575 | 86.39 | 368.4422 | 368.4422 | 0 | 0 | 0 | 1515.679 | 0 | 0
6402 | 1742.4091 | 13.71 | 27.5834 | 27.5834 | 0 | 0 | 0 | 1715.857 | 0 | 0
6403 | 1712.774 | 0 | 0 | 0 | 0 | 0 | 0 | 1712.774 | 0 | 0
6404 | 1736.2529 | 0 | 0 | 0 | 0 | 0 | 0 | 1736.253 | 0 | 0
6405 | 1571.8691 | 0 | 0 | 0 | 0 | 0 | 0 | 1571.869 | 0 | 0
6406 | 1566.1442 | 0 | 0 | 0 | 0 | 0 | 0 | 1260.271 | 0 | 317.7434
6407 | 1353.5085 | 0 | 0 | 0 | 0 | 0 | 0 | 761.508 | 0 | 614.9724
6408 | 390.9227 | 0 | 0 | 0 | 0 | 0 | 0 | 390.923 | 0 | 0
6409 | 403.1901 | 0 | 0 | 0 | 0 | 0 | 0 | 403.19 | 0 | 0
6410 | 386.8335 | 0 | 0 | 0 | 0 | 0 | 0 | 386.834 | 0 | 0
6411 | 365.57 | 0 | 0 | 0 | 0 | 0 | 0 | 365.57 | 0 | 0
6412 | 375.3839 | 0 | 0 | 0 | 0 | 0 | 0 | 375.384 | 0 | 0
6413 | 388.4692 | 0 | 0 | 0 | 0 | 0 | 0 | 388.469 | 0 | 0
6414 | 406.4615 | 0 | 0 | 0 | 0 | 0 | 0 | 406.461 | 0 | 0
6415 | 362.2986 | 58.74 | 237.7783 | 237.7783 | 0 | 0 | 0 | 133.403 | 0 | 0
6416 | 452.8416 | 190.62 | 859.1206 | 470.4134 | -388.7072 | 0 | 0 | 0 | 0 | 0
6417 | 1718.3751 | 332.25 | 1493.8469 | 1493.8469 | 0 | 0 | 0 | 0 | 0 | 291.2092
6418 | 1870.1756 | 592.67 | 2614.2249 | 1942.7477 | -614.9724 | 0 | 56.5047 | 0 | 0 | 0
6419 | 1892.5228 | 612.65 | 2671.65 | 1965.9619 | -358.4167 | 0 | 347.2714 | 0 | 0 | 0
6420 | 1967.7386 | 430.28 | 1882.3911 | 1882.3911 | 0 | 0 | 0 | 0 | 0 | 161.7055
6421 | 1715.3512 | 681.36 | 2949.9385 | 1781.9148 | -179.9605 | 0 | 988.0633 | 0 | 0 | 0
6422 | 1757.0441 | 575.34 | 2517.5308 | 1825.2257 | 0 | 0 | 692.3052 | 0 | 0 | 0
6423 | 1950.1113 | 249.57 | 1100.0516 | 1100.0516 | 0 | 0 | 0 | 891.153 | 0 | 0
6424 | 1726.1516 | 337.35 | 1518.1716 | 1518.1716 | 0 | 0 | 0 | 264.692 | 0 | 0
6425 | 2137.608 | 238.58 | 1036.6825 | 1036.6825 | 0 | 0 | 0 | 1139.651 | 0 | 0
6426 | 1644.1407 | 28.93 | 74.5581 | 74.5581 | 0 | 0 | 0 | 1572.368 | 0 | 0
6427 | 1812.7762 | 0 | 0 | 0 | 0 | 0 | 0 | 1812.776 | 0 | 0
6428 | 1637.2954 | 0 | 0 | 0 | 0 | 0 | 0 | 1637.295 | 0 | 0
6429 | 1228.3805 | 0 | 0 | 0 | 0 | 0 | 0 | 1228.38 | 0 | 0
6430 | 1411.5744 | 0 | 0 | 0 | 0 | 0 | 0 | 1105.701 | 0 | 317.7434
6431 | 1350.2371 | 0 | 0 | 0 | 0 | 0 | 0 | 758.237 | 0 | 614.9724
6432 | 369.6591 | 0 | 0 | 0 | 0 | 0 | 0 | 369.659 | 0 | 0
6433 | 112.8605 | 0 | 0 | 0 | 0 | 0 | 0 | 112.861 | 0 | 0
6434 | 119.4032 | 0 | 0 | 0 | 0 | 0 | 0 | 119.403 | 0 | 0
6435 | 113.6784 | 0 | 0 | 0 | 0 | 0 | 0 | 113.678 | 0 | 0
6436 | 116.1318 | 0 | 0 | 0 | 0 | 0 | 0 | 116.132 | 0 | 0
6437 | 112.8605 | 0 | 0 | 0 | 0 | 0 | 0 | 112.861 | 0 | 0
6438 | 116.9497 | 0 | 0 | 0 | 0 | 0 | 0 | 116.95 | 0 | 0
6439 | 100.5931 | 62.51 | 253.9057 | 104.4965 | -149.4092 | 0 | 0 | 0 | 0 | 0
6440 | 225.1445 | 213.25 | 964.177 | 233.8807 | -614.9724 | 0 | 115.3239 | 0 | 0 | 0
6441 | 1240.0192 | 592.54 | 2695.5477 | 1288.1376 | -273.6295 | 0 | 1133.7806 | 0 | 0 | 0
6442 | 1266.4219 | 795.58 | 3521.1419 | 1315.5641 | 0 | 0 | 2205.5778 | 0 | 0 | 0
6443 | 1701.8192 | 929.41 | 4024.3171 | 1767.8577 | 0 | 0 | 2256.4595 | 0 | 0 | 0
6444 | 1591.6166 | 992.44 | 4251.8943 | 1653.3793 | 0 | 0 | 2598.515 | 0 | 0 | 0
6445 | 1439.8744 | 971.24 | 4175.0944 | 1495.7479 | 0 | 0 | 2679.3465 | 0 | 0 | 0
6446 | 1622.9691 | 866.91 | 3775.1608 | 1685.9479 | 0 | 0 | 2089.2129 | 0 | 0 | 0
6447 | 1764.8544 | 704.99 | 3134.13 | 1833.3387 | 0 | 0 | 1300.7913 | 0 | 0 | 0
6448 | 1749.6223 | 487.19 | 2215.8516 | 1817.5156 | 0 | 0 | 398.3359 | 0 | 0 | 0
6449 | 1578.746 | 208.02 | 915.375 | 915.375 | 0 | 0 | 0 | 697.565 | 0 | 0
6450 | 1433.9206 | 19.59 | 49.5531 | 49.5531 | 0 | 0 | 0 | 1386.218 | 0 | 0
6451 | 1471.9558 | 0 | 0 | 0 | 0 | 0 | 0 | 1471.956 | 0 | 0
6452 | 1491.7217 | 0 | 0 | 0 | 0 | 0 | 0 | 1491.722 | 0 | 0
6453 | 1544.0628 | 0 | 0 | 0 | 0 | 0 | 0 | 1544.063 | 0 | 0
6454 | 1414.8457 | 0 | 0 | 0 | 0 | 0 | 0 | 1108.972 | 0 | 317.7434
6455 | 1431.2023 | 0 | 0 | 0 | 0 | 0 | 0 | 839.202 | 0 | 614.9724
6456 | 482.5196 | 0 | 0 | 0 | 0 | 0 | 0 | 482.52 | 0 | 0
6457 | 426.0894 | 0 | 0 | 0 | 0 | 0 | 0 | 426.089 | 0 | 0
6458 | 399.101 | 0 | 0 | 0 | 0 | 0 | 0 | 399.101 | 0 | 0
6459 | 440.8103 | 0 | 0 | 0 | 0 | 0 | 0 | 440.81 | 0 | 0
6460 | 390.1049 | 0 | 0 | 0 | 0 | 0 | 0 | 390.105 | 0 | 0
6461 | 392.5583 | 0 | 0 | 0 | 0 | 0 | 0 | 392.558 | 0 | 0
6462 | 495.6049 | 0 | 0 | 0 | 0 | 0 | 0 | 495.605 | 0 | 0
6463 | 433.4498 | 76.54 | 315.4351 | 315.4351 | 0 | 0 | 0 | 129.798 | 0 | 0
6464 | 442.7905 | 239.98 | 1096.0533 | 459.9724 | -614.9724 | 0 | 21.1085 | 0 | 0 | 0
6465 | 1681.4818 | 608.43 | 2806.2105 | 1746.7315 | -423.0387 | 0 | 636.4403 | 0 | 0 | 0
6466 | 1826.7294 | 451.03 | 2022.0553 | 1897.6148 | 0 | 0 | 124.4405 | 0 | 0 | 0
6467 | 1832.1434 | 432.09 | 1923.1205 | 1903.2399 | 0 | 0 | 19.8806 | 0 | 0 | 0
6468 | 1642.4999 | 484.52 | 2152.1105 | 1706.2368 | 0 | 0 | 445.8737 | 0 | 0 | 0
6469 | 1936.4576 | 234.78 | 1033.1578 | 1033.1578 | 0 | 0 | 0 | 349.893 | 0 | 614.9724
6470 | 1870.011 | 483.41 | 2164.8317 | 1942.5763 | -222.2554 | 0 | 0 | 0 | 0 | 0
6471 | 1945.9424 | 576.54 | 2610.1912 | 2021.4538 | -462.1424 | 0 | 126.595 | 0 | 0 | 0
6472 | 1509.5259 | 310.88 | 1421.6729 | 1421.6729 | 0 | 0 | 0 | 140.96 | 0 | 0
6473 | 1569.9972 | 126.16 | 557.0632 | 557.0632 | 0 | 0 | 0 | 1033.743 | 0 | 0
6474 | 1518.9095 | 16.65 | 37.8437 | 37.8437 | 0 | 0 | 0 | 1482.479 | 0 | 0
6475 | 1387.3227 | 0 | 0 | 0 | 0 | 0 | 0 | 1387.323 | 0 | 0
6476 | 1625.028 | 0 | 0 | 0 | 0 | 0 | 0 | 1625.028 | 0 | 0
6477 | 1559.6016 | 0 | 0 | 0 | 0 | 0 | 0 | 1559.602 | 0 | 0
6478 | 1286.4464 | 0 | 0 | 0 | 0 | 0 | 0 | 980.573 | 0 | 317.7434
6479 | 1165.4076 | 0 | 0 | 0 | 0 | 0 | 0 | 573.408 | 0 | 614.9724
6480 | 1319.1596 | 0 | 0 | 0 | 0 | 0 | 0 | 1319.16 | 0 | 0
6481 | 1503.1713 | 0 | 0 | 0 | 0 | 0 | 0 | 1503.171 | 0 | 0
6482 | 924.9656 | 0 | 0 | 0 | 0 | 0 | 0 | 924.966 | 0 | 0
6483 | 1193.2138 | 0 | 0 | 0 | 0 | 0 | 0 | 1193.214 | 0 | 0
6484 | 1166.2254 | 0 | 0 | 0 | 0 | 0 | 0 | 1166.225 | 0 | 0
6485 | 1228.3805 | 0 | 0 | 0 | 0 | 0 | 0 | 1228.38 | 0 | 0
6486 | 1238.1945 | 0 | 0 | 0 | 0 | 0 | 0 | 1238.194 | 0 | 0
6487 | 1037.0083 | 29.39 | 103.6665 | 103.6665 | 0 | 0 | 0 | 937.214 | 0 | 0
6488 | 344.9167 | 93.16 | 400.8571 | 358.3014 | -42.5557 | 0 | 0 | 0 | 0 | 0
6489 | 280.4042 | 178.34 | 791.3521 | 291.285 | -500.0671 | 0 | 0 | 0 | 0 | 0
6490 | 270.3306 | 253.49 | 1128.1897 | 280.8201 | -495.3883 | 0 | 351.9813 | 0 | 0 | 0
6491 | 287.6502 | 470.21 | 2094.6916 | 298.8122 | 0 | 0 | 1795.8794 | 0 | 0 | 0
6492 | 303.9311 | 537.85 | 2385.7553 | 315.726 | 0 | 0 | 2070.0293 | 0 | 0 | 0
6493 | 295.44 | 482.12 | 2141.2051 | 306.9045 | 0 | 0 | 1834.3006 | 0 | 0 | 0
6494 | 282.4089 | 613.38 | 2726.289 | 293.3678 | 0 | 0 | 2432.9212 | 0 | 0 | 0
6495 | 273.0489 | 373.31 | 1677.5533 | 283.6446 | 0 | 0 | 1393.9087 | 0 | 0 | 0
6496 | 209.159 | 194.09 | 869.1742 | 217.2743 | 0 | 0 | 651.8998 | 0 | 0 | 0
6497 | 292.731 | 65 | 268.7731 | 268.7731 | 0 | 0 | 0 | 33.997 | 0 | 0
6498 | 235.0545 | 10.77 | 14.4892 | 14.4892 | 0 | 0 | 0 | 221.106 | 0 | 0
6499 | 209.7018 | 0 | 0 | 0 | 0 | 0 | 0 | 209.702 | 0 | 0
6500 | 305.8684 | 0 | 0 | 0 | 0 | 0 | 0 | 305.868 | 0 | 0
6501 | 293.6009 | 0 | 0 | 0 | 0 | 0 | 0 | 98.243 | 0 | 202.9388
6502 | 298.5079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 310.0915
6503 | 235.535 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 244.6749
6504 | 168.473 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 175.0106
6505 | 199.5505 | 0 | 0 | 0 | 0 | 0 | 0 | 199.55 | 0 | 0
6506 | 243.7133 | 0 | 0 | 0 | 0 | 0 | 0 | 243.713 | 0 | 0
6507 | 191.3722 | 0 | 0 | 0 | 0 | 0 | 0 | 191.372 | 0 | 0
6508 | 152.1164 | 0 | 0 | 0 | 0 | 0 | 0 | 152.116 | 0 | 0
6509 | 135.7598 | 0 | 0 | 0 | 0 | 0 | 0 | 135.76 | 0 | 0
6510 | 197.097 | 0 | 0 | 0 | 0 | 0 | 0 | 197.097 | 0 | 0
6511 | 122.6745 | 62.59 | 254.6869 | 127.4354 | -127.2515 | 0 | 0 | 0 | 0 | 0
6512 | 195.7169 | 201.94 | 915.2857 | 203.3107 | -614.9724 | 0 | 97.0025 | 0 | 0 | 0
6513 | 885.4685 | 392.69 | 1781.5512 | 919.8294 | -295.7872 | 0 | 565.9346 | 0 | 0 | 0
6514 | 1487.9546 | 586.54 | 2621.8715 | 1545.6947 | 0 | 0 | 1076.1768 | 0 | 0 | 0
6515 | 1782.3192 | 279.94 | 1234.66 | 1234.66 | 0 | 0 | 0 | 1.78 | 0 | 614.9724
6516 | 1685.3849 | 808.93 | 3543.5863 | 1750.7859 | -614.9724 | 0 | 1177.828 | 0 | 0 | 0
6517 | 1718.2943 | 759.09 | 3337.1696 | 1784.972 | -69.4254 | 0 | 1482.7722 | 0 | 0 | 0
6518 | 1671.8876 | 676.61 | 3001.1661 | 1736.7652 | 0 | 0 | 1264.4009 | 0 | 0 | 0
6519 | 1697.546 | 474.54 | 2133.2333 | 1763.4188 | 0 | 0 | 369.8145 | 0 | 0 | 0
6520 | 1755.8511 | 237.16 | 1067.0395 | 1067.0395 | 0 | 0 | 0 | 728.671 | 0 | 0
6521 | 1623.5477 | 59.44 | 241.5927 | 241.5927 | 0 | 0 | 0 | 1390.98 | 0 | 0
6522 | 1905.103 | 9.79 | 11.1422 | 11.1422 | 0 | 0 | 0 | 1894.377 | 0 | 0
6523 | 1574.8582 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.858 | 0 | 0
6524 | 1257.8224 | 0 | 0 | 0 | 0 | 0 | 0 | 1257.822 | 0 | 0
6525 | 1468.0047 | 0 | 0 | 0 | 0 | 0 | 0 | 1468.005 | 0 | 0
6526 | 1599.6753 | 0 | 0 | 0 | 0 | 0 | 0 | 1293.802 | 0 | 317.7434
6527 | 1683.9117 | 0 | 0 | 0 | 0 | 0 | 0 | 1091.912 | 0 | 614.9724
6528 | 1453.2837 | 0 | 0 | 0 | 0 | 0 | 0 | 1453.284 | 0 | 0
6529 | 1407.4852 | 0 | 0 | 0 | 0 | 0 | 0 | 1407.485 | 0 | 0
6530 | 1535.8845 | 0 | 0 | 0 | 0 | 0 | 0 | 1535.885 | 0 | 0
6531 | 1660.1947 | 0 | 0 | 0 | 0 | 0 | 0 | 1660.195 | 0 | 0
6532 | 1321.6131 | 0 | 0 | 0 | 0 | 0 | 0 | 1321.613 | 0 | 0
6533 | 1273.3611 | 0 | 0 | 0 | 0 | 0 | 0 | 1273.361 | 0 | 0
6534 | 1310.1635 | 0 | 0 | 0 | 0 | 0 | 0 | 1310.163 | 0 | 0
6535 | 1068.0858 | 5.87 | 0 | 0 | 0 | 0 | 0 | 1068.086 | 0 | 0
6536 | 1296.3319 | 15.67 | 42.244 | 42.244 | 0 | 0 | 0 | 1255.666 | 0 | 0
6537 | 1701.5656 | 35.31 | 127.2806 | 127.2806 | 0 | 0 | 0 | 1579.039 | 0 | 0
6538 | 1384.2118 | 558.56 | 2482.4192 | 1437.926 | -614.9724 | 0 | 429.5208 | 0 | 0 | 0
6539 | 1713.281 | 726.86 | 3184.5172 | 1779.7644 | -423.0387 | 0 | 981.7141 | 0 | 0 | 0
6540 | 1435.638 | 558.2 | 2453.4875 | 1491.3476 | 0 | 0 | 962.1399 | 0 | 0 | 0
6541 | 1436.8198 | 606.02 | 2663.2045 | 1492.5754 | 0 | 0 | 1170.6291 | 0 | 0 | 0
6542 | 1416.2125 | 617.37 | 2728.2285 | 1471.1678 | 0 | 0 | 1257.0607 | 0 | 0 | 0
6543 | 1458.112 | 601.01 | 2688.6054 | 1514.6937 | 0 | 0 | 1173.9117 | 0 | 0 | 0
6544 | 1580.7302 | 384.68 | 1750.0889 | 1642.0709 | 0 | 0 | 108.018 | 0 | 0 | 0
6545 | 1546.2679 | 110.44 | 478.2065 | 478.2065 | 0 | 0 | 0 | 1085.925 | 0 | 0
6546 | 1753.4948 | 13.71 | 24.762 | 24.762 | 0 | 0 | 0 | 1729.658 | 0 | 0
6547 | 1580.4767 | 0 | 0 | 0 | 0 | 0 | 0 | 1580.477 | 0 | 0
6548 | 1247.1906 | 0 | 0 | 0 | 0 | 0 | 0 | 1247.191 | 0 | 0
6549 | 1584.9543 | 0 | 0 | 0 | 0 | 0 | 0 | 1584.954 | 0 | 0
6550 | 1818.0358 | 0 | 0 | 0 | 0 | 0 | 0 | 1512.162 | 0 | 317.7434
6551 | 1714.1715 | 0 | 0 | 0 | 0 | 0 | 0 | 1122.171 | 0 | 614.9724
6552 | 1513.8031 | 0 | 0 | 0 | 0 | 0 | 0 | 1513.803 | 0 | 0
6553 | 1295.9329 | 0 | 0 | 0 | 0 | 0 | 0 | 1295.933 | 0 | 0
6554 | 1429.5663 | 0 | 0 | 0 | 0 | 0 | 0 | 1429.566 | 0 | 0
6555 | 1403.1504 | 0 | 0 | 0 | 0 | 0 | 0 | 1403.15 | 0 | 0
6556 | 223.7582 | 0 | 0 | 0 | 0 | 0 | 0 | 223.758 | 0 | 0
6557 | 344.1836 | 0 | 0 | 0 | 0 | 0 | 0 | 344.184 | 0 | 0
6558 | 855.4089 | 0 | 0 | 0 | 0 | 0 | 0 | 855.409 | 0 | 0
6559 | 1351.1431 | 85.36 | 351.5752 | 351.5752 | 0 | 0 | 0 | 1012.701 | 0 | 0
6560 | 1327.7543 | 345.43 | 1583.9529 | 1379.2782 | -204.6747 | 0 | 0 | 0 | 0 | 0
6561 | 1082.8362 | 335.35 | 1508.8452 | 1124.8562 | -383.989 | 0 | 0 | 0 | 0 | 0
6562 | 962.5079 | 689.07 | 3045.3081 | 999.8589 | -449.3464 | 0 | 1596.1027 | 0 | 0 | 0
6563 | 1672.8606 | 853.8 | 3696.7228 | 1737.7749 | 0 | 0 | 1958.9479 | 0 | 0 | 0
6564 | 1223.3853 | 670.34 | 2889.1009 | 1270.8581 | 0 | 0 | 1618.2428 | 0 | 0 | 0
6565 | 988.9209 | 863.97 | 3669.1996 | 1027.2958 | 0 | 0 | 2641.9038 | 0 | 0 | 0
6566 | 879.0094 | 816.1 | 3493.92 | 913.1187 | 0 | 0 | 2580.8013 | 0 | 0 | 0
6567 | 1120.1603 | 643.98 | 2821.9474 | 1163.6275 | 0 | 0 | 1658.3199 | 0 | 0 | 0
6568 | 1590.8052 | 400.48 | 1797.8802 | 1652.5368 | 0 | 0 | 145.3433 | 0 | 0 | 0
6569 | 1557.5416 | 140.57 | 605.0259 | 605.0259 | 0 | 0 | 0 | 975.117 | 0 | 0
6570 | 1465.6696 | 13.71 | 23.0885 | 23.0885 | 0 | 0 | 0 | 1443.444 | 0 | 0
6571 | 966.144 | 0 | 0 | 0 | 0 | 0 | 0 | 966.144 | 0 | 0
6572 | 1198.0387 | 0 | 0 | 0 | 0 | 0 | 0 | 1198.039 | 0 | 0
6573 | 1423.3507 | 0 | 0 | 0 | 0 | 0 | 0 | 1423.351 | 0 | 0
6574 | 1421.0199 | 0 | 0 | 0 | 0 | 0 | 0 | 1115.146 | 0 | 317.7434
6575 | 1225.2315 | 0 | 0 | 0 | 0 | 0 | 0 | 633.232 | 0 | 614.9724
6576 | 1382.173 | 0 | 0 | 0 | 0 | 0 | 0 | 1382.173 | 0 | 0
6577 | 1511.9217 | 0 | 0 | 0 | 0 | 0 | 0 | 1511.922 | 0 | 0
6578 | 1197.2617 | 0 | 0 | 0 | 0 | 0 | 0 | 1197.262 | 0 | 0
6579 | 1518.9141 | 0 | 0 | 0 | 0 | 0 | 0 | 1518.914 | 0 | 0
6580 | 1238.4395 | 0 | 0 | 0 | 0 | 0 | 0 | 1238.439 | 0 | 0
6581 | 1274.9556 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.956 | 0 | 0
6582 | 1134.3297 | 0 | 0 | 0 | 0 | 0 | 0 | 1134.33 | 0 | 0
6583 | 1236.1086 | 52.08 | 206.2807 | 206.2807 | 0 | 0 | 0 | 1037.534 | 0 | 0
6584 | 895.8243 | 186.61 | 833.1817 | 833.1817 | 0 | 0 | 0 | 93.766 | 0 | 0
6585 | 1078.1882 | 243.36 | 1074.5625 | 1074.5625 | 0 | 0 | 0 | 43.767 | 0 | 0
6586 | 1521.983 | 420.91 | 1839.1062 | 1581.0432 | -258.063 | 0 | 0 | 0 | 0 | 0
6587 | 1177.4916 | 562.27 | 2417.9801 | 1223.1832 | -614.9724 | 0 | 579.8245 | 0 | 0 | 0
6588 | 1060.1419 | 573.52 | 2453.4345 | 1101.2805 | -164.9757 | 0 | 1187.1783 | 0 | 0 | 0
6589 | 943.5293 | 638.62 | 2721.1854 | 980.1424 | 0 | 0 | 1741.043 | 0 | 0 | 0
6590 | 1025.0301 | 639.63 | 2746.7805 | 1064.806 | 0 | 0 | 1681.9745 | 0 | 0 | 0
6591 | 930.0669 | 546.38 | 2392.0765 | 966.157 | 0 | 0 | 1425.9195 | 0 | 0 | 0
6592 | 968.8011 | 249.26 | 1105.575 | 1006.3951 | 0 | 0 | 99.1799 | 0 | 0 | 0
6593 | 1132.6778 | 26.45 | 89.1294 | 89.1294 | 0 | 0 | 0 | 1046.877 | 0 | 0
6594 | 1010.9393 | 3.91 | 0 | 0 | 0 | 0 | 0 | 1010.939 | 0 | 0
6595 | 1250.7879 | 0 | 0 | 0 | 0 | 0 | 0 | 1250.788 | 0 | 0
6596 | 1191.8232 | 0 | 0 | 0 | 0 | 0 | 0 | 1191.823 | 0 | 0
6597 | 1114.1294 | 0 | 0 | 0 | 0 | 0 | 0 | 1114.129 | 0 | 0
6598 | 1338.6645 | 0 | 0 | 0 | 0 | 0 | 0 | 1032.791 | 0 | 317.7434
6599 | 1141.3222 | 0 | 0 | 0 | 0 | 0 | 0 | 549.322 | 0 | 614.9724
6600 | 156.1646 | 0 | 0 | 0 | 0 | 0 | 0 | 156.165 | 0 | 0
6601 | 101.7789 | 0 | 0 | 0 | 0 | 0 | 0 | 101.779 | 0 | 0
6602 | 103.3328 | 0 | 0 | 0 | 0 | 0 | 0 | 103.333 | 0 | 0
6603 | 99.4481 | 0 | 0 | 0 | 0 | 0 | 0 | 99.448 | 0 | 0
6604 | 104.8867 | 0 | 0 | 0 | 0 | 0 | 0 | 104.887 | 0 | 0
6605 | 98.6711 | 0 | 0 | 0 | 0 | 0 | 0 | 98.671 | 0 | 0
6606 | 101.002 | 0 | 0 | 0 | 0 | 0 | 0 | 101.002 | 0 | 0
6607 | 84.2832 | 6.85 | 3.9568 | 3.9568 | 0 | 0 | 0 | 80.475 | 0 | 0
6608 | 99.5365 | 18.61 | 55.1481 | 55.1481 | 0 | 0 | 0 | 46.448 | 0 | 0
6609 | 1023.3432 | 42.18 | 157.8921 | 157.8921 | 0 | 0 | 0 | 871.349 | 0 | 0
6610 | 1312.2971 | 82.5 | 335.5485 | 335.5485 | 0 | 0 | 0 | 989.283 | 0 | 0
6611 | 985.1178 | 337.07 | 1474.5968 | 1023.3453 | -451.2516 | 0 | 0 | 0 | 0 | 0
6612 | 1098.0768 | 465.77 | 2025.6516 | 1140.6876 | -586.7595 | 0 | 298.2045 | 0 | 0 | 0
6613 | 1289.3435 | 565.28 | 2448.2893 | 1339.3756 | 0 | 0 | 1108.9137 | 0 | 0 | 0
6614 | 1274.6729 | 367.04 | 1600.553 | 1324.1364 | 0 | 0 | 276.4166 | 0 | 0 | 0
6615 | 1148.4205 | 108.07 | 451.3035 | 451.3035 | 0 | 0 | 0 | 713.976 | 0 | 0
6616 | 1234.0498 | 62.77 | 251.5995 | 251.5995 | 0 | 0 | 0 | 991.849 | 0 | 0
6617 | 1363.2866 | 40.18 | 152.055 | 152.055 | 0 | 0 | 0 | 1216.912 | 0 | 0
6618 | 1689.6706 | 3.91 | 0 | 0 | 0 | 0 | 0 | 1689.671 | 0 | 0
6619 | 1542.9749 | 0 | 0 | 0 | 0 | 0 | 0 | 1542.975 | 0 | 0
6620 | 1457.536 | 0 | 0 | 0 | 0 | 0 | 0 | 1457.536 | 0 | 0
6621 | 1491.7213 | 0 | 0 | 0 | 0 | 0 | 0 | 1491.721 | 0 | 0
6622 | 1543.7762 | 0 | 0 | 0 | 0 | 0 | 0 | 1237.903 | 0 | 317.7434
6623 | 1860.7669 | 0 | 0 | 0 | 0 | 0 | 0 | 1268.767 | 0 | 614.9724
6624 | 186.4652 | 0 | 0 | 0 | 0 | 0 | 0 | 186.465 | 0 | 0
6625 | 104.1097 | 0 | 0 | 0 | 0 | 0 | 0 | 104.11 | 0 | 0
6626 | 112.656 | 0 | 0 | 0 | 0 | 0 | 0 | 112.656 | 0 | 0
6627 | 107.2175 | 0 | 0 | 0 | 0 | 0 | 0 | 107.217 | 0 | 0
6628 | 107.2175 | 0 | 0 | 0 | 0 | 0 | 0 | 107.217 | 0 | 0
6629 | 104.8867 | 0 | 0 | 0 | 0 | 0 | 0 | 104.887 | 0 | 0
6630 | 107.2175 | 0 | 0 | 0 | 0 | 0 | 0 | 107.217 | 0 | 0
6631 | 100.2454 | 125.03 | 480.5189 | 104.136 | -376.3829 | 0 | 0 | 0 | 0 | 0
6632 | 123.1185 | 330.53 | 1505.7402 | 127.8966 | -614.9724 | 0 | 762.8712 | 0 | 0 | 0
6633 | 971.1397 | 408 | 1830.9921 | 1008.8248 | -46.6558 | 0 | 775.5114 | 0 | 0 | 0
6634 | 1916.0218 | 505.1 | 2219.4354 | 1990.3728 | 0 | 0 | 229.0627 | 0 | 0 | 0
6635 | 1454.101 | 682.14 | 2939.0747 | 1510.527 | 0 | 0 | 1428.5477 | 0 | 0 | 0
6636 | 1405.6336 | 721.96 | 3078.2195 | 1460.1793 | 0 | 0 | 1618.0402 | 0 | 0 | 0
6637 | 1449.3753 | 849.91 | 3588.1542 | 1505.6187 | 0 | 0 | 2082.5355 | 0 | 0 | 0
6638 | 1617.9573 | 672.22 | 2887.1023 | 1680.7414 | 0 | 0 | 1206.3608 | 0 | 0 | 0
6639 | 1296.6671 | 381.45 | 1677.2167 | 1346.9849 | 0 | 0 | 330.2319 | 0 | 0 | 0
6640 | 1542.1261 | 149.56 | 649.5106 | 649.5106 | 0 | 0 | 0 | 916.878 | 0 | 0
6641 | 1368.5009 | 119.63 | 513.0574 | 513.0574 | 0 | 0 | 0 | 874.609 | 0 | 0
6642 | 1900.383 | 10.77 | 11.1298 | 11.1298 | 0 | 0 | 0 | 1889.669 | 0 | 0
6643 | 1656.3215 | 0 | 0 | 0 | 0 | 0 | 0 | 1656.321 | 0 | 0
6644 | 1599.7157 | 0 | 0 | 0 | 0 | 0 | 0 | 1599.716 | 0 | 0
6645 | 1535.2298 | 0 | 0 | 0 | 0 | 0 | 0 | 1535.23 | 0 | 0
6646 | 1731.7952 | 0 | 0 | 0 | 0 | 0 | 0 | 1425.922 | 0 | 317.7434
6647 | 1424.1277 | 0 | 0 | 0 | 0 | 0 | 0 | 832.128 | 0 | 614.9724
6648 | 1595.0541 | 0 | 0 | 0 | 0 | 0 | 0 | 1595.054 | 0 | 0
6649 | 1460.6438 | 0 | 0 | 0 | 0 | 0 | 0 | 1460.644 | 0 | 0
6650 | 1355.7571 | 0 | 0 | 0 | 0 | 0 | 0 | 1355.757 | 0 | 0
6651 | 1222.1238 | 0 | 0 | 0 | 0 | 0 | 0 | 1222.124 | 0 | 0
6652 | 1309.9178 | 0 | 0 | 0 | 0 | 0 | 0 | 1309.918 | 0 | 0
6653 | 1102.4753 | 0 | 0 | 0 | 0 | 0 | 0 | 1102.475 | 0 | 0
6654 | 1162.2995 | 0 | 0 | 0 | 0 | 0 | 0 | 1162.3 | 0 | 0
6655 | 1174.1449 | 125.49 | 482.2215 | 482.2215 | 0 | 0 | 0 | 709.937 | 0 | 0
6656 | 224.0097 | 314.26 | 1432.0806 | 232.7016 | -614.9724 | 0 | 584.4066 | 0 | 0 | 0
6657 | 279.8454 | 393.38 | 1766.9788 | 290.7043 | -423.0387 | 0 | 1053.2358 | 0 | 0 | 0
6658 | 322.6469 | 652.89 | 2861.3586 | 335.1672 | 0 | 0 | 2526.1914 | 0 | 0 | 0
6659 | 279.4598 | 613.63 | 2655.3273 | 290.3044 | 0 | 0 | 2365.0229 | 0 | 0 | 0
6660 | 226.3163 | 681.9 | 2928.7957 | 235.0981 | 0 | 0 | 2693.6976 | 0 | 0 | 0
6661 | 249.9566 | 791.42 | 3388.8221 | 259.6555 | 0 | 0 | 3129.1666 | 0 | 0 | 0
6662 | 247.4402 | 804.74 | 3478.9166 | 257.0418 | 0 | 0 | 3221.8747 | 0 | 0 | 0
6663 | 268.3642 | 319.8 | 1413.1443 | 278.7778 | 0 | 0 | 1134.3665 | 0 | 0 | 0
6664 | 198.7923 | 280.88 | 1256.453 | 206.5061 | 0 | 0 | 1049.947 | 0 | 0 | 0
6665 | 292.6697 | 25.47 | 85.0791 | 85.0791 | 0 | 0 | 0 | 210.769 | 0 | 0
6666 | 221.6323 | 2.94 | 0 | 0 | 0 | 0 | 0 | 221.632 | 0 | 0
6667 | 210.0695 | 0 | 0 | 0 | 0 | 0 | 0 | 210.07 | 0 | 0
6668 | 235.4123 | 0 | 0 | 0 | 0 | 0 | 0 | 235.412 | 0 | 0
6669 | 195.0115 | 0 | 0 | 0 | 0 | 0 | 0 | 127.685 | 0 | 69.9396
6670 | 287.4671 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 298.6221
6671 | 260.2743 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270.3739
6672 | 282.8055 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293.7792
6673 | 230.7506 | 0 | 0 | 0 | 0 | 0 | 0 | 230.751 | 0 | 0
6674 | 185.6882 | 0 | 0 | 0 | 0 | 0 | 0 | 185.688 | 0 | 0
6675 | 236.1892 | 0 | 0 | 0 | 0 | 0 | 0 | 236.189 | 0 | 0
6676 | 198.1192 | 0 | 0 | 0 | 0 | 0 | 0 | 198.119 | 0 | 0
6677 | 229.1968 | 0 | 0 | 0 | 0 | 0 | 0 | 229.197 | 0 | 0
6678 | 285.1363 | 0 | 0 | 0 | 0 | 0 | 0 | 285.136 | 0 | 0
6679 | 164.7109 | 128.21 | 492.755 | 171.1026 | -321.6524 | 0 | 0 | 0 | 0 | 0
6680 | 199.3876 | 349.54 | 1596.6793 | 207.1242 | -614.9724 | 0 | 774.5827 | 0 | 0 | 0
6681 | 1165.9822 | 430.24 | 1938.8335 | 1211.2266 | -101.3873 | 0 | 626.2196 | 0 | 0 | 0
6682 | 1779.2506 | 662.74 | 2918.0327 | 1848.2944 | 0 | 0 | 1069.7383 | 0 | 0 | 0
6683 | 1668.8448 | 772.77 | 3350.5889 | 1733.6041 | 0 | 0 | 1616.9848 | 0 | 0 | 0
6684 | 1306.7683 | 762.96 | 3308.51 | 1357.4768 | 0 | 0 | 1951.0332 | 0 | 0 | 0
6685 | 1367.4141 | 704.59 | 3070.5012 | 1420.4762 | 0 | 0 | 1650.025 | 0 | 0 | 0
6686 | 1211.3632 | 319.46 | 1401.7839 | 1258.3696 | 0 | 0 | 143.4143 | 0 | 0 | 0
6687 | 1187.0499 | 45.13 | 168.6022 | 168.6022 | 0 | 0 | 0 | 1024.746 | 0 | 0
6688 | 1289.3338 | 71.61 | 292.6604 | 292.6604 | 0 | 0 | 0 | 1007.606 | 0 | 0
6689 | 1473.5876 | 47.05 | 183.724 | 183.724 | 0 | 0 | 0 | 1296.726 | 0 | 0
6690 | 1450.7679 | 7.83 | 1.07 | 1.07 | 0 | 0 | 0 | 1449.737 | 0 | 0
6691 | 1377.5454 | 0 | 0 | 0 | 0 | 0 | 0 | 1377.545 | 0 | 0
6692 | 1000.6964 | 0 | 0 | 0 | 0 | 0 | 0 | 1000.696 | 0 | 0
6693 | 1480.0672 | 0 | 0 | 0 | 0 | 0 | 0 | 1480.067 | 0 | 0
6694 | 1346.4339 | 0 | 0 | 0 | 0 | 0 | 0 | 1040.56 | 0 | 317.7434
6695 | 1285.8327 | 0 | 0 | 0 | 0 | 0 | 0 | 693.833 | 0 | 614.9724
6696 | 1184.8307 | 0 | 0 | 0 | 0 | 0 | 0 | 1184.831 | 0 | 0
6697 | 1309.9178 | 0 | 0 | 0 | 0 | 0 | 0 | 1309.918 | 0 | 0
6698 | 1500.2676 | 0 | 0 | 0 | 0 | 0 | 0 | 1500.268 | 0 | 0
6699 | 1316.9102 | 0 | 0 | 0 | 0 | 0 | 0 | 1316.91 | 0 | 0
6700 | 1187.9385 | 0 | 0 | 0 | 0 | 0 | 0 | 1187.938 | 0 | 0
6701 | 966.5111 | 0 | 0 | 0 | 0 | 0 | 0 | 966.511 | 0 | 0
6702 | 1231.447 | 0 | 0 | 0 | 0 | 0 | 0 | 1231.447 | 0 | 0
6703 | 1040.3999 | 107.79 | 427.3632 | 427.3632 | 0 | 0 | 0 | 629.001 | 0 | 0
6704 | 1049.4094 | 288.13 | 1314.6936 | 1090.1311 | -224.5626 | 0 | 0 | 0 | 0 | 0
6705 | 1392.0499 | 477.14 | 2154.0146 | 1446.0681 | -614.9724 | 0 | 92.9741 | 0 | 0 | 0
6706 | 1491.899 | 629.82 | 2780.5147 | 1549.7918 | -198.4761 | 0 | 1032.2468 | 0 | 0 | 0
6707 | 1479.7011 | 653.35 | 2849.7146 | 1537.1215 | 0 | 0 | 1312.5932 | 0 | 0 | 0
6708 | 1376.6976 | 791.1 | 3423.2896 | 1430.1204 | 0 | 0 | 1993.1692 | 0 | 0 | 0
6709 | 1804.4341 | 758.97 | 3295.2985 | 1874.4546 | 0 | 0 | 1420.8439 | 0 | 0 | 0
6710 | 1768.6143 | 730.18 | 3206.4817 | 1837.2446 | 0 | 0 | 1369.2371 | 0 | 0 | 0
6711 | 1995.8376 | 485.68 | 2175.7132 | 2073.286 | 0 | 0 | 102.4272 | 0 | 0 | 0
6712 | 1636.7689 | 407.44 | 1868.9604 | 1700.2834 | 0 | 0 | 168.677 | 0 | 0 | 0
6713 | 1880.17 | 68.28 | 277.497 | 277.497 | 0 | 0 | 0 | 1613.039 | 0 | 0
6714 | 1605.2708 | 3.91 | 0 | 0 | 0 | 0 | 0 | 1605.271 | 0 | 0
6715 | 1176.8108 | 0 | 0 | 0 | 0 | 0 | 0 | 1176.811 | 0 | 0
6716 | 1179.3922 | 0 | 0 | 0 | 0 | 0 | 0 | 1179.392 | 0 | 0
6717 | 1017.789 | 0 | 0 | 0 | 0 | 0 | 0 | 1017.789 | 0 | 0
6718 | 1282.7249 | 0 | 0 | 0 | 0 | 0 | 0 | 976.851 | 0 | 317.7434
6719 | 1643.2243 | 0 | 0 | 0 | 0 | 0 | 0 | 1051.224 | 0 | 614.9724
6720 | 1414.8044 | 0 | 0 | 0 | 0 | 0 | 0 | 1414.804 | 0 | 0
6721 | 1612.9237 | 0 | 0 | 0 | 0 | 0 | 0 | 1612.924 | 0 | 0
6722 | 1513.4756 | 0 | 0 | 0 | 0 | 0 | 0 | 1513.476 | 0 | 0
6723 | 1312.2486 | 0 | 0 | 0 | 0 | 0 | 0 | 1312.249 | 0 | 0
6724 | 926.8872 | 0 | 0 | 0 | 0 | 0 | 0 | 926.887 | 0 | 0
6725 | 1116.4602 | 0 | 0 | 0 | 0 | 0 | 0 | 1116.46 | 0 | 0
6726 | 923.0026 | 0 | 0 | 0 | 0 | 0 | 0 | 923.003 | 0 | 0
6727 | 974.5728 | 5.87 | 0 | 0 | 0 | 0 | 0 | 974.573 | 0 | 0
6728 | 1109.3055 | 29.85 | 106.0142 | 106.0142 | 0 | 0 | 0 | 1007.251 | 0 | 0
6729 | 1453.1366 | 101.85 | 431.9412 | 431.9412 | 0 | 0 | 0 | 1037.331 | 0 | 0
6730 | 1636.4299 | 101.21 | 421.4078 | 421.4078 | 0 | 0 | 0 | 1230.764 | 0 | 0
6731 | 1700.6594 | 100.29 | 412.6787 | 412.6787 | 0 | 0 | 0 | 1303.396 | 0 | 0
6732 | 1576.4513 | 171.65 | 731.2074 | 731.2074 | 0 | 0 | 0 | 872.559 | 0 | 0
6733 | 1782.2292 | 383.61 | 1677.3757 | 1677.3757 | 0 | 0 | 0 | 167.512 | 0 | 0
6734 | 1708.3705 | 615.71 | 2704.4482 | 1774.6629 | -614.9724 | 0 | 314.8129 | 0 | 0 | 0
6735 | 1688.8665 | 602.67 | 2688.2387 | 1754.4031 | -423.0387 | 0 | 510.7969 | 0 | 0 | 0
6736 | 1513.6533 | 443.45 | 2024.0009 | 1572.3899 | 0 | 0 | 451.611 | 0 | 0 | 0
6737 | 1543.6956 | 198.97 | 846.9853 | 846.9853 | 0 | 0 | 0 | 728.35 | 0 | 0
6738 | 1589.396 | 22.99 | 33.6978 | 33.6978 | 0 | 0 | 0 | 1556.957 | 0 | 0
6739 | 1404.3944 | 0 | 0 | 0 | 0 | 0 | 0 | 1404.394 | 0 | 0
6740 | 1464.5285 | 0 | 0 | 0 | 0 | 0 | 0 | 1464.528 | 0 | 0
6741 | 1266.4092 | 0 | 0 | 0 | 0 | 0 | 0 | 1266.409 | 0 | 0
6742 | 1237.6625 | 0 | 0 | 0 | 0 | 0 | 0 | 931.789 | 0 | 317.7434
6743 | 1469.1901 | 0 | 0 | 0 | 0 | 0 | 0 | 877.19 | 0 | 614.9724
6744 | 1402.3734 | 0 | 0 | 0 | 0 | 0 | 0 | 1402.373 | 0 | 0
6745 | 1487.8366 | 0 | 0 | 0 | 0 | 0 | 0 | 1487.837 | 0 | 0
6746 | 1173.9536 | 0 | 0 | 0 | 0 | 0 | 0 | 1173.954 | 0 | 0
6747 | 1220.5699 | 0 | 0 | 0 | 0 | 0 | 0 | 1220.57 | 0 | 0
6748 | 1091.5981 | 0 | 0 | 0 | 0 | 0 | 0 | 1091.598 | 0 | 0
6749 | 1039.5433 | 0 | 0 | 0 | 0 | 0 | 0 | 1039.543 | 0 | 0
6750 | 1033.3278 | 0 | 0 | 0 | 0 | 0 | 0 | 1033.328 | 0 | 0
6751 | 1125.2328 | 88.61 | 345.3122 | 345.3122 | 0 | 0 | 0 | 792.819 | 0 | 0
6752 | 1299.0474 | 212.06 | 958.9674 | 958.9674 | 0 | 0 | 0 | 375.903 | 0 | 0
6753 | 1556.2421 | 323.1 | 1445.8729 | 1445.8729 | 0 | 0 | 0 | 164.381 | 0 | 0
6754 | 1612.0778 | 179.59 | 775.047 | 775.047 | 0 | 0 | 0 | 865.982 | 0 | 0
6755 | 0 | 447.11 | 1948.4674 | 0 | -614.9724 | 0 | 1333.495 | 0 | 0 | 0
6756 | 1493.2053 | 702.76 | 3003.1347 | 1551.1484 | -423.0387 | 0 | 1028.9475 | 0 | 0 | 0
6757 | 1246.7915 | 665.37 | 2851.358 | 1295.1724 | 0 | 0 | 1556.1856 | 0 | 0 | 0
6758 | 1561.9623 | 618.17 | 2670.3016 | 1622.5746 | 0 | 0 | 1047.727 | 0 | 0 | 0
6759 | 1551.8563 | 327.3 | 1438.8526 | 1438.8526 | 0 | 0 | 0 | 166.752 | 0 | 0
6760 | 1685.1478 | 324.99 | 1465.5426 | 1465.5426 | 0 | 0 | 0 | 274.351 | 0 | 0
6761 | 1491.6931 | 163.89 | 701.1818 | 701.1818 | 0 | 0 | 0 | 816.704 | 0 | 0
6762 | 1361.0005 | 15.85 | 19.3031 | 19.3031 | 0 | 0 | 0 | 1342.418 | 0 | 0
6763 | 1278.8742 | 0 | 0 | 0 | 0 | 0 | 0 | 1278.874 | 0 | 0
6764 | 1114.9063 | 0 | 0 | 0 | 0 | 0 | 0 | 1114.906 | 0 | 0
6765 | 1342.5492 | 0 | 0 | 0 | 0 | 0 | 0 | 1342.549 | 0 | 0
6766 | 1593.5002 | 0 | 0 | 0 | 0 | 0 | 0 | 1287.627 | 0 | 317.7434
6767 | 1337.8875 | 0 | 0 | 0 | 0 | 0 | 0 | 745.888 | 0 | 614.9724
6768 | 1203.4772 | 0 | 0 | 0 | 0 | 0 | 0 | 1203.477 | 0 | 0
6769 | 923.0026 | 0 | 0 | 0 | 0 | 0 | 0 | 923.003 | 0 | 0
6770 | 1208.9158 | 0 | 0 | 0 | 0 | 0 | 0 | 1208.916 | 0 | 0
6771 | 935.4336 | 0 | 0 | 0 | 0 | 0 | 0 | 935.434 | 0 | 0
6772 | 835.9855 | 0 | 0 | 0 | 0 | 0 | 0 | 835.985 | 0 | 0
6773 | 948.6415 | 0 | 0 | 0 | 0 | 0 | 0 | 948.642 | 0 | 0
6774 | 1023.2276 | 0 | 0 | 0 | 0 | 0 | 0 | 1023.228 | 0 | 0
6775 | 855.543 | 7.83 | 8.2201 | 8.2201 | 0 | 0 | 0 | 847.63 | 0 | 0
6776 | 734.4698 | 124.84 | 548.3466 | 548.3466 | 0 | 0 | 0 | 206.607 | 0 | 0
6777 | 1354.9452 | 493.25 | 2229.3352 | 1407.5233 | -614.9724 | 0 | 206.8395 | 0 | 0 | 0
6778 | 1584.1702 | 549.98 | 2427.7262 | 1645.6433 | -423.0387 | 0 | 359.0442 | 0 | 0 | 0
6779 | 1585.9435 | 442.88 | 1934.5817 | 1647.4851 | 0 | 0 | 287.0965 | 0 | 0 | 0
6780 | 1196.4829 | 492.73 | 2141.7962 | 1242.9122 | 0 | 0 | 898.884 | 0 | 0 | 0
6781 | 1424.9425 | 374.48 | 1633.6898 | 1480.2376 | 0 | 0 | 153.4522 | 0 | 0 | 0
6782 | 1249.168 | 402.92 | 1767.0495 | 1297.6416 | 0 | 0 | 469.4078 | 0 | 0 | 0
6783 | 1398.008 | 531.78 | 2359.8517 | 1452.2573 | 0 | 0 | 907.5944 | 0 | 0 | 0
6784 | 1407.3079 | 395.43 | 1796.4362 | 1461.9182 | 0 | 0 | 334.518 | 0 | 0 | 0
6785 | 1093.0432 | 150.67 | 646.8377 | 646.8377 | 0 | 0 | 0 | 470.368 | 0 | 0
6786 | 1275.5441 | 15.21 | 16.0745 | 16.0745 | 0 | 0 | 0 | 1260.07 | 0 | 0
6787 | 1074.0238 | 0 | 0 | 0 | 0 | 0 | 0 | 1074.024 | 0 | 0
6788 | 1001.4733 | 0 | 0 | 0 | 0 | 0 | 0 | 1001.473 | 0 | 0
6789 | 1020.8968 | 0 | 0 | 0 | 0 | 0 | 0 | 1020.897 | 0 | 0
6790 | 1296.7098 | 0 | 0 | 0 | 0 | 0 | 0 | 990.836 | 0 | 317.7434
6791 | 1046.5357 | 0 | 0 | 0 | 0 | 0 | 0 | 454.536 | 0 | 614.9724
6792 | 1089.2673 | 0 | 0 | 0 | 0 | 0 | 0 | 1089.267 | 0 | 0
6793 | 1177.0613 | 0 | 0 | 0 | 0 | 0 | 0 | 1177.061 | 0 | 0
6794 | 1226.0084 | 0 | 0 | 0 | 0 | 0 | 0 | 1226.008 | 0 | 0
6795 | 1172.3997 | 0 | 0 | 0 | 0 | 0 | 0 | 1172.4 | 0 | 0
6796 | 942.426 | 0 | 0 | 0 | 0 | 0 | 0 | 942.426 | 0 | 0
6797 | 939.3183 | 0 | 0 | 0 | 0 | 0 | 0 | 939.318 | 0 | 0
6798 | 1045.7588 | 0 | 0 | 0 | 0 | 0 | 0 | 1045.759 | 0 | 0
6799 | 671.3979 | 66.79 | 271.3753 | 271.3753 | 0 | 0 | 0 | 410.16 | 0 | 0
6800 | 872.0645 | 177.36 | 789.9331 | 789.9331 | 0 | 0 | 0 | 111.64 | 0 | 0
6801 | 485.7777 | 290.44 | 1290.932 | 504.6285 | -614.9724 | 0 | 171.3311 | 0 | 0 | 0
6802 | 364.5171 | 508.37 | 2233.1799 | 378.662 | -423.0387 | 0 | 1431.4792 | 0 | 0 | 0
6803 | 364.7608 | 627.75 | 2720.4395 | 378.9144 | 0 | 0 | 2341.5251 | 0 | 0 | 0
6804 | 378.6719 | 455.85 | 1985.9454 | 393.3663 | 0 | 0 | 1592.5791 | 0 | 0 | 0
6805 | 728.4592 | 268.73 | 1164.3723 | 756.7277 | 0 | 0 | 407.6446 | 0 | 0 | 0
6806 | 1278.5809 | 340.68 | 1495.5682 | 1328.196 | 0 | 0 | 167.3722 | 0 | 0 | 0
6807 | 1456.5445 | 57.9 | 225.6367 | 225.6367 | 0 | 0 | 0 | 1239.336 | 0 | 0
6808 | 1463.702 | 55.98 | 221.4264 | 221.4264 | 0 | 0 | 0 | 1250.547 | 0 | 0
6809 | 1357.0867 | 12.73 | 29.1447 | 29.1447 | 0 | 0 | 0 | 1329.031 | 0 | 0
6810 | 968.9779 | 1.96 | 0 | 0 | 0 | 0 | 0 | 968.978 | 0 | 0
6811 | 859.4179 | 0 | 0 | 0 | 0 | 0 | 0 | 859.418 | 0 | 0
6812 | 666.613 | 0 | 0 | 0 | 0 | 0 | 0 | 666.613 | 0 | 0
6813 | 1020.8968 | 0 | 0 | 0 | 0 | 0 | 0 | 1020.897 | 0 | 0
6814 | 1041.8741 | 0 | 0 | 0 | 0 | 0 | 0 | 736 | 0 | 317.7434
6815 | 1133.5528 | 0 | 0 | 0 | 0 | 0 | 0 | 541.553 | 0 | 614.9724
6816 | 1121.8987 | 0 | 0 | 0 | 0 | 0 | 0 | 1121.899 | 0 | 0
6817 | 916.0101 | 0 | 0 | 0 | 0 | 0 | 0 | 916.01 | 0 | 0
6818 | 1391.4963 | 0 | 0 | 0 | 0 | 0 | 0 | 1391.496 | 0 | 0
6819 | 1013.9043 | 0 | 0 | 0 | 0 | 0 | 0 | 1013.904 | 0 | 0
6820 | 1124.2295 | 0 | 0 | 0 | 0 | 0 | 0 | 1124.23 | 0 | 0
6821 | 933.1028 | 0 | 0 | 0 | 0 | 0 | 0 | 933.103 | 0 | 0
6822 | 828.2161 | 0 | 0 | 0 | 0 | 0 | 0 | 828.216 | 0 | 0
6823 | 1121.5161 | 29.39 | 103.0515 | 103.0515 | 0 | 0 | 0 | 1022.314 | 0 | 0
6824 | 241.5452 | 124.11 | 541.3617 | 250.9181 | -290.4436 | 0 | 0 | 0 | 0 | 0
6825 | 286.4047 | 241.87 | 1072.7228 | 297.5189 | -614.9724 | 0 | 160.2315 | 0 | 0 | 0
6826 | 227.0213 | 466.31 | 2061.7324 | 235.8305 | -132.5951 | 0 | 1693.3068 | 0 | 0 | 0
6827 | 226.7086 | 630.09 | 2750.4537 | 235.5064 | 0 | 0 | 2514.9473 | 0 | 0 | 0
6828 | 265.6099 | 641.32 | 2789.8462 | 275.9159 | 0 | 0 | 2513.9303 | 0 | 0 | 0
6829 | 180.5099 | 620.14 | 2701.1188 | 187.5146 | 0 | 0 | 2513.6042 | 0 | 0 | 0
6830 | 244.417 | 387.58 | 1704.0065 | 253.9015 | 0 | 0 | 1450.1049 | 0 | 0 | 0
6831 | 281.7887 | 43.17 | 160.2637 | 160.2637 | 0 | 0 | 0 | 123.399 | 0 | 4.2726
6832 | 244.5879 | 32.35 | 114.8087 | 114.8087 | 0 | 0 | 0 | 0 | 0 | 139.2705
6833 | 259.577 | 100.57 | 429.3983 | 269.6498 | -159.7484 | 0 | 0 | 0 | 0 | 0
6834 | 261.3999 | 9.44 | 1.9935 | 1.9935 | 0 | 0 | 0 | 259.481 | 0 | 0
6835 | 181.0159 | 0 | 0 | 0 | 0 | 0 | 0 | 181.016 | 0 | 0
6836 | 341.8528 | 0 | 0 | 0 | 0 | 0 | 0 | 341.853 | 0 | 0
6837 | 203.5578 | 0 | 0 | 0 | 0 | 0 | 0 | 87.284 | 0 | 120.786
6838 | 261.8282 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 271.9882
6839 | 280.4747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 291.3588
6840 | 239.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 248.5829
6841 | 247.8433 | 0 | 0 | 0 | 0 | 0 | 0 | 247.843 | 0 | 0
6842 | 213.658 | 0 | 0 | 0 | 0 | 0 | 0 | 213.658 | 0 | 0
6843 | 278.9208 | 0 | 0 | 0 | 0 | 0 | 0 | 278.921 | 0 | 0
6844 | 284.3594 | 0 | 0 | 0 | 0 | 0 | 0 | 284.359 | 0 | 0
6845 | 227.6429 | 0 | 0 | 0 | 0 | 0 | 0 | 227.643 | 0 | 0
6846 | 224.5351 | 0 | 0 | 0 | 0 | 0 | 0 | 224.535 | 0 | 0
6847 | 211.1465 | 63.84 | 245.1236 | 219.3405 | -25.7831 | 0 | 0 | 0 | 0 | 0
6848 | 228.4266 | 394.31 | 1797.9799 | 237.29 | -614.9724 | 0 | 945.7175 | 0 | 0 | 0
6849 | 798.5303 | 287.98 | 1283.5388 | 829.5168 | -397.2556 | 0 | 56.7665 | 0 | 0 | 0
6850 | 1189.1388 | 485.15 | 2143.9725 | 1235.2832 | 0 | 0 | 908.6893 | 0 | 0 | 0
6851 | 1149.785 | 352.93 | 1542.3654 | 1194.4021 | 0 | 0 | 347.9632 | 0 | 0 | 0
6852 | 1049.2511 | 496.13 | 2156.9835 | 1089.9669 | 0 | 0 | 1067.0166 | 0 | 0 | 0
6853 | 1004.3509 | 635.55 | 2755.5397 | 1043.3246 | 0 | 0 | 1712.2151 | 0 | 0 | 0
6854 | 1250.2042 | 666.15 | 2904.2114 | 1298.7179 | 0 | 0 | 1605.4935 | 0 | 0 | 0
6855 | 903.8122 | 441.83 | 1957.6992 | 938.8842 | 0 | 0 | 1018.815 | 0 | 0 | 0
6856 | 1265.9984 | 208.1 | 923.9327 | 923.9327 | 0 | 0 | 0 | 376.58 | 0 | 0
6857 | 1338.141 | 9.79 | 16.3051 | 16.3051 | 0 | 0 | 0 | 1322.445 | 0 | 0
6858 | 1446.2015 | 6.55 | 0 | 0 | 0 | 0 | 0 | 1446.201 | 0 | 0
6859 | 1536.9168 | 0 | 0 | 0 | 0 | 0 | 0 | 1536.917 | 0 | 0
6860 | 1201.1464 | 0 | 0 | 0 | 0 | 0 | 0 | 1201.146 | 0 | 0
6861 | 1445.882 | 0 | 0 | 0 | 0 | 0 | 0 | 1445.882 | 0 | 0
6862 | 1395.381 | 0 | 0 | 0 | 0 | 0 | 0 | 1089.507 | 0 | 317.7434
6863 | 1485.5058 | 0 | 0 | 0 | 0 | 0 | 0 | 893.506 | 0 | 614.9724
6864 | 1257.086 | 0 | 0 | 0 | 0 | 0 | 0 | 1257.086 | 0 | 0
6865 | 1266.4092 | 0 | 0 | 0 | 0 | 0 | 0 | 1266.409 | 0 | 0
6866 | 1198.8156 | 0 | 0 | 0 | 0 | 0 | 0 | 1198.816 | 0 | 0
6867 | 1652.5475 | 0 | 0 | 0 | 0 | 0 | 0 | 1652.548 | 0 | 0
6868 | 1262.5245 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.525 | 0 | 0
6869 | 1325.4565 | 0 | 0 | 0 | 0 | 0 | 0 | 1325.457 | 0 | 0
6870 | 1463.7515 | 0 | 0 | 0 | 0 | 0 | 0 | 1463.752 | 0 | 0
6871 | 1647.1089 | 133.93 | 518.1963 | 518.1963 | 0 | 0 | 0 | 1148.27 | 0 | 0
6872 | 1347.642 | 289.23 | 1301.5704 | 1301.5704 | 0 | 0 | 0 | 94.692 | 0 | 0
6873 | 1537.3752 | 332.34 | 1467.8197 | 1467.8197 | 0 | 0 | 0 | 124.387 | 0 | 0
6874 | 2055.2559 | 580.22 | 2503.775 | 2135.0097 | -368.7653 | 0 | 0 | 0 | 0 | 0
6875 | 1950.1673 | 604.51 | 2585.1747 | 2025.8427 | -559.332 | 0 | 0 | 0 | 0 | 0
6876 | 1632.9415 | 632.58 | 2699.2562 | 1696.3079 | -109.9139 | 0 | 893.0345 | 0 | 0 | 0
6877 | 1578.9248 | 605.95 | 2594.4959 | 1640.1948 | 0 | 0 | 954.3011 | 0 | 0 | 0
6878 | 1500.0918 | 588.25 | 2548.1475 | 1558.3027 | 0 | 0 | 989.8448 | 0 | 0 | 0
6879 | 1560.4337 | 469.9 | 2073.9041 | 1620.9862 | 0 | 0 | 452.9178 | 0 | 0 | 0
6880 | 1354.9627 | 237.27 | 1056.3647 | 1056.3647 | 0 | 0 | 0 | 338.059 | 0 | 0
6881 | 1401.9869 | 135.36 | 577.7323 | 577.7323 | 0 | 0 | 0 | 845.835 | 0 | 0
6882 | 1511.5332 | 9.14 | 0 | 0 | 0 | 0 | 0 | 1511.533 | 0 | 0
6883 | 1511.2516 | 0 | 0 | 0 | 0 | 0 | 0 | 1511.252 | 0 | 0
6884 | 1042.651 | 0 | 0 | 0 | 0 | 0 | 0 | 1042.651 | 0 | 0
6885 | 1417.1352 | 0 | 0 | 0 | 0 | 0 | 0 | 1417.135 | 0 | 0
6886 | 1734.126 | 0 | 0 | 0 | 0 | 0 | 0 | 1428.252 | 0 | 317.7434
6887 | 1786.9578 | 0 | 0 | 0 | 0 | 0 | 0 | 1194.958 | 0 | 614.9724
6888 | 1498.7138 | 0 | 0 | 0 | 0 | 0 | 0 | 1498.714 | 0 | 0
6889 | 1306.0331 | 0 | 0 | 0 | 0 | 0 | 0 | 1306.033 | 0 | 0
6890 | 1539.8915 | 0 | 0 | 0 | 0 | 0 | 0 | 1539.891 | 0 | 0
6891 | 1354.9802 | 0 | 0 | 0 | 0 | 0 | 0 | 1354.98 | 0 | 0
6892 | 1587.2847 | 0 | 0 | 0 | 0 | 0 | 0 | 1587.285 | 0 | 0
6893 | 1386.8347 | 0 | 0 | 0 | 0 | 0 | 0 | 1386.835 | 0 | 0
6894 | 1682.8481 | 0 | 0 | 0 | 0 | 0 | 0 | 1682.848 | 0 | 0
6895 | 1314.5969 | 83.6 | 330.7284 | 330.7284 | 0 | 0 | 0 | 996.223 | 0 | 0
6896 | 1491.5815 | 236.77 | 1073.1601 | 1073.1601 | 0 | 0 | 0 | 458.509 | 0 | 0
6897 | 1238.8415 | 361.64 | 1630.6908 | 1286.9139 | -343.7768 | 0 | 0 | 0 | 0 | 0
6898 | 1931.0148 | 566.73 | 2520.7543 | 2005.9476 | -514.8067 | 0 | 0 | 0 | 0 | 0
6899 | 1849.8422 | 498.25 | 2196.7853 | 1921.6247 | -179.4286 | 0 | 95.7321 | 0 | 0 | 0
6900 | 1624.0727 | 848.19 | 3654.6564 | 1687.0937 | 0 | 0 | 1967.5627 | 0 | 0 | 0
6901 | 1805.6859 | 681.81 | 2968.5383 | 1875.7552 | 0 | 0 | 1092.7831 | 0 | 0 | 0
6902 | 1579.4376 | 655.97 | 2874.6241 | 1640.7277 | 0 | 0 | 1233.8964 | 0 | 0 | 0
6903 | 1451.8731 | 500.53 | 2234.5397 | 1508.2126 | 0 | 0 | 726.3271 | 0 | 0 | 0
6904 | 1128.7455 | 150.11 | 657.152 | 657.152 | 0 | 0 | 0 | 496.142 | 0 | 0
6905 | 1228.0848 | 29.39 | 103.1751 | 103.1751 | 0 | 0 | 0 | 1128.763 | 0 | 0
6906 | 1434.2978 | 1.96 | 0 | 0 | 0 | 0 | 0 | 1434.298 | 0 | 0
6907 | 1492.2516 | 0 | 0 | 0 | 0 | 0 | 0 | 1492.252 | 0 | 0
6908 | 1240.7703 | 0 | 0 | 0 | 0 | 0 | 0 | 1240.77 | 0 | 0
6909 | 1418.6891 | 0 | 0 | 0 | 0 | 0 | 0 | 1418.689 | 0 | 0
6910 | 1613.7006 | 0 | 0 | 0 | 0 | 0 | 0 | 1307.827 | 0 | 317.7434
6911 | 1366.6343 | 0 | 0 | 0 | 0 | 0 | 0 | 774.634 | 0 | 614.9724
6912 | 1386.8347 | 0 | 0 | 0 | 0 | 0 | 0 | 1386.835 | 0 | 0
6913 | 1509.5909 | 0 | 0 | 0 | 0 | 0 | 0 | 1509.591 | 0 | 0
6914 | 1275.7325 | 0 | 0 | 0 | 0 | 0 | 0 | 1275.732 | 0 | 0
6915 | 1501.8215 | 0 | 0 | 0 | 0 | 0 | 0 | 1501.822 | 0 | 0
6916 | 1306.0331 | 0 | 0 | 0 | 0 | 0 | 0 | 1306.033 | 0 | 0
6917 | 1323.1257 | 0 | 0 | 0 | 0 | 0 | 0 | 1323.126 | 0 | 0
6918 | 1096.2598 | 0 | 0 | 0 | 0 | 0 | 0 | 1096.26 | 0 | 0
6919 | 1443.5696 | 52.2 | 206.5466 | 206.5466 | 0 | 0 | 0 | 1244.739 | 0 | 0
6920 | 1285.1606 | 182.11 | 814.772 | 814.772 | 0 | 0 | 0 | 500.825 | 0 | 0
6921 | 1191.5872 | 350.95 | 1574.2006 | 1237.8262 | -336.3743 | 0 | 0 | 0 | 0 | 0
6922 | 1744.2447 | 358.61 | 1582.0716 | 1582.0716 | 0 | 0 | 0 | 0 | 0 | 229.8574
6923 | 1620.4415 | 509.44 | 2215.4963 | 1683.3218 | -532.1745 | 0 | 0 | 0 | 0 | 0
6924 | 1876.2766 | 699.5 | 2987.5277 | 1949.0844 | -425.27 | 0 | 613.1732 | 0 | 0 | 0
6925 | 1620.8484 | 803.71 | 3409.1899 | 1683.7446 | 0 | 0 | 1725.4453 | 0 | 0 | 0
6926 | 1712.8476 | 568.45 | 2473.6424 | 1779.3136 | 0 | 0 | 694.3288 | 0 | 0 | 0
6927 | 1534.4519 | 488.51 | 2169.8761 | 1593.996 | 0 | 0 | 575.8801 | 0 | 0 | 0
6928 | 1664.7066 | 72.95 | 300.7506 | 300.7506 | 0 | 0 | 0 | 1375.191 | 0 | 0
6929 | 1575.5306 | 21.55 | 68.2058 | 68.2058 | 0 | 0 | 0 | 1509.872 | 0 | 0
6930 | 1789.0993 | 1.96 | 0 | 0 | 0 | 0 | 0 | 1789.099 | 0 | 0
6931 | 1655.2046 | 0 | 0 | 0 | 0 | 0 | 0 | 1655.205 | 0 | 0
6932 | 1494.8291 | 0 | 0 | 0 | 0 | 0 | 0 | 1494.829 | 0 | 0
6933 | 1709.264 | 0 | 0 | 0 | 0 | 0 | 0 | 1709.264 | 0 | 0
6934 | 1697.6099 | 0 | 0 | 0 | 0 | 0 | 0 | 1391.736 | 0 | 317.7434
6935 | 1894.9522 | 0 | 0 | 0 | 0 | 0 | 0 | 1302.952 | 0 | 614.9724
6936 | 1490.1674 | 0 | 0 | 0 | 0 | 0 | 0 | 1490.167 | 0 | 0
6937 | 1436.5587 | 0 | 0 | 0 | 0 | 0 | 0 | 1436.559 | 0 | 0
6938 | 1714.7026 | 0 | 0 | 0 | 0 | 0 | 0 | 1714.703 | 0 | 0
6939 | 1420.243 | 0 | 0 | 0 | 0 | 0 | 0 | 1420.243 | 0 | 0
6940 | 1859.99 | 0 | 0 | 0 | 0 | 0 | 0 | 1859.99 | 0 | 0
6941 | 1577.9614 | 0 | 0 | 0 | 0 | 0 | 0 | 1577.961 | 0 | 0
6942 | 1522.7988 | 0 | 0 | 0 | 0 | 0 | 0 | 1522.799 | 0 | 0
6943 | 1380.6823 | 95 | 380.4768 | 380.4768 | 0 | 0 | 0 | 1014.418 | 0 | 0
6944 | 1445.3682 | 272.3 | 1244.2824 | 1244.2824 | 0 | 0 | 0 | 247.567 | 0 | 0
6945 | 1443.6317 | 489.94 | 2225.3203 | 1499.6518 | -614.9724 | 0 | 110.6961 | 0 | 0 | 0
6946 | 1751.3527 | 701.95 | 3119.4694 | 1819.3138 | -423.0387 | 0 | 877.1169 | 0 | 0 | 0
6947 | 1975.004 | 636.98 | 2802.2132 | 2051.6435 | 0 | 0 | 750.5697 | 0 | 0 | 0
6948 | 1647.8616 | 820.64 | 3562.4521 | 1711.8069 | 0 | 0 | 1850.6452 | 0 | 0 | 0
6949 | 1546.6392 | 747.1 | 3251.2033 | 1606.6559 | 0 | 0 | 1644.5474 | 0 | 0 | 0
6950 | 1415.4066 | 673.12 | 2960.2996 | 1470.3305 | 0 | 0 | 1489.9691 | 0 | 0 | 0
6951 | 1594.654 | 537.83 | 2409.009 | 1656.5341 | 0 | 0 | 752.4748 | 0 | 0 | 0
6952 | 1899.5274 | 183.75 | 817.4157 | 817.4157 | 0 | 0 | 0 | 1112.647 | 0 | 0
6953 | 1653.7527 | 58.02 | 226.8615 | 226.8615 | 0 | 0 | 0 | 1435.366 | 0 | 0
6954 | 1424.522 | 1.96 | 0 | 0 | 0 | 0 | 0 | 1424.522 | 0 | 0
6955 | 1615.5546 | 0 | 0 | 0 | 0 | 0 | 0 | 1615.555 | 0 | 0
6956 | 1257.086 | 0 | 0 | 0 | 0 | 0 | 0 | 1257.086 | 0 | 0
6957 | 1328.5643 | 0 | 0 | 0 | 0 | 0 | 0 | 1328.564 | 0 | 0
6958 | 1113.3524 | 0 | 0 | 0 | 0 | 0 | 0 | 807.479 | 0 | 317.7434
6959 | 1417.1352 | 0 | 0 | 0 | 0 | 0 | 0 | 825.135 | 0 | 614.9724
6960 | 1232.224 | 0 | 0 | 0 | 0 | 0 | 0 | 1232.224 | 0 | 0
6961 | 896.5867 | 0 | 0 | 0 | 0 | 0 | 0 | 896.587 | 0 | 0
6962 | 1312.2486 | 0 | 0 | 0 | 0 | 0 | 0 | 1312.249 | 0 | 0
6963 | 996.8117 | 0 | 0 | 0 | 0 | 0 | 0 | 996.812 | 0 | 0
6964 | 1216.6852 | 0 | 0 | 0 | 0 | 0 | 0 | 1216.685 | 0 | 0
6965 | 1229.1162 | 0 | 0 | 0 | 0 | 0 | 0 | 1229.116 | 0 | 0
6966 | 891.925 | 0 | 0 | 0 | 0 | 0 | 0 | 891.925 | 0 | 0
6967 | 1020.5365 | 56.27 | 225.7021 | 225.7021 | 0 | 0 | 0 | 803.266 | 0 | 0
6968 | 782.7914 | 200 | 902.606 | 813.167 | -89.439 | 0 | 0 | 0 | 0 | 0
6969 | 1064.2324 | 202.01 | 896.0065 | 896.0065 | 0 | 0 | 0 | 124.332 | 0 | 80.3661
6970 | 1233.7118 | 443.74 | 1977.3222 | 1281.5859 | -614.9724 | 0 | 80.764 | 0 | 0 | 0
6971 | 1280.4233 | 520.17 | 2291.8702 | 1330.1105 | -423.0387 | 0 | 538.721 | 0 | 0 | 0
6972 | 1104.2739 | 515.44 | 2264.1217 | 1147.1251 | 0 | 0 | 1116.9966 | 0 | 0 | 0
6973 | 1300.3109 | 663.35 | 2903.1829 | 1350.7692 | 0 | 0 | 1552.4137 | 0 | 0 | 0
6974 | 1092.2168 | 361.71 | 1599.1755 | 1134.6002 | 0 | 0 | 464.5753 | 0 | 0 | 0
6975 | 1134.3734 | 409.07 | 1835.0901 | 1178.3921 | 0 | 0 | 656.6981 | 0 | 0 | 0
6976 | 1436.7588 | 208.34 | 933.8855 | 933.8855 | 0 | 0 | 0 | 537.759 | 0 | 0
6977 | 1263.9143 | 104.13 | 445.4717 | 445.4717 | 0 | 0 | 0 | 835.083 | 0 | 0
6978 | 1435.7711 | 4.89 | 0 | 0 | 0 | 0 | 0 | 1435.771 | 0 | 0
6979 | 1114.3042 | 0 | 0 | 0 | 0 | 0 | 0 | 1114.304 | 0 | 0
6980 | 986.7115 | 0 | 0 | 0 | 0 | 0 | 0 | 986.711 | 0 | 0
6981 | 1394.604 | 0 | 0 | 0 | 0 | 0 | 0 | 1394.604 | 0 | 0
6982 | 1505.7062 | 0 | 0 | 0 | 0 | 0 | 0 | 1199.833 | 0 | 317.7434
6983 | 1400.0426 | 0 | 0 | 0 | 0 | 0 | 0 | 808.043 | 0 | 614.9724
6984 | 1386.8347 | 0 | 0 | 0 | 0 | 0 | 0 | 1386.835 | 0 | 0
6985 | 1262.5245 | 0 | 0 | 0 | 0 | 0 | 0 | 1262.525 | 0 | 0
6986 | 1246.9858 | 0 | 0 | 0 | 0 | 0 | 0 | 1246.986 | 0 | 0
6987 | 1582.6231 | 0 | 0 | 0 | 0 | 0 | 0 | 1582.623 | 0 | 0
6988 | 1398.4887 | 0 | 0 | 0 | 0 | 0 | 0 | 1398.489 | 0 | 0
6989 | 1537.5607 | 0 | 0 | 0 | 0 | 0 | 0 | 1537.561 | 0 | 0
6990 | 1553.8764 | 0 | 0 | 0 | 0 | 0 | 0 | 1553.876 | 0 | 0
6991 | 1107.5098 | 106.02 | 422.2419 | 422.2419 | 0 | 0 | 0 | 701.041 | 0 | 0
6992 | 198.9214 | 268.81 | 1229.5916 | 206.6401 | -614.9724 | 0 | 407.9791 | 0 | 0 | 0
6993 | 298.2132 | 541.94 | 2467.4979 | 309.7851 | -423.0387 | 0 | 1734.6741 | 0 | 0 | 0
6994 | 304.1927 | 481.41 | 2145.6107 | 315.9961 | 0 | 0 | 1829.6146 | 0 | 0 | 0
6995 | 345.2975 | 496.87 | 2187.8308 | 358.6962 | 0 | 0 | 1829.1347 | 0 | 0 | 0
6996 | 302.5368 | 724.97 | 3148.5247 | 314.2769 | 0 | 0 | 2834.2479 | 0 | 0 | 0
6997 | 291.076 | 317.85 | 1390.624 | 302.3711 | 0 | 0 | 1088.2529 | 0 | 0 | 0
6998 | 306.2603 | 535.89 | 2361.9272 | 318.1443 | 0 | 0 | 2043.7829 | 0 | 0 | 0
6999 | 275.21 | 556.99 | 2489.8706 | 285.8895 | 0 | 0 | 2203.9811 | 0 | 0 | 0
7000 | 224.034 | 387.61 | 1771.3023 | 232.7276 | 0 | 0 | 1538.5748 | 0 | 0 | 0
7001 | 243.4565 | 65.22 | 266.6799 | 252.9032 | 0 | 0 | 13.7766 | 0 | 0 | 0
7002 | 289.9125 | 3.91 | 0 | 0 | 0 | 0 | 0 | 289.913 | 0 | 0
7003 | 248.7805 | 0 | 0 | 0 | 0 | 0 | 0 | 248.78 | 0 | 0
7004 | 309.2214 | 0 | 0 | 0 | 0 | 0 | 0 | 309.221 | 0 | 0
7005 | 289.7979 | 0 | 0 | 0 | 0 | 0 | 0 | 82.622 | 0 | 215.2154
7006 | 230.7506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 239.7052
7007 | 296.7904 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 308.3069
7008 | 163.157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 169.4883
7009 | 222.2043 | 0 | 0 | 0 | 0 | 0 | 0 | 222.204 | 0 | 0
7010 | 219.8735 | 0 | 0 | 0 | 0 | 0 | 0 | 219.874 | 0 | 0
7011 | 215.2119 | 0 | 0 | 0 | 0 | 0 | 0 | 215.212 | 0 | 0
7012 | 131.3026 | 0 | 0 | 0 | 0 | 0 | 0 | 131.303 | 0 | 0
7013 | 144.5105 | 0 | 0 | 0 | 0 | 0 | 0 | 144.511 | 0 | 0
7014 | 197.3423 | 0 | 0 | 0 | 0 | 0 | 0 | 197.342 | 0 | 0
7015 | 135.9137 | 66.28 | 269.4358 | 141.1881 | -128.2477 | 0 | 0 | 0 | 0 | 0
7016 | 163.4921 | 233.01 | 1060.6051 | 169.8363 | -614.9724 | 0 | 275.7964 | 0 | 0 | 0
7017 | 970.3841 | 393.39 | 1787.382 | 1008.0395 | -294.791 | 0 | 484.5515 | 0 | 0 | 0
7018 | 1153.9649 | 485.7 | 2171.1185 | 1198.7443 | 0 | 0 | 972.3742 | 0 | 0 | 0
7019 | 1330.2706 | 754.1 | 3321.2312 | 1381.8908 | 0 | 0 | 1939.3404 | 0 | 0 | 0
7020 | 1342.4171 | 822.77 | 3598.805 | 1394.5092 | 0 | 0 | 2204.2959 | 0 | 0 | 0
7021 | 1361.5307 | 616.38 | 2721.6051 | 1414.3649 | 0 | 0 | 1307.2402 | 0 | 0 | 0
7022 | 1355.7183 | 265.9 | 1170.6291 | 1170.6291 | 0 | 0 | 0 | 228.818 | 0 | 0
7023 | 1394.876 | 198.79 | 873.2432 | 873.2432 | 0 | 0 | 0 | 554.253 | 0 | 0
7024 | 1538.6163 | 110.19 | 473.0436 | 473.0436 | 0 | 0 | 0 | 1083.244 | 0 | 0
7025 | 1416.4175 | 39.2 | 147.797 | 147.797 | 0 | 0 | 0 | 1274.142 | 0 | 0
7026 | 1352.2386 | 1.96 | 0 | 0 | 0 | 0 | 0 | 1352.239 | 0 | 0
7027 | 1554.2017 | 0 | 0 | 0 | 0 | 0 | 0 | 1554.202 | 0 | 0
7028 | 1215.1313 | 0 | 0 | 0 | 0 | 0 | 0 | 1215.131 | 0 | 0
7029 | 895.0328 | 0 | 0 | 0 | 0 | 0 | 0 | 895.033 | 0 | 0
7030 | 1180.946 | 0 | 0 | 0 | 0 | 0 | 0 | 875.072 | 0 | 317.7434
7031 | 1267.9631 | 0 | 0 | 0 | 0 | 0 | 0 | 675.963 | 0 | 614.9724
7032 | 849.9704 | 0 | 0 | 0 | 0 | 0 | 0 | 849.97 | 0 | 0
7033 | 1104.8061 | 0 | 0 | 0 | 0 | 0 | 0 | 1104.806 | 0 | 0
7034 | 738.0913 | 0 | 0 | 0 | 0 | 0 | 0 | 738.091 | 0 | 0
7035 | 1162.2995 | 0 | 0 | 0 | 0 | 0 | 0 | 1162.3 | 0 | 0
7036 | 1122.6757 | 0 | 0 | 0 | 0 | 0 | 0 | 1122.676 | 0 | 0
7037 | 1184.8307 | 0 | 0 | 0 | 0 | 0 | 0 | 1184.831 | 0 | 0
7038 | 1024.0045 | 0 | 0 | 0 | 0 | 0 | 0 | 1024.005 | 0 | 0
7039 | 1256.0216 | 53.72 | 213.5253 | 213.5253 | 0 | 0 | 0 | 1050.473 | 0 | 0
7040 | 1353.606 | 259.63 | 1183.6224 | 1183.6224 | 0 | 0 | 0 | 214.198 | 0 | 0
7041 | 1534.3568 | 211.41 | 939.6934 | 939.6934 | 0 | 0 | 0 | 629.766 | 0 | 0
7042 | 1602.1427 | 505.97 | 2253.3992 | 1664.3127 | -589.0864 | 0 | 0 | 0 | 0 | 0
7043 | 1628.6013 | 747.3 | 3275.5695 | 1691.7995 | -448.9247 | 0 | 1134.8454 | 0 | 0 | 0
7044 | 1636.1784 | 852.02 | 3701.1522 | 1699.6695 | 0 | 0 | 2001.4828 | 0 | 0 | 0
7045 | 1876.1804 | 868.28 | 3776.7752 | 1948.9857 | 0 | 0 | 1827.7894 | 0 | 0 | 0
7046 | 1679.1101 | 762.81 | 3363.469 | 1744.2674 | 0 | 0 | 1619.2016 | 0 | 0 | 0
7047 | 1605.5447 | 499.11 | 2243.3518 | 1667.8478 | 0 | 0 | 575.5041 | 0 | 0 | 0
7048 | 1427.7269 | 253.76 | 1146.8664 | 1146.8664 | 0 | 0 | 0 | 323.702 | 0 | 0
7049 | 1587.1934 | 167.6 | 706.1847 | 706.1847 | 0 | 0 | 0 | 907.388 | 0 | 0
7050 | 1493.7656 | 7.48 | 0 | 0 | 0 | 0 | 0 | 1493.766 | 0 | 0
7051 | 1428.0124 | 0 | 0 | 0 | 0 | 0 | 0 | 1428.012 | 0 | 0
7052 | 1214.3544 | 0 | 0 | 0 | 0 | 0 | 0 | 1214.354 | 0 | 0
7053 | 1286.6096 | 0 | 0 | 0 | 0 | 0 | 0 | 1286.61 | 0 | 0
7054 | 1485.5058 | 0 | 0 | 0 | 0 | 0 | 0 | 1179.632 | 0 | 317.7434
7055 | 1588.0616 | 0 | 0 | 0 | 0 | 0 | 0 | 996.062 | 0 | 614.9724
7056 | 1464.5285 | 0 | 0 | 0 | 0 | 0 | 0 | 1464.528 | 0 | 0
7057 | 943.9799 | 0 | 0 | 0 | 0 | 0 | 0 | 943.98 | 0 | 0
7058 | 1055.082 | 0 | 0 | 0 | 0 | 0 | 0 | 1055.082 | 0 | 0
7059 | 1517.3603 | 0 | 0 | 0 | 0 | 0 | 0 | 1517.36 | 0 | 0
7060 | 1184.8307 | 0 | 0 | 0 | 0 | 0 | 0 | 1184.831 | 0 | 0
7061 | 1555.4302 | 0 | 0 | 0 | 0 | 0 | 0 | 1555.43 | 0 | 0
7062 | 1419.4661 | 0 | 0 | 0 | 0 | 0 | 0 | 1419.466 | 0 | 0
7063 | 1509.6793 | 122.01 | 480.8793 | 480.8793 | 0 | 0 | 0 | 1046.763 | 0 | 0
7064 | 1222.5996 | 331.66 | 1525.2323 | 1270.0427 | -255.1897 | 0 | 0 | 0 | 0 | 0
7065 | 1098.0623 | 457.55 | 2076.0274 | 1140.6731 | -614.9724 | 0 | 320.3819 | 0 | 0 | 0
7066 | 1450.0124 | 587.93 | 2614.6331 | 1506.2804 | -167.849 | 0 | 940.5037 | 0 | 0 | 0
7067 | 1367.1296 | 628.25 | 2755.8119 | 1420.1811 | 0 | 0 | 1335.6307 | 0 | 0 | 0
7068 | 1547.1005 | 718.56 | 3124.9335 | 1607.1348 | 0 | 0 | 1517.7987 | 0 | 0 | 0
7069 | 1876.2222 | 766.01 | 3325.6139 | 1949.0283 | 0 | 0 | 1376.5856 | 0 | 0 | 0
7070 | 1289.5668 | 641.05 | 2817.8732 | 1339.6083 | 0 | 0 | 1478.2649 | 0 | 0 | 0
7071 | 1309.7799 | 94.97 | 395.0668 | 395.0668 | 0 | 0 | 0 | 929.471 | 0 | 0
7072 | 1430.0072 | 43.13 | 164.0252 | 164.0252 | 0 | 0 | 0 | 1272.11 | 0 | 0
7073 | 1378.6088 | 15.67 | 42.108 | 42.108 | 0 | 0 | 0 | 1338.074 | 0 | 0
7074 | 911.5146 | 0.98 | 0 | 0 | 0 | 0 | 0 | 911.515 | 0 | 0
7075 | 1308.9971 | 0 | 0 | 0 | 0 | 0 | 0 | 1308.997 | 0 | 0
7076 | 978.1652 | 0 | 0 | 0 | 0 | 0 | 0 | 978.165 | 0 | 0
7077 | 1111.0216 | 0 | 0 | 0 | 0 | 0 | 0 | 1111.022 | 0 | 0
7078 | 1313.0255 | 0 | 0 | 0 | 0 | 0 | 0 | 1007.152 | 0 | 317.7434
7079 | 1476.9595 | 0 | 0 | 0 | 0 | 0 | 0 | 884.959 | 0 | 614.9724
7080 | 1488.6136 | 0 | 0 | 0 | 0 | 0 | 0 | 1488.614 | 0 | 0
7081 | 1055.859 | 0 | 0 | 0 | 0 | 0 | 0 | 1055.859 | 0 | 0
7082 | 1290.4943 | 0 | 0 | 0 | 0 | 0 | 0 | 1290.494 | 0 | 0
7083 | 1036.4355 | 0 | 0 | 0 | 0 | 0 | 0 | 1036.436 | 0 | 0
7084 | 1038.7663 | 0 | 0 | 0 | 0 | 0 | 0 | 1038.766 | 0 | 0
7085 | 936.9874 | 0 | 0 | 0 | 0 | 0 | 0 | 936.987 | 0 | 0
7086 | 1198.0387 | 0 | 0 | 0 | 0 | 0 | 0 | 1198.039 | 0 | 0
7087 | 1205.407 | 126.2 | 496.4032 | 496.4032 | 0 | 0 | 0 | 727.547 | 0 | 0
7088 | 1106.8931 | 306.86 | 1411.3523 | 1149.8457 | -261.5066 | 0 | 0 | 0 | 0 | 0
7089 | 1442.5236 | 553.5 | 2520.4644 | 1498.5008 | -614.9724 | 0 | 406.9912 | 0 | 0 | 0
7090 | 1737.0055 | 665.29 | 2955.2852 | 1804.4101 | -161.5321 | 0 | 989.3431 | 0 | 0 | 0
7091 | 1443.4841 | 659.55 | 2886.0084 | 1499.498 | 0 | 0 | 1386.5104 | 0 | 0 | 0
7092 | 1588.2695 | 472.06 | 2062.472 | 1649.9014 | 0 | 0 | 412.5707 | 0 | 0 | 0
7093 | 1786.2343 | 802.33 | 3414.3829 | 1855.5484 | 0 | 0 | 1558.8346 | 0 | 0 | 0
7094 | 1390.1667 | 791.57 | 3387.1901 | 1444.1121 | 0 | 0 | 1943.078 | 0 | 0 | 0
7095 | 1677.3843 | 562.62 | 2465.8243 | 1742.4745 | 0 | 0 | 723.3499 | 0 | 0 | 0
7096 | 1676.6695 | 361.54 | 1630.4487 | 1630.4487 | 0 | 0 | 0 | 107.127 | 0 | 0
7097 | 1553.3917 | 121.01 | 508.1542 | 508.1542 | 0 | 0 | 0 | 1064.219 | 0 | 0
7098 | 1585.9659 | 4.22 | 0 | 0 | 0 | 0 | 0 | 1585.966 | 0 | 0
7099 | 1572.7909 | 0 | 0 | 0 | 0 | 0 | 0 | 1572.791 | 0 | 0
7100 | 1489.3905 | 0 | 0 | 0 | 0 | 0 | 0 | 1489.39 | 0 | 0
7101 | 1698.3869 | 0 | 0 | 0 | 0 | 0 | 0 | 1698.387 | 0 | 0
7102 | 1112.5755 | 0 | 0 | 0 | 0 | 0 | 0 | 806.702 | 0 | 317.7434
7103 | 1168.515 | 0 | 0 | 0 | 0 | 0 | 0 | 576.515 | 0 | 614.9724
7104 | 371.3765 | 0 | 0 | 0 | 0 | 0 | 0 | 371.376 | 0 | 0
7105 | 116.5407 | 0 | 0 | 0 | 0 | 0 | 0 | 116.541 | 0 | 0
7106 | 122.7562 | 0 | 0 | 0 | 0 | 0 | 0 | 122.756 | 0 | 0
7107 | 114.9869 | 0 | 0 | 0 | 0 | 0 | 0 | 114.987 | 0 | 0
7108 | 121.2024 | 0 | 0 | 0 | 0 | 0 | 0 | 121.202 | 0 | 0
7109 | 123.5332 | 0 | 0 | 0 | 0 | 0 | 0 | 123.533 | 0 | 0
7110 | 101.7789 | 0 | 0 | 0 | 0 | 0 | 0 | 101.779 | 0 | 0
7111 | 87.8474 | 83.05 | 326.9669 | 91.2559 | -235.711 | 0 | 0 | 0 | 0 | 0
7112 | 176.3999 | 236.06 | 1069.5825 | 183.2452 | -614.9724 | 0 | 271.3649 | 0 | 0 | 0
7113 | 1266.3005 | 155.49 | 677.0825 | 677.0825 | 0 | 0 | 0 | 614.511 | 0 | 0
7114 | 1548.0484 | 47.11 | 177.7634 | 177.7634 | 0 | 0 | 0 | 1233.09 | 0 | 149.4175
7115 | 1673.0266 | 147.66 | 626.0918 | 626.0918 | 0 | 0 | 0 | 478.323 | 0 | 614.9724
7116 | 1771.9988 | 556.23 | 2401.5099 | 1840.761 | -560.7489 | 0 | 0 | 0 | 0 | 0
7117 | 1494.0026 | 755.85 | 3223.3426 | 1551.9764 | -477.2622 | 0 | 1194.104 | 0 | 0 | 0
7118 | 1420.6499 | 540.58 | 2356.4984 | 1475.778 | 0 | 0 | 880.7205 | 0 | 0 | 0
7119 | 1712.2377 | 540.75 | 2403.9583 | 1778.681 | 0 | 0 | 625.2774 | 0 | 0 | 0
7120 | 1677.291 | 247.34 | 1114.0028 | 1114.0028 | 0 | 0 | 0 | 604.902 | 0 | 0
7121 | 1676.9667 | 8.81 | 12.3784 | 12.3784 | 0 | 0 | 0 | 1665.051 | 0 | 0
7122 | 1398.5489 | 0.98 | 0 | 0 | 0 | 0 | 0 | 1398.549 | 0 | 0
7123 | 1443.0422 | 0 | 0 | 0 | 0 | 0 | 0 | 1443.042 | 0 | 0
7124 | 1379.0653 | 0 | 0 | 0 | 0 | 0 | 0 | 1379.065 | 0 | 0
7125 | 1510.3678 | 0 | 0 | 0 | 0 | 0 | 0 | 1510.368 | 0 | 0
7126 | 1776.0807 | 0 | 0 | 0 | 0 | 0 | 0 | 1470.207 | 0 | 317.7434
7127 | 1299.0406 | 0 | 0 | 0 | 0 | 0 | 0 | 707.041 | 0 | 614.9724
7128 | 1407.035 | 0 | 0 | 0 | 0 | 0 | 0 | 1407.035 | 0 | 0
7129 | 1057.4129 | 0 | 0 | 0 | 0 | 0 | 0 | 1057.413 | 0 | 0
7130 | 1358.0879 | 0 | 0 | 0 | 0 | 0 | 0 | 1358.088 | 0 | 0
7131 | 1203.4772 | 0 | 0 | 0 | 0 | 0 | 0 | 1203.477 | 0 | 0
7132 | 1147.5377 | 0 | 0 | 0 | 0 | 0 | 0 | 1147.538 | 0 | 0
7133 | 1421.0199 | 0 | 0 | 0 | 0 | 0 | 0 | 1421.02 | 0 | 0
7134 | 1152.9763 | 0 | 0 | 0 | 0 | 0 | 0 | 1152.976 | 0 | 0
7135 | 1150.6454 | 31.36 | 112.0174 | 112.0174 | 0 | 0 | 0 | 1042.813 | 0 | 0
7136 | 1557.2327 | 91.31 | 390.6436 | 390.6436 | 0 | 0 | 0 | 1181.182 | 0 | 0
7137 | 1562.9559 | 34.32 | 123.248 | 123.248 | 0 | 0 | 0 | 1444.312 | 0 | 0
7138 | 1484.153 | 194.89 | 850.3271 | 850.3271 | 0 | 0 | 0 | 665.59 | 0 | 0
7139 | 1538.7348 | 679.17 | 2954.1613 | 1598.4452 | -614.9724 | 0 | 740.7436 | 0 | 0 | 0
7140 | 1370.921 | 657.2 | 2867.3972 | 1424.1192 | -423.0387 | 0 | 1020.2392 | 0 | 0 | 0
7141 | 1755.5239 | 166.42 | 711.9033 | 711.9033 | 0 | 0 | 0 | 1070.214 | 0 | 0
7142 | 1535.2541 | 260.15 | 1144.3941 | 1144.3941 | 0 | 0 | 0 | 433.609 | 0 | 0
7143 | 1077.4462 | 56.91 | 223.2298 | 223.2298 | 0 | 0 | 0 | 862.555 | 0 | 0
7144 | 1517.8449 | 76.51 | 317.9844 | 317.9844 | 0 | 0 | 0 | 1211.739 | 0 | 0
7145 | 1251.0074 | 98.36 | 417.7003 | 417.7003 | 0 | 0 | 0 | 848.911 | 0 | 0
7146 | 1642.0142 | 3.91 | 0 | 0 | 0 | 0 | 0 | 1642.014 | 0 | 0
7147 | 1603.6198 | 0 | 0 | 0 | 0 | 0 | 0 | 1603.62 | 0 | 0
7148 | 1352.6494 | 0 | 0 | 0 | 0 | 0 | 0 | 1352.649 | 0 | 0
7149 | 1404.7042 | 0 | 0 | 0 | 0 | 0 | 0 | 1404.704 | 0 | 0
7150 | 1233.7778 | 0 | 0 | 0 | 0 | 0 | 0 | 927.904 | 0 | 317.7434
7151 | 1466.0823 | 0 | 0 | 0 | 0 | 0 | 0 | 874.082 | 0 | 614.9724
7152 | 1573.2998 | 0 | 0 | 0 | 0 | 0 | 0 | 1573.3 | 0 | 0
7153 | 1475.4056 | 0 | 0 | 0 | 0 | 0 | 0 | 1475.406 | 0 | 0
7154 | 1317.6872 | 0 | 0 | 0 | 0 | 0 | 0 | 1317.687 | 0 | 0
7155 | 1793.9503 | 0 | 0 | 0 | 0 | 0 | 0 | 1793.95 | 0 | 0
7156 | 1639.3396 | 0 | 0 | 0 | 0 | 0 | 0 | 1639.34 | 0 | 0
7157 | 1427.2354 | 0 | 0 | 0 | 0 | 0 | 0 | 1427.235 | 0 | 0
7158 | 1366.6343 | 0 | 0 | 0 | 0 | 0 | 0 | 1366.634 | 0 | 0
7159 | 1260.9775 | 76.77 | 295.9721 | 295.9721 | 0 | 0 | 0 | 976.062 | 0 | 0
7160 | 331.6128 | 347.36 | 1599.0332 | 344.4812 | -614.9724 | 0 | 639.5796 | 0 | 0 | 0
7161 | 268.4554 | 386.29 | 1753.8618 | 278.8734 | -423.0387 | 0 | 1051.9498 | 0 | 0 | 0
7162 | 276.049 | 472.4 | 2123.8592 | 286.761 | 0 | 0 | 1837.0981 | 0 | 0 | 0
7163 | 261.2493 | 669.06 | 2978.0953 | 271.3867 | 0 | 0 | 2706.7086 | 0 | 0 | 0
7164 | 324.2289 | 815.69 | 3601.5257 | 336.8106 | 0 | 0 | 3264.715 | 0 | 0 | 0
7165 | 205.8624 | 876.13 | 3876.5326 | 213.8515 | 0 | 0 | 3662.6811 | 0 | 0 | 0
7166 | 205.1622 | 581.37 | 2608.6184 | 213.1243 | 0 | 0 | 2395.4941 | 0 | 0 | 0
7167 | 333.7513 | 566.08 | 2578.8764 | 346.7021 | 0 | 0 | 2232.1743 | 0 | 0 | 0
7168 | 381.8331 | 288.03 | 1322.9085 | 396.6499 | 0 | 0 | 926.2586 | 0 | 0 | 0
7169 | 308.0162 | 163.65 | 687.8394 | 319.9685 | 0 | 0 | 367.8709 | 0 | 0 | 0
7170 | 338.7742 | 8.27 | 0 | 0 | 0 | 0 | 0 | 338.774 | 0 | 0
7171 | 273.5706 | 0 | 0 | 0 | 0 | 0 | 0 | 273.571 | 0 | 0
7172 | 258.7204 | 0 | 0 | 0 | 0 | 0 | 0 | 258.72 | 0 | 0
7173 | 300.6751 | 0 | 0 | 0 | 0 | 0 | 0 | 57.76 | 0 | 252.3413
7174 | 283.5824 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 294.5863
7175 | 236.1892 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 245.3543
7176 | 135.1872 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140.4329
7177 | 138.295 | 0 | 0 | 0 | 0 | 0 | 0 | 138.295 | 0 | 0
7178 | 120.4254 | 0 | 0 | 0 | 0 | 0 | 0 | 120.425 | 0 | 0
7179 | 114.9869 | 0 | 0 | 0 | 0 | 0 | 0 | 114.987 | 0 | 0
7180 | 111.8791 | 0 | 0 | 0 | 0 | 0 | 0 | 111.879 | 0 | 0
7181 | 98.6711 | 0 | 0 | 0 | 0 | 0 | 0 | 98.671 | 0 | 0
7182 | 96.3403 | 0 | 0 | 0 | 0 | 0 | 0 | 96.34 | 0 | 0
7183 | 79.4371 | 140.73 | 541.2318 | 82.5195 | -458.7123 | 0 | 0 | 0 | 0 | 0
7184 | 86.9093 | 365.24 | 1679.0554 | 90.2815 | -579.2999 | 0 | 1009.4741 | 0 | 0 | 0
7185 | 86.5519 | 639.01 | 2910.2323 | 89.9106 | 0 | 0 | 2820.3216 | 0 | 0 | 0
7186 | 85.5428 | 820.55 | 3643.1776 | 88.8625 | 0 | 0 | 3554.3151 | 0 | 0 | 0
7187 | 82.0117 | 525.36 | 2326.7741 | 85.1934 | 0 | 0 | 2241.5807 | 0 | 0 | 0
7188 | 89.4741 | 555.48 | 2441.8259 | 92.946 | 0 | 0 | 2348.8799 | 0 | 0 | 0
7189 | 85.7196 | 644.5 | 2838.9391 | 89.0463 | 0 | 0 | 2749.8928 | 0 | 0 | 0
7190 | 90.0355 | 732.28 | 3244.4386 | 93.5298 | 0 | 0 | 3150.9088 | 0 | 0 | 0
7191 | 84.2988 | 115.75 | 490.1403 | 87.5702 | 0 | 0 | 402.5701 | 0 | 0 | 0
7192 | 95.4148 | 233.41 | 1054.1998 | 99.1176 | 0 | 0 | 955.0823 | 0 | 0 | 0
7193 | 85.638 | 30.37 | 107.4103 | 88.9612 | 0 | 0 | 18.4492 | 0 | 0 | 0
7194 | 92.1604 | 1.96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.7362
7195 | 99.1266 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.9736
7196 | 101.7789 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105.7285
7197 | 100.225 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.1142
7198 | 107.9944 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112.1847
7199 | 98.6711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.4999
7200 | 104.1097 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.15
7201 | 94.0095 | 0 | 0 | 0 | 0 | 0 | 0 | 94.01 | 0 | 0
7202 | 100.225 | 0 | 0 | 0 | 0 | 0 | 0 | 100.225 | 0 | 0
7203 | 97.1173 | 0 | 0 | 0 | 0 | 0 | 0 | 97.117 | 0 | 0
7204 | 98.6711 | 0 | 0 | 0 | 0 | 0 | 0 | 96.767 | 0 | 1.9779
7205 | 93.2326 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 96.8509
7206 | 98.6711 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.4999
7207 | 88.0252 | 101.11 | 395.5581 | 91.4408 | -304.1174 | 0 | 0 | 0 | 0 | 0
7208 | 138.2668 | 339.4 | 1549.7159 | 143.6314 | -614.9724 | 0 | 791.1121 | 0 | 0 | 0
7209 | 851.5291 | 558.92 | 2511.486 | 884.5713 | -118.9224 | 0 | 1507.9923 | 0 | 0 | 0
7210 | 1151.9371 | 803.56 | 3501.9157 | 1196.6376 | 0 | 0 | 2305.2781 | 0 | 0 | 0
7211 | 1368.5727 | 924.84 | 3948.4522 | 1421.6791 | 0 | 0 | 2526.7731 | 0 | 0 | 0
7212 | 1597.6423 | 779.49 | 3344.8993 | 1659.6381 | 0 | 0 | 1685.2613 | 0 | 0 | 0
7213 | 1506.7813 | 680.43 | 2946.3307 | 1565.2513 | 0 | 0 | 1381.0795 | 0 | 0 | 0
7214 | 1412.897 | 599.57 | 2631.014 | 1467.7241 | 0 | 0 | 1163.2899 | 0 | 0 | 0
7215 | 1414.7093 | 396.22 | 1765.323 | 1469.6064 | 0 | 0 | 295.7165 | 0 | 0 | 0
7216 | 1584.3586 | 224.19 | 1004.5346 | 1004.5346 | 0 | 0 | 0 | 617.349 | 0 | 0
7217 | 1584.5198 | 83.9 | 351.9419 | 351.9419 | 0 | 0 | 0 | 1245.725 | 0 | 0
7218 | 1715.024 | 2.94 | 0 | 0 | 0 | 0 | 0 | 1715.024 | 0 | 0
7219 | 1680.964 | 0 | 0 | 0 | 0 | 0 | 0 | 1680.964 | 0 | 0
7220 | 1793.1733 | 0 | 0 | 0 | 0 | 0 | 0 | 1793.173 | 0 | 0
7221 | 1675.8557 | 0 | 0 | 0 | 0 | 0 | 0 | 1675.856 | 0 | 0
7222 | 1509.5909 | 0 | 0 | 0 | 0 | 0 | 0 | 1203.717 | 0 | 317.7434
7223 | 1940.7916 | 0 | 0 | 0 | 0 | 0 | 0 | 1348.792 | 0 | 614.9724
7224 | 1651.7706 | 0 | 0 | 0 | 0 | 0 | 0 | 1651.771 | 0 | 0
7225 | 1884.852 | 0 | 0 | 0 | 0 | 0 | 0 | 1884.852 | 0 | 0
7226 | 1574.8537 | 0 | 0 | 0 | 0 | 0 | 0 | 1574.854 | 0 | 0
7227 | 1236.1086 | 0 | 0 | 0 | 0 | 0 | 0 | 1236.109 | 0 | 0
7228 | 1240.7703 | 0 | 0 | 0 | 0 | 0 | 0 | 1240.77 | 0 | 0
7229 | 1692.1714 | 0 | 0 | 0 | 0 | 0 | 0 | 1692.171 | 0 | 0
7230 | 1647.1089 | 0 | 0 | 0 | 0 | 0 | 0 | 1647.109 | 0 | 0
7231 | 1061.519 | 137.66 | 530.0896 | 530.0896 | 0 | 0 | 0 | 551.231 | 0 | 0
7232 | 1120.1186 | 381.55 | 1750.0411 | 1163.5839 | -586.4572 | 0 | 0 | 0 | 0 | 0
7233 | 1674.4572 | 564.2 | 2562.8965 | 1739.4328 | -451.5549 | 0 | 371.9087 | 0 | 0 | 0
7234 | 2076.6159 | 775.49 | 3442.9417 | 2157.1986 | 0 | 0 | 1285.7432 | 0 | 0 | 0
7235 | 1845.2748 | 883.27 | 3862.8588 | 1916.8794 | 0 | 0 | 1945.9794 | 0 | 0 | 0
7236 | 2071.6969 | 711.6 | 3111.7459 | 2152.0887 | 0 | 0 | 959.6572 | 0 | 0 | 0
7237 | 1651.0189 | 743.83 | 3254.675 | 1715.0864 | 0 | 0 | 1539.5886 | 0 | 0 | 0
7238 | 1496.2674 | 682.98 | 3023.7279 | 1554.3303 | 0 | 0 | 1469.3976 | 0 | 0 | 0
7239 | 1315.4865 | 58.87 | 231.8643 | 231.8643 | 0 | 0 | 0 | 1092.284 | 0 | 0
7240 | 1605.1611 | 248.35 | 1127.4158 | 1127.4158 | 0 | 0 | 0 | 519.861 | 0 | 0
7241 | 1758.8346 | 130.18 | 547.9851 | 547.9851 | 0 | 0 | 0 | 1231.319 | 0 | 0
7242 | 1473.3059 | 5.96 | 0 | 0 | 0 | 0 | 0 | 1473.306 | 0 | 0
7243 | 1812.4967 | 0 | 0 | 0 | 0 | 0 | 0 | 1812.497 | 0 | 0
7244 | 1695.2791 | 0 | 0 | 0 | 0 | 0 | 0 | 1695.279 | 0 | 0
7245 | 1998.285 | 0 | 0 | 0 | 0 | 0 | 0 | 1998.285 | 0 | 0
7246 | 1626.9086 | 0 | 0 | 0 | 0 | 0 | 0 | 1321.035 | 0 | 317.7434
7247 | 1615.2545 | 0 | 0 | 0 | 0 | 0 | 0 | 1023.254 | 0 | 614.9724
7248 | 1388.3885 | 0 | 0 | 0 | 0 | 0 | 0 | 1388.389 | 0 | 0
7249 | 1436.5587 | 0 | 0 | 0 | 0 | 0 | 0 | 1436.559 | 0 | 0
7250 | 1567.0843 | 0 | 0 | 0 | 0 | 0 | 0 | 1567.084 | 0 | 0
7251 | 991.3731 | 0 | 0 | 0 | 0 | 0 | 0 | 991.373 | 0 | 0
7252 | 1218.2391 | 0 | 0 | 0 | 0 | 0 | 0 | 1218.239 | 0 | 0
7253 | 1230.6701 | 0 | 0 | 0 | 0 | 0 | 0 | 1230.67 | 0 | 0
7254 | 1351.8724 | 0 | 0 | 0 | 0 | 0 | 0 | 1351.872 | 0 | 0
7255 | 1256.2333 | 44.27 | 171.595 | 171.595 | 0 | 0 | 0 | 1091.049 | 0 | 0
7256 | 631.5235 | 124.52 | 550.2507 | 550.2507 | 0 | 0 | 0 | 101.828 | 0 | 0
7257 | 1426.3624 | 204.61 | 912.1402 | 912.1402 | 0 | 0 | 0 | 548.296 | 0 | 0
7258 | 1434.29 | 608.15 | 2721.4628 | 1489.9473 | -614.9724 | 0 | 616.5431 | 0 | 0 | 0
7259 | 1329.046 | 591.66 | 2616.9154 | 1380.6193 | -423.0387 | 0 | 813.2574 | 0 | 0 | 0
7260 | 1071.6104 | 579.78 | 2553.9254 | 1113.1936 | 0 | 0 | 1440.7318 | 0 | 0 | 0
7261 | 1688.5431 | 485.84 | 2146.4272 | 1754.0665 | 0 | 0 | 392.3607 | 0 | 0 | 0
7262 | 1314.6289 | 196.59 | 855.892 | 855.892 | 0 | 0 | 0 | 490.709 | 0 | 0
7263 | 1623.5803 | 188.41 | 833.0165 | 833.0165 | 0 | 0 | 0 | 821.681 | 0 | 0
7264 | 1596.3166 | 81.44 | 340.8827 | 340.8827 | 0 | 0 | 0 | 1268.167 | 0 | 0
7265 | 1509.3432 | 63.11 | 257.8324 | 257.8324 | 0 | 0 | 0 | 1261.142 | 0 | 0
7266 | 1577.5497 | 1.96 | 0 | 0 | 0 | 0 | 0 | 1577.55 | 0 | 0
7267 | 1551.363 | 0 | 0 | 0 | 0 | 0 | 0 | 1551.363 | 0 | 0
7268 | 1267.9631 | 0 | 0 | 0 | 0 | 0 | 0 | 1267.963 | 0 | 0
7269 | 1587.2847 | 0 | 0 | 0 | 0 | 0 | 0 | 1587.285 | 0 | 0
7270 | 1797.835 | 0 | 0 | 0 | 0 | 0 | 0 | 1491.961 | 0 | 317.7434
7271 | 1567.0843 | 0 | 0 | 0 | 0 | 0 | 0 | 975.084 | 0 | 614.9724
7272 | 1323.9027 | 0 | 0 | 0 | 0 | 0 | 0 | 1323.903 | 0 | 0
7273 | 1209.6927 | 0 | 0 | 0 | 0 | 0 | 0 | 1209.693 | 0 | 0
7274 | 1199.5926 | 0 | 0 | 0 | 0 | 0 | 0 | 1199.593 | 0 | 0
7275 | 1285.8327 | 0 | 0 | 0 | 0 | 0 | 0 | 1285.833 | 0 | 0
7276 | 1353.4263 | 0 | 0 | 0 | 0 | 0 | 0 | 1353.426 | 0 | 0
7277 | 1157.6379 | 0 | 0 | 0 | 0 | 0 | 0 | 1157.638 | 0 | 0
7278 | 1076.0594 | 0 | 0 | 0 | 0 | 0 | 0 | 1076.059 | 0 | 0
7279 | 1040.5708 | 122.71 | 477.9458 | 477.9458 | 0 | 0 | 0 | 580.479 | 0 | 0
7280 | 680.187 | 346 | 1586.9446 | 706.5815 | -614.9724 | 0 | 265.3907 | 0 | 0 | 0
7281 | 1145.7167 | 562.58 | 2546.0834 | 1190.1763 | -423.0387 | 0 | 932.8685 | 0 | 0 | 0
7282 | 1580.9303 | 700.01 | 3093.6551 | 1642.2786 | 0 | 0 | 1451.3764 | 0 | 0 | 0
7283 | 1460.9439 | 632.81 | 2752.2041 | 1517.6356 | 0 | 0 | 1234.5685 | 0 | 0 | 0
7284 | 1561.3107 | 586.59 | 2541.8783 | 1621.8962 | 0 | 0 | 919.9821 | 0 | 0 | 0
7285 | 1658.8698 | 646.63 | 2800.4742 | 1723.242 | 0 | 0 | 1077.2322 | 0 | 0 | 0
7286 | 1697.236 | 335.97 | 1474.5023 | 1474.5023 | 0 | 0 | 0 | 0 | 0 | 288.5945
7287 | 1609.0448 | 522.66 | 2333.0256 | 1671.4836 | -321.1745 | 0 | 340.3675 | 0 | 0 | 0
7288 | 1884.7238 | 52.98 | 207.8711 | 207.8711 | 0 | 0 | 0 | 1684.618 | 0 | 0
7289 | 1429.3409 | 95.01 | 398.4502 | 398.4502 | 0 | 0 | 0 | 1045.775 | 0 | 0
7290 | 1778.5902 | 4.26 | 0 | 0 | 0 | 0 | 0 | 1778.59 | 0 | 0
7291 | 1691.5158 | 0 | 0 | 0 | 0 | 0 | 0 | 1691.516 | 0 | 0
7292 | 1294.379 | 0 | 0 | 0 | 0 | 0 | 0 | 1294.379 | 0 | 0
7293 | 1858.4361 | 0 | 0 | 0 | 0 | 0 | 0 | 1858.436 | 0 | 0
7294 | 1860.7669 | 0 | 0 | 0 | 0 | 0 | 0 | 1554.893 | 0 | 317.7434
7295 | 1745.7801 | 0 | 0 | 0 | 0 | 0 | 0 | 1153.78 | 0 | 614.9724
7296 | 1270.2939 | 0 | 0 | 0 | 0 | 0 | 0 | 1270.294 | 0 | 0
7297 | 979.2 | 0 | 0 | 0 | 0 | 0 | 0 | 979.2 | 0 | 0
7298 | 1126.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1126.4 | 0 | 0
7299 | 942.4 | 0 | 0 | 0 | 0 | 0 | 0 | 942.4 | 0 | 0
7300 | 1153.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1153.6 | 0 | 0
7301 | 813.6 | 0 | 0 | 0 | 0 | 0 | 0 | 813.6 | 0 | 0
7302 | 752.8 | 0 | 0 | 0 | 0 | 0 | 0 | 752.8 | 0 | 0
7303 | 972.165 | 83.85 | 335.0166 | 335.0166 | 0 | 0 | 0 | 649.663 | 0 | 0
7304 | 714.13 | 118.74 | 518.6337 | 518.6337 | 0 | 0 | 0 | 214.87 | 0 | 0
7305 | 999.303 | 360.31 | 1623.5469 | 1038.0807 | -585.4662 | 0 | 0 | 0 | 0 | 0
7306 | 1215.461 | 671.32 | 2950.1577 | 1262.6277 | -452.5449 | 0 | 1234.9851 | 0 | 0 | 0
7307 | 1450.762 | 927.84 | 3909.4378 | 1507.0585 | 0 | 0 | 2402.3793 | 0 | 0 | 0
7308 | 1203.09 | 831.32 | 3474.6461 | 1249.7756 | 0 | 0 | 2224.8705 | 0 | 0 | 0
7309 | 1458.605 | 662.5 | 2788.0076 | 1515.2058 | 0 | 0 | 1272.8018 | 0 | 0 | 0
7310 | 1394.271 | 597.71 | 2526.0231 | 1448.3753 | 0 | 0 | 1077.6477 | 0 | 0 | 0
7311 | 1158.39 | 477.03 | 2080.3675 | 1203.341 | 0 | 0 | 877.0265 | 0 | 0 | 0
7312 | 1214.189 | 361.53 | 1620.2227 | 1261.3053 | 0 | 0 | 358.9174 | 0 | 0 | 0
7313 | 1159.956 | 154.49 | 638.6052 | 638.6052 | 0 | 0 | 0 | 545.206 | 0 | 0
7314 | 1375.523 | 2.94 | 0 | 0 | 0 | 0 | 0 | 1375.523 | 0 | 0
7315 | 1310.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1310.4 | 0 | 0
7316 | 1376 | 0 | 0 | 0 | 0 | 0 | 0 | 1376 | 0 | 0
7317 | 1444 | 0 | 0 | 0 | 0 | 0 | 0 | 1444 | 0 | 0
7318 | 890.4 | 0 | 0 | 0 | 0 | 0 | 0 | 584.526 | 0 | 317.7434
7319 | 1152 | 0 | 0 | 0 | 0 | 0 | 0 | 560 | 0 | 614.9724
7320 | 1338.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1338.4 | 0 | 0
7321 | 1149.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1149.6 | 0 | 0
7322 | 1115.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1115.2 | 0 | 0
7323 | 995.2 | 0 | 0 | 0 | 0 | 0 | 0 | 995.2 | 0 | 0
7324 | 1403.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1403.2 | 0 | 0
7325 | 927.2 | 0 | 0 | 0 | 0 | 0 | 0 | 927.2 | 0 | 0
7326 | 899.2 | 0 | 0 | 0 | 0 | 0 | 0 | 899.2 | 0 | 0
7327 | 729.6 | 81.05 | 323.4661 | 323.4661 | 0 | 0 | 0 | 418.217 | 0 | 0
7328 | 1140.583 | 292.1 | 1314.8245 | 1184.843 | -129.9815 | 0 | 0 | 0 | 0 | 0
7329 | 1125.237 | 460.31 | 2033.9132 | 1168.9015 | -614.9724 | 0 | 250.0393 | 0 | 0 | 0
7330 | 1053.168 | 646.62 | 2781.6262 | 1094.0349 | -293.0582 | 0 | 1394.533 | 0 | 0 | 0
7331 | 1214.887 | 736.09 | 3117.3222 | 1262.0304 | 0 | 0 | 1855.2918 | 0 | 0 | 0
7332 | 1367.312 | 821.74 | 3449.5953 | 1420.3702 | 0 | 0 | 2029.2251 | 0 | 0 | 0
7333 | 1412.702 | 629.21 | 2686.2275 | 1467.5215 | 0 | 0 | 1218.706 | 0 | 0 | 0
7334 | 992.147 | 456.85 | 1985.6493 | 1030.647 | 0 | 0 | 955.0023 | 0 | 0 | 0
7335 | 979.152 | 311.56 | 1372.3494 | 1017.1477 | 0 | 0 | 355.2016 | 0 | 0 | 0
7336 | 1263.475 | 275.25 | 1235.1098 | 1235.1098 | 0 | 0 | 0 | 74.503 | 0 | 0
7337 | 1350.183 | 172.84 | 709.3842 | 709.3842 | 0 | 0 | 0 | 667.298 | 0 | 0
7338 | 1374.738 | 1.96 | 0 | 0 | 0 | 0 | 0 | 1374.738 | 0 | 0
7339 | 1219.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1219.2 | 0 | 0
7340 | 1216 | 0 | 0 | 0 | 0 | 0 | 0 | 1216 | 0 | 0
7341 | 1084.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1084.8 | 0 | 0
7342 | 1232 | 0 | 0 | 0 | 0 | 0 | 0 | 1232 | 0 | 0
7343 | 838.4 | 0 | 0 | 0 | 0 | 0 | 0 | 838.4 | 0 | 0
7344 | 932 | 0 | 0 | 0 | 0 | 0 | 0 | 583.669 | 0 | 361.8479
7345 | 870.547 | 0 | 0 | 0 | 0 | 0 | 0 | 870.547 | 0 | 0
7346 | 870.2682 | 0 | 0 | 0 | 0 | 0 | 0 | 870.268 | 0 | 0
7347 | 862.4134 | 0 | 0 | 0 | 0 | 0 | 0 | 862.413 | 0 | 0
7348 | 826.5843 | 0 | 0 | 0 | 0 | 0 | 0 | 826.584 | 0 | 0
7349 | 819.3456 | 0 | 0 | 0 | 0 | 0 | 0 | 819.346 | 0 | 0
7350 | 813.6014 | 0 | 0 | 0 | 0 | 0 | 0 | 813.601 | 0 | 0
7351 | 903.9083 | 92.31 | 368.1171 | 368.1171 | 0 | 0 | 0 | 0 | 0 | 570.8668
7352 | 791.2837 | 315.48 | 1437.3328 | 821.9896 | -614.9724 | 0 | 0.37085 | 0 | 0 | 0
7353 | 1005.2559 | 518.88 | 2307.1937 | 1044.2647 | -423.0387 | 0 | 839.8903 | 0 | 0 | 0
7354 | 1195.4363 | 637.77 | 2748.5548 | 1241.8246 | 0 | 0 | 1506.7302 | 0 | 0 | 0
7355 | 1226.7781 | 933.73 | 3841.6755 | 1274.3828 | 0 | 0 | 2567.2927 | 0 | 0 | 0
7356 | 1217.1598 | 884.58 | 3623.2242 | 1264.3916 | 0 | 0 | 2358.8326 | 0 | 0 | 0
7357 | 1234.1608 | 775.12 | 3187.8175 | 1282.0523 | 0 | 0 | 1905.7652 | 0 | 0 | 0
7358 | 1231.0896 | 685.1 | 2871.2054 | 1278.8611 | 0 | 0 | 1592.3443 | 0 | 0 | 0
7359 | 1249.2235 | 479.27 | 2081.2256 | 1297.6998 | 0 | 0 | 783.5258 | 0 | 0 | 0
7360 | 1250.9173 | 352.17 | 1571.616 | 1299.4585 | 0 | 0 | 272.1575 | 0 | 0 | 0
7361 | 1257.5245 | 146.74 | 600.3066 | 600.3066 | 0 | 0 | 0 | 679.643 | 0 | 0
7362 | 1230.4932 | 2.94 | 0 | 0 | 0 | 0 | 0 | 1230.493 | 0 | 0
7363 | 1196.9072 | 0 | 0 | 0 | 0 | 0 | 0 | 1196.907 | 0 | 0
7364 | 1113.5542 | 0 | 0 | 0 | 0 | 0 | 0 | 1113.554 | 0 | 0
7365 | 1185.424 | 0 | 0 | 0 | 0 | 0 | 0 | 1185.424 | 0 | 0
7366 | 1185.7689 | 0 | 0 | 0 | 0 | 0 | 0 | 879.895 | 0 | 317.7434
7367 | 1162.3773 | 0 | 0 | 0 | 0 | 0 | 0 | 570.377 | 0 | 614.9724
7368 | 889.2698 | 0 | 0 | 0 | 0 | 0 | 0 | 889.27 | 0 | 0
7369 | 85.6 | 0 | 0 | 0 | 0 | 0 | 0 | 85.6 | 0 | 0
7370 | 91.2 | 0 | 0 | 0 | 0 | 0 | 0 | 91.2 | 0 | 0
7371 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 84 | 0 | 0
7372 | 87.2 | 0 | 0 | 0 | 0 | 0 | 0 | 87.2 | 0 | 0
7373 | 81.6 | 0 | 0 | 0 | 0 | 0 | 0 | 81.6 | 0 | 0
7374 | 85.6 | 0 | 0 | 0 | 0 | 0 | 0 | 85.6 | 0 | 0
7375 | 65.492 | 19.59 | 58.9335 | 58.9335 | 0 | 0 | 0 | 8.76 | 0 | 0
7376 | 93.277 | 34.3 | 125.5541 | 96.8966 | -28.6575 | 0 | 0 | 0 | 0 | 0
7377 | 618.406 | 351.42 | 1563.0646 | 642.4031 | -614.9724 | 0 | 305.6891 | 0 | 0 | 0
7378 | 770.837 | 545.52 | 2369.2664 | 800.7491 | -394.3812 | 0 | 1174.1361 | 0 | 0 | 0
7379 | 1352.587 | 685.08 | 2909.1498 | 1405.0738 | 0 | 0 | 1504.076 | 0 | 0 | 0
7380 | 1093.259 | 793.87 | 3321.3559 | 1135.6826 | 0 | 0 | 2185.6732 | 0 | 0 | 0
7381 | 1179.255 | 775.79 | 3265.249 | 1225.0157 | 0 | 0 | 2040.2333 | 0 | 0 | 0
7382 | 1555.276 | 644.34 | 2773.0332 | 1615.6281 | 0 | 0 | 1157.4051 | 0 | 0 | 0
7383 | 1278.067 | 559.79 | 2464.7783 | 1327.6621 | 0 | 0 | 1137.1162 | 0 | 0 | 0
7384 | 1480.787 | 296.88 | 1335.0791 | 1335.0791 | 0 | 0 | 0 | 195.58 | 0 | 0
7385 | 1756.931 | 152.64 | 633.5431 | 633.5431 | 0 | 0 | 0 | 1147.054 | 0 | 0
7386 | 1617.657 | 3.15 | 0 | 0 | 0 | 0 | 0 | 1617.657 | 0 | 0
7387 | 1474.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1474.4 | 0 | 0
7388 | 1431.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1431.2 | 0 | 0
7389 | 1365.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1365.6 | 0 | 0
7390 | 1100.8 | 0 | 0 | 0 | 0 | 0 | 0 | 794.926 | 0 | 317.7434
7391 | 1292.8 | 0 | 0 | 0 | 0 | 0 | 0 | 700.8 | 0 | 614.9724
7392 | 1215.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1215.2 | 0 | 0
7393 | 949.6 | 0 | 0 | 0 | 0 | 0 | 0 | 949.6 | 0 | 0
7394 | 1412.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1412.8 | 0 | 0
7395 | 1319.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1319.2 | 0 | 0
7396 | 1212.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1212.8 | 0 | 0
7397 | 1012 | 0 | 0 | 0 | 0 | 0 | 0 | 1012 | 0 | 0
7398 | 1101.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1101.6 | 0 | 0
7399 | 1240.205 | 128.12 | 495.4694 | 495.4694 | 0 | 0 | 0 | 763.244 | 0 | 0
7400 | 972.841 | 339.25 | 1537.9951 | 1010.5919 | -527.4032 | 0 | 0 | 0 | 0 | 0
7401 | 1091.276 | 613.4 | 2725.0705 | 1133.6227 | -510.6079 | 0 | 1080.84 | 0 | 0 | 0
7402 | 1317.246 | 668.43 | 2886.4935 | 1368.3614 | 0 | 0 | 1518.1321 | 0 | 0 | 0
7403 | 1461.008 | 804.34 | 3375.9118 | 1517.702 | 0 | 0 | 1858.2098 | 0 | 0 | 0
7404 | 1485.364 | 800.33 | 3329.4222 | 1543.0032 | 0 | 0 | 1786.419 | 0 | 0 | 0
7405 | 1859.342 | 742.79 | 3092.9684 | 1931.4933 | 0 | 0 | 1161.4751 | 0 | 0 | 0
7406 | 1111.595 | 786.91 | 3296.7591 | 1154.7302 | 0 | 0 | 2142.0289 | 0 | 0 | 0
7407 | 1623.432 | 601.18 | 2616.9808 | 1686.4289 | 0 | 0 | 930.5519 | 0 | 0 | 0
7408 | 1529.712 | 236.96 | 1052.5855 | 1052.5855 | 0 | 0 | 0 | 516.446 | 0 | 0
7409 | 1351.591 | 114.64 | 476.2722 | 476.2722 | 0 | 0 | 0 | 893.11 | 0 | 0
7410 | 1119.86 | 3.15 | 0 | 0 | 0 | 0 | 0 | 1119.86 | 0 | 0
7411 | 915.2 | 0 | 0 | 0 | 0 | 0 | 0 | 915.2 | 0 | 0
7412 | 1072.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1072.8 | 0 | 0
7413 | 1204 | 0 | 0 | 0 | 0 | 0 | 0 | 1204 | 0 | 0
7414 | 921.6 | 0 | 0 | 0 | 0 | 0 | 0 | 615.726 | 0 | 317.7434
7415 | 1499.2 | 0 | 0 | 0 | 0 | 0 | 0 | 907.2 | 0 | 614.9724
7416 | 1340 | 0 | 0 | 0 | 0 | 0 | 0 | 1340 | 0 | 0
7417 | 1268 | 0 | 0 | 0 | 0 | 0 | 0 | 1268 | 0 | 0
7418 | 1223.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1223.2 | 0 | 0
7419 | 1244.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1244.8 | 0 | 0
7420 | 1196 | 0 | 0 | 0 | 0 | 0 | 0 | 1196 | 0 | 0
7421 | 920 | 0 | 0 | 0 | 0 | 0 | 0 | 920 | 0 | 0
7422 | 1409.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1409.6 | 0 | 0
7423 | 1301.174 | 48.48 | 188.4911 | 188.4911 | 0 | 0 | 0 | 1119.724 | 0 | 0
7424 | 900.704 | 145.41 | 644.1296 | 644.1296 | 0 | 0 | 0 | 280.636 | 0 | 0
7425 | 1025.232 | 73.26 | 299.6443 | 299.6443 | 0 | 0 | 0 | 736.781 | 0 | 0
7426 | 1161.734 | 343.28 | 1514.569 | 1206.8148 | -307.7542 | 0 | 0 | 0 | 0 | 0
7427 | 1161.093 | 510.05 | 2218.5483 | 1206.1489 | -614.9724 | 0 | 397.427 | 0 | 0 | 0
7428 | 1382.406 | 466.93 | 2021.512 | 1436.0499 | -115.2845 | 0 | 470.1776 | 0 | 0 | 0
7429 | 1308.312 | 467.01 | 2019.424 | 1359.0807 | 0 | 0 | 660.3432 | 0 | 0 | 0
7430 | 1078.045 | 437.25 | 1898.4531 | 1119.8783 | 0 | 0 | 778.5748 | 0 | 0 | 0
7431 | 1313.362 | 346.46 | 1523.7656 | 1364.3267 | 0 | 0 | 159.4389 | 0 | 0 | 0
7432 | 1419.024 | 140.59 | 609.4086 | 609.4086 | 0 | 0 | 0 | 832.38 | 0 | 0
7433 | 1209.14 | 79.89 | 329.6231 | 329.6231 | 0 | 0 | 0 | 891.83 | 0 | 0
7434 | 1214.131 | 0.98 | 0 | 0 | 0 | 0 | 0 | 1214.131 | 0 | 0
7435 | 1495.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1495.2 | 0 | 0
7436 | 1044.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1044.8 | 0 | 0
7437 | 1540.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1540.8 | 0 | 0
7438 | 1288 | 0 | 0 | 0 | 0 | 0 | 0 | 982.126 | 0 | 317.7434
7439 | 1128.8 | 0 | 0 | 0 | 0 | 0 | 0 | 536.8 | 0 | 614.9724
7440 | 1216 | 0 | 0 | 0 | 0 | 0 | 0 | 1216 | 0 | 0
7441 | 784.8 | 0 | 0 | 0 | 0 | 0 | 0 | 784.8 | 0 | 0
7442 | 1167.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1167.2 | 0 | 0
7443 | 1024 | 0 | 0 | 0 | 0 | 0 | 0 | 1024 | 0 | 0
7444 | 1230.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1230.4 | 0 | 0
7445 | 1207.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1207.2 | 0 | 0
7446 | 961.6 | 0 | 0 | 0 | 0 | 0 | 0 | 961.6 | 0 | 0
7447 | 1106.751 | 104.12 | 415.7837 | 415.7837 | 0 | 0 | 0 | 706.499 | 0 | 0
7448 | 981.304 | 347.9 | 1598.0578 | 1019.3833 | -578.6745 | 0 | 0 | 0 | 0 | 0
7449 | 1087.115 | 588.28 | 2679.1606 | 1129.3013 | -459.3366 | 0 | 1090.5227 | 0 | 0 | 0
7450 | 1162.094 | 780.12 | 3451.7124 | 1207.1888 | 0 | 0 | 2244.5236 | 0 | 0 | 0
7451 | 1710.031 | 734.77 | 3226.1224 | 1776.3883 | 0 | 0 | 1449.7341 | 0 | 0 | 0
7452 | 1447.547 | 765.88 | 3342.214 | 1503.7187 | 0 | 0 | 1838.4953 | 0 | 0 | 0
7453 | 1355.19 | 563.09 | 2468.279 | 1407.7778 | 0 | 0 | 1060.5012 | 0 | 0 | 0
7454 | 1224.544 | 610.74 | 2701.9052 | 1272.0621 | 0 | 0 | 1429.8431 | 0 | 0 | 0
7455 | 1435.996 | 359.68 | 1612.4992 | 1491.7195 | 0 | 0 | 120.7798 | 0 | 0 | 0
7456 | 1576.816 | 336.78 | 1540.4664 | 1540.4664 | 0 | 0 | 0 | 93.894 | 0 | 0
7457 | 1545.343 | 161.88 | 674.178 | 674.178 | 0 | 0 | 0 | 896.349 | 0 | 0
7458 | 1644.762 | 1.96 | 0 | 0 | 0 | 0 | 0 | 1644.762 | 0 | 0
7459 | 1521.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1521.6 | 0 | 0
7460 | 1470.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1470.4 | 0 | 0
7461 | 1567.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1567.2 | 0 | 0
7462 | 1155.2 | 0 | 0 | 0 | 0 | 0 | 0 | 849.326 | 0 | 317.7434
7463 | 1411.2 | 0 | 0 | 0 | 0 | 0 | 0 | 819.2 | 0 | 614.9724
7464 | 1588.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1588.8 | 0 | 0
7465 | 1478.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1478.4 | 0 | 0
7466 | 1609.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1609.6 | 0 | 0
7467 | 1016 | 0 | 0 | 0 | 0 | 0 | 0 | 1016 | 0 | 0
7468 | 1200 | 0 | 0 | 0 | 0 | 0 | 0 | 1200 | 0 | 0
7469 | 1240 | 0 | 0 | 0 | 0 | 0 | 0 | 1240 | 0 | 0
7470 | 1102.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1102.4 | 0 | 0
7471 | 1127.493 | 55.02 | 217.5174 | 217.5174 | 0 | 0 | 0 | 918.101 | 0 | 0
7472 | 1108.431 | 91.14 | 389.5019 | 389.5019 | 0 | 0 | 0 | 733.479 | 0 | 0
7473 | 1506.879 | 227.17 | 1003.9965 | 1003.9965 | 0 | 0 | 0 | 540.387 | 0 | 0
7474 | 1545.101 | 316.88 | 1381.3859 | 1381.3859 | 0 | 0 | 0 | 215.317 | 0 | 0
7475 | 1717.536 | 757.06 | 3164.7883 | 1784.1846 | -614.9724 | 0 | 765.6313 | 0 | 0 | 0
7476 | 1743.337 | 897.05 | 3672.1208 | 1810.9868 | -423.0387 | 0 | 1438.0953 | 0 | 0 | 0
7477 | 1659.288 | 881.42 | 3651.4631 | 1723.6763 | 0 | 0 | 1927.7868 | 0 | 0 | 0
7478 | 1711.846 | 824.31 | 3486.4209 | 1778.2738 | 0 | 0 | 1708.1472 | 0 | 0 | 0
7479 | 1778.711 | 300.73 | 1321.2765 | 1321.2765 | 0 | 0 | 0 | 506.791 | 0 | 0
7480 | 1671.964 | 311.63 | 1399.2586 | 1399.2586 | 0 | 0 | 0 | 324.975 | 0 | 0
7481 | 1740.399 | 7.83 | 7.7765 | 7.7765 | 0 | 0 | 0 | 1732.913 | 0 | 0
7482 | 1561.823 | 0 | 0 | 0 | 0 | 0 | 0 | 1561.823 | 0 | 0
7483 | 1636 | 0 | 0 | 0 | 0 | 0 | 0 | 1636 | 0 | 0
7484 | 1423.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1423.2 | 0 | 0
7485 | 1198.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1198.4 | 0 | 0
7486 | 1556.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1250.926 | 0 | 317.7434
7487 | 1191.2 | 0 | 0 | 0 | 0 | 0 | 0 | 599.2 | 0 | 614.9724
7488 | 1529.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1529.6 | 0 | 0
7489 | 1598.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1598.4 | 0 | 0
7490 | 1415.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1415.2 | 0 | 0
7491 | 1582.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1582.4 | 0 | 0
7492 | 1364.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1364.8 | 0 | 0
7493 | 1329.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1329.6 | 0 | 0
7494 | 1695.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1695.2 | 0 | 0
7495 | 1435.98 | 55.23 | 208.699 | 208.699 | 0 | 0 | 0 | 1235.077 | 0 | 0
7496 | 1870.081 | 281.17 | 1293.0844 | 1293.0844 | 0 | 0 | 0 | 625.3 | 0 | 0
7497 | 1222.75 | 476.72 | 2164.4941 | 1270.1985 | -614.9724 | 0 | 279.3232 | 0 | 0 | 0
7498 | 1723.893 | 679.54 | 2985.6298 | 1790.7882 | -423.0387 | 0 | 771.8028 | 0 | 0 | 0
7499 | 1512.119 | 625.15 | 2708.1858 | 1570.7964 | 0 | 0 | 1137.3894 | 0 | 0 | 0
7500 | 1701.586 | 783.23 | 3329.9073 | 1767.6156 | 0 | 0 | 1562.2917 | 0 | 0 | 0
7501 | 1506.384 | 628.5 | 2694.7613 | 1564.8389 | 0 | 0 | 1129.9225 | 0 | 0 | 0
7502 | 1400.986 | 425.31 | 1852.2824 | 1455.3509 | 0 | 0 | 396.9314 | 0 | 0 | 0
7503 | 1718.665 | 451.34 | 1996.3303 | 1785.3574 | 0 | 0 | 210.9729 | 0 | 0 | 0
7504 | 1537.608 | 46.07 | 176.8991 | 176.8991 | 0 | 0 | 0 | 1367.317 | 0 | 0
7505 | 1343.34 | 39.2 | 146.5369 | 146.5369 | 0 | 0 | 0 | 1202.277 | 0 | 0
7506 | 1522.828 | 0.98 | 0 | 0 | 0 | 0 | 0 | 1522.828 | 0 | 0
7507 | 1356.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1356.8 | 0 | 0
7508 | 1599.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1599.2 | 0 | 0
7509 | 1412.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1412.8 | 0 | 0
7510 | 1264.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1264.8 | 0 | 0
7511 | 1524 | 0 | 0 | 0 | 0 | 0 | 0 | 1524 | 0 | 0
7512 | 828.8 | 0 | 0 | 0 | 0 | 0 | 0 | 522.926 | 0 | 317.7434
7513 | 1140 | 0 | 0 | 0 | 0 | 0 | 0 | 1140 | 0 | 0
7514 | 1248.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1248.8 | 0 | 0
7515 | 1267.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1267.2 | 0 | 0
7516 | 1367.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1367.2 | 0 | 0
7517 | 1266.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1266.4 | 0 | 0
7518 | 1180 | 0 | 0 | 0 | 0 | 0 | 0 | 1180 | 0 | 0
7519 | 1235.738 | 95.7 | 375.5861 | 375.5861 | 0 | 0 | 0 | 282.182 | 0 | 614.9724
7520 | 932.415 | 276.36 | 1281.9837 | 968.5971 | -313.3866 | 0 | 0 | 0 | 0 | 0
7521 | 1225.774 | 470.92 | 2183.0284 | 1273.3399 | -614.9724 | 0 | 294.7162 | 0 | 0 | 0
7522 | 1183.594 | 623.96 | 2834.4681 | 1229.5231 | -109.6521 | 0 | 1495.293 | 0 | 0 | 0
7523 | 1167.775 | 747.37 | 3340.6112 | 1213.0902 | 0 | 0 | 2127.5209 | 0 | 0 | 0
7524 | 1149.101 | 613.69 | 2735.952 | 1193.6916 | 0 | 0 | 1542.2604 | 0 | 0 | 0
7525 | 1061.564 | 581.27 | 2592.6447 | 1102.7577 | 0 | 0 | 1489.887 | 0 | 0 | 0
7526 | 1207.035 | 462.95 | 2080.2907 | 1253.8737 | 0 | 0 | 826.417 | 0 | 0 | 0
7527 | 1229.373 | 258.06 | 1159.3684 | 1159.3684 | 0 | 0 | 0 | 113.313 | 0 | 0
7528 | 1219.569 | 159.94 | 714.0744 | 714.0744 | 0 | 0 | 0 | 532.169 | 0 | 0
7529 | 850.341 | 60.24 | 246.0347 | 246.0347 | 0 | 0 | 0 | 613.497 | 0 | 0
7530 | 1029.964 | 0.98 | 0 | 0 | 0 | 0 | 0 | 1029.964 | 0 | 0
7531 | 1183.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1183.2 | 0 | 0
7532 | 1294.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1294.4 | 0 | 0
7533 | 1021.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1021.6 | 0 | 0
7534 | 1191.2 | 0 | 0 | 0 | 0 | 0 | 0 | 885.326 | 0 | 317.7434
7535 | 1176 | 0 | 0 | 0 | 0 | 0 | 0 | 584 | 0 | 614.9724
7536 | 173.6 | 0 | 0 | 0 | 0 | 0 | 0 | 173.6 | 0 | 0
7537 | 89.6 | 0 | 0 | 0 | 0 | 0 | 0 | 89.6 | 0 | 0
7538 | 171.2 | 0 | 0 | 0 | 0 | 0 | 0 | 171.2 | 0 | 0
7539 | 109.6 | 0 | 0 | 0 | 0 | 0 | 0 | 109.6 | 0 | 0
7540 | 114.4 | 0 | 0 | 0 | 0 | 0 | 0 | 114.4 | 0 | 0
7541 | 85.6 | 0 | 0 | 0 | 0 | 0 | 0 | 85.6 | 0 | 0
7542 | 88.8 | 0 | 0 | 0 | 0 | 0 | 0 | 88.8 | 0 | 0
7543 | 85.749 | 54.76 | 207.8648 | 89.0765 | -118.7884 | 0 | 0 | 0 | 0 | 0
7544 | 209.928 | 43.12 | 168.33 | 168.33 | 0 | 0 | 0 | 47.886 | 0 | 0
7545 | 856.951 | 130.08 | 566.614 | 566.614 | 0 | 0 | 0 | 311.503 | 0 | 0
7546 | 1343.987 | 159.45 | 693.4167 | 693.4167 | 0 | 0 | 0 | 676.473 | 0 | 0
7547 | 1233.607 | 253.77 | 1116.3796 | 1116.3796 | 0 | 0 | 0 | 56.178 | 0 | 106.7393
7548 | 1009.939 | 423.35 | 1869.6346 | 1049.1294 | -614.9724 | 0 | 205.5327 | 0 | 0 | 0
7549 | 1251.764 | 353.01 | 1557.0021 | 1300.3384 | -256.6637 | 0 | 0 | 0 | 0 | 0
7550 | 1114.082 | 529.05 | 2355.0078 | 1157.3137 | -166.375 | 0 | 1031.3191 | 0 | 0 | 0
7551 | 1131.027 | 617.02 | 2803.922 | 1174.9162 | 0 | 0 | 1629.0058 | 0 | 0 | 0
7552 | 1306.039 | 424.41 | 1967.0495 | 1356.7195 | 0 | 0 | 610.33 | 0 | 0 | 0
7553 | 1317.887 | 190.12 | 784.7287 | 784.7287 | 0 | 0 | 0 | 562.472 | 0 | 0
7554 | 1482.151 | 5.56 | 0 | 0 | 0 | 0 | 0 | 1482.151 | 0 | 0
7555 | 1344.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1344.8 | 0 | 0
7556 | 1447.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1447.2 | 0 | 0
7557 | 1483.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1483.2 | 0 | 0
7558 | 1075.2 | 0 | 0 | 0 | 0 | 0 | 0 | 769.326 | 0 | 317.7434
7559 | 1232.8 | 0 | 0 | 0 | 0 | 0 | 0 | 640.8 | 0 | 614.9724
7560 | 1115.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1115.2 | 0 | 0
7561 | 1131.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1131.2 | 0 | 0
7562 | 1402.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1402.4 | 0 | 0
7563 | 878.4 | 0 | 0 | 0 | 0 | 0 | 0 | 878.4 | 0 | 0
7564 | 985.6 | 0 | 0 | 0 | 0 | 0 | 0 | 985.6 | 0 | 0
7565 | 1147.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1147.2 | 0 | 0
7566 | 1303.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1303.2 | 0 | 0
7567 | 1182.365 | 133.03 | 501.7084 | 501.7084 | 0 | 0 | 0 | 699.398 | 0 | 0
7568 | 1335.808 | 384.58 | 1766.3171 | 1387.6437 | -378.6734 | 0 | 0 | 0 | 0 | 0
7569 | 1230.58 | 620.64 | 2825.8034 | 1278.3323 | -614.9724 | 0 | 932.4987 | 0 | 0 | 0
7570 | 1363.817 | 805.14 | 3560.6238 | 1416.7385 | -44.3663 | 0 | 2099.5189 | 0 | 0 | 0
7571 | 1384.068 | 923.8 | 4000.7799 | 1437.7764 | 0 | 0 | 2563.0035 | 0 | 0 | 0
7572 | 1456.248 | 971.75 | 4160.3507 | 1512.7573 | 0 | 0 | 2647.5934 | 0 | 0 | 0
7573 | 1474.147 | 892.81 | 3851.1255 | 1531.3509 | 0 | 0 | 2319.7746 | 0 | 0 | 0
7574 | 1408.803 | 329.96 | 1455.4766 | 1455.4766 | 0 | 0 | 0 | 7.696 | 0 | 0
7575 | 1416.215 | 79.49 | 323.3062 | 323.3062 | 0 | 0 | 0 | 1104.986 | 0 | 0
7576 | 1598.239 | 172.02 | 759.5533 | 759.5533 | 0 | 0 | 0 | 867.059 | 0 | 0
7577 | 1617.779 | 134.19 | 555.8987 | 555.8987 | 0 | 0 | 0 | 1082.646 | 0 | 0
7578 | 1347.526 | 1.96 | 0 | 0 | 0 | 0 | 0 | 1347.526 | 0 | 0
7579 | 1315.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1315.2 | 0 | 0
7580 | 1236.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1236.8 | 0 | 0
7581 | 1147.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1147.2 | 0 | 0
7582 | 1199.2 | 0 | 0 | 0 | 0 | 0 | 0 | 893.326 | 0 | 317.7434
7583 | 1183.2 | 0 | 0 | 0 | 0 | 0 | 0 | 591.2 | 0 | 614.9724
7584 | 1420 | 0 | 0 | 0 | 0 | 0 | 0 | 1420 | 0 | 0
7585 | 1430.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1430.4 | 0 | 0
7586 | 1165.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1165.6 | 0 | 0
7587 | 1365.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1365.6 | 0 | 0
7588 | 876.8 | 0 | 0 | 0 | 0 | 0 | 0 | 876.8 | 0 | 0
7589 | 816 | 0 | 0 | 0 | 0 | 0 | 0 | 816 | 0 | 0
7590 | 768 | 0 | 0 | 0 | 0 | 0 | 0 | 768 | 0 | 0
7591 | 1244.499 | 110.44 | 421.0359 | 421.0359 | 0 | 0 | 0 | 839.191 | 0 | 0
7592 | 1277.595 | 387.72 | 1771.0541 | 1327.1718 | -443.8823 | 0 | 0 | 0 | 0 | 0
7593 | 1546.546 | 525.92 | 2355.8128 | 1606.5604 | -594.1288 | 0 | 155.1237 | 0 | 0 | 0
7594 | 1572.208 | 802.49 | 3419.5697 | 1633.2171 | 0 | 0 | 1786.3525 | 0 | 0 | 0
7595 | 1429.627 | 917.02 | 3766.5138 | 1485.1033 | 0 | 0 | 2281.4105 | 0 | 0 | 0
7596 | 1773.524 | 430.94 | 1846.1555 | 1842.3452 | 0 | 0 | 3.8103 | 0 | 0 | 0
7597 | 1456.594 | 237.98 | 1016.7759 | 1016.7759 | 0 | 0 | 0 | 0 | 0 | 496.3409
7598 | 1568.38 | 365.39 | 1580.7232 | 1580.7232 | 0 | 0 | 0 | 0 | 0 | 48.5174
7599 | 1614.354 | 556.63 | 2435.9649 | 1676.9986 | -606.368 | 0 | 152.5983 | 0 | 0 | 0
7600 | 1835.767 | 378.08 | 1701.3222 | 1701.3222 | 0 | 0 | 0 | 197.998 | 0 | 0
7601 | 1488.288 | 74.2 | 294.5759 | 294.5759 | 0 | 0 | 0 | 1204.716 | 0 | 0
7602 | 1561.284 | 3.61 | 0 | 0 | 0 | 0 | 0 | 1561.284 | 0 | 0
7603 | 1532 | 0 | 0 | 0 | 0 | 0 | 0 | 1532 | 0 | 0
7604 | 1440.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1440.8 | 0 | 0
7605 | 1496.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1496.8 | 0 | 0
7606 | 967.2 | 0 | 0 | 0 | 0 | 0 | 0 | 661.326 | 0 | 317.7434
7607 | 1389.6 | 0 | 0 | 0 | 0 | 0 | 0 | 797.6 | 0 | 614.9724
7608 | 994.4 | 0 | 0 | 0 | 0 | 0 | 0 | 994.4 | 0 | 0
7609 | 1131.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1131.2 | 0 | 0
7610 | 1332.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1332.8 | 0 | 0
7611 | 1132.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1132.8 | 0 | 0
7612 | 1163.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1163.2 | 0 | 0
7613 | 1312.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1312.8 | 0 | 0
7614 | 1239.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1239.2 | 0 | 0
7615 | 1053.267 | 98.81 | 380.7843 | 380.7843 | 0 | 0 | 0 | 686.707 | 0 | 0
7616 | 1323.515 | 296.05 | 1350.7817 | 1350.7817 | 0 | 0 | 0 | 23.192 | 0 | 0
7617 | 1381.943 | 538.46 | 2412.865 | 1435.569 | -614.9724 | 0 | 362.3237 | 0 | 0 | 0
7618 | 1401.676 | 810.9 | 3465.0839 | 1456.0677 | -423.0387 | 0 | 1585.9775 | 0 | 0 | 0
7619 | 1376.532 | 931.89 | 3872.0554 | 1429.948 | 0 | 0 | 2442.1074 | 0 | 0 | 0
7620 | 1661.105 | 980.4 | 4023.4778 | 1725.5638 | 0 | 0 | 2297.914 | 0 | 0 | 0
7621 | 1751.024 | 949.99 | 3929.8887 | 1818.972 | 0 | 0 | 2110.9167 | 0 | 0 | 0
7622 | 1832.523 | 845.61 | 3567.0529 | 1903.6336 | 0 | 0 | 1663.4193 | 0 | 0 | 0
7623 | 1589.617 | 532.77 | 2331.7427 | 1651.3017 | 0 | 0 | 680.441 | 0 | 0 | 0
7624 | 1620.881 | 346.91 | 1553.1232 | 1553.1232 | 0 | 0 | 0 | 125.775 | 0 | 0
7625 | 1347.911 | 134.05 | 550.8418 | 550.8418 | 0 | 0 | 0 | 817.646 | 0 | 0
7626 | 1547.415 | 1.96 | 0 | 0 | 0 | 0 | 0 | 1547.415 | 0 | 0
7627 | 1665.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1665.6 | 0 | 0
7628 | 1189.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1189.6 | 0 | 0
7629 | 890.4 | 0 | 0 | 0 | 0 | 0 | 0 | 890.4 | 0 | 0
7630 | 993.6 | 0 | 0 | 0 | 0 | 0 | 0 | 687.726 | 0 | 317.7434
7631 | 1250.4 | 0 | 0 | 0 | 0 | 0 | 0 | 658.4 | 0 | 614.9724
7632 | 1127.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1127.2 | 0 | 0
7633 | 1052 | 0 | 0 | 0 | 0 | 0 | 0 | 1052 | 0 | 0
7634 | 1386.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1386.4 | 0 | 0
7635 | 1046.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1046.4 | 0 | 0
7636 | 1260 | 0 | 0 | 0 | 0 | 0 | 0 | 1260 | 0 | 0
7637 | 1321.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1321.6 | 0 | 0
7638 | 721.6 | 0 | 0 | 0 | 0 | 0 | 0 | 721.6 | 0 | 0
7639 | 904.057 | 63.03 | 244.8993 | 244.8993 | 0 | 0 | 0 | 668.306 | 0 | 0
7640 | 979.12 | 370.98 | 1671.3496 | 1017.1145 | -614.9724 | 0 | 39.2627 | 0 | 0 | 0
7641 | 1105.275 | 502.81 | 2239.7202 | 1148.1649 | -423.0387 | 0 | 668.5166 | 0 | 0 | 0
7642 | 1633.544 | 464.19 | 2030.962 | 1696.9333 | 0 | 0 | 334.0287 | 0 | 0 | 0
7643 | 1559.029 | 854.61 | 3641.9238 | 1619.5267 | 0 | 0 | 2022.397 | 0 | 0 | 0
7644 | 1491.985 | 602.12 | 2604.4134 | 1549.8811 | 0 | 0 | 1054.5323 | 0 | 0 | 0
7645 | 1664.025 | 566.3 | 2453.7482 | 1728.5971 | 0 | 0 | 725.1512 | 0 | 0 | 0
7646 | 1509.416 | 529.96 | 2322.2916 | 1567.9885 | 0 | 0 | 754.3031 | 0 | 0 | 0
7647 | 1181.19 | 552.72 | 2465.789 | 1227.0258 | 0 | 0 | 1238.7632 | 0 | 0 | 0
7648 | 1646.173 | 430.77 | 1964.921 | 1710.0523 | 0 | 0 | 254.8687 | 0 | 0 | 0
7649 | 1321.611 | 184.74 | 757.1754 | 757.1754 | 0 | 0 | 0 | 592.72 | 0 | 0
7650 | 1456.398 | 4.24 | 0 | 0 | 0 | 0 | 0 | 1456.398 | 0 | 0
7651 | 1341.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1341.6 | 0 | 0
7652 | 1266.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1266.4 | 0 | 0
7653 | 1124.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1124.8 | 0 | 0
7654 | 1446.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1140.526 | 0 | 317.7434
7655 | 1150.4 | 0 | 0 | 0 | 0 | 0 | 0 | 558.4 | 0 | 614.9724
7656 | 1467.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1467.2 | 0 | 0
7657 | 1057.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1057.6 | 0 | 0
7658 | 1108 | 0 | 0 | 0 | 0 | 0 | 0 | 1108 | 0 | 0
7659 | 1446.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1446.4 | 0 | 0
7660 | 1334.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1334.4 | 0 | 0
7661 | 826.4 | 0 | 0 | 0 | 0 | 0 | 0 | 826.4 | 0 | 0
7662 | 1045.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1045.6 | 0 | 0
7663 | 960.752 | 134.64 | 498.7987 | 498.7987 | 0 | 0 | 0 | 480.586 | 0 | 0
7664 | 891.267 | 385.89 | 1762.7862 | 925.8524 | -614.9724 | 0 | 221.9614 | 0 | 0 | 0
7665 | 1021.024 | 623 | 2816.4833 | 1060.6446 | -423.0387 | 0 | 1332.8 | 0 | 0 | 0
7666 | 1278.022 | 809.37 | 3553.5391 | 1327.6153 | 0 | 0 | 2225.9238 | 0 | 0 | 0
7667 | 1410.682 | 935.24 | 4038.3981 | 1465.4232 | 0 | 0 | 2572.975 | 0 | 0 | 0
7668 | 1375.315 | 847.32 | 3674.6939 | 1428.6838 | 0 | 0 | 2246.0101 | 0 | 0 | 0
7669 | 1500.064 | 853.11 | 3701.1938 | 1558.2736 | 0 | 0 | 2142.9202 | 0 | 0 | 0
7670 | 1347.201 | 524.92 | 2327.2301 | 1399.4788 | 0 | 0 | 927.7513 | 0 | 0 | 0
7671 | 1165.374 | 647.39 | 2898.1853 | 1210.596 | 0 | 0 | 1687.5892 | 0 | 0 | 0
7672 | 1265.572 | 374.17 | 1709.3823 | 1314.6822 | 0 | 0 | 394.7001 | 0 | 0 | 0
7673 | 1012.197 | 60.47 | 234.4956 | 234.4956 | 0 | 0 | 0 | 786.461 | 0 | 0
7674 | 1011.616 | 0.98 | 0 | 0 | 0 | 0 | 0 | 1011.616 | 0 | 0
7675 | 971.2 | 0 | 0 | 0 | 0 | 0 | 0 | 971.2 | 0 | 0
7676 | 1312 | 0 | 0 | 0 | 0 | 0 | 0 | 1312 | 0 | 0
7677 | 1095.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1095.2 | 0 | 0
7678 | 1071.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1071.2 | 0 | 0
7679 | 1172 | 0 | 0 | 0 | 0 | 0 | 0 | 1172 | 0 | 0
7680 | 1040 | 0 | 0 | 0 | 0 | 0 | 0 | 538.156 | 0 | 521.3179
7681 | 1044 | 0 | 0 | 0 | 0 | 0 | 0 | 1044 | 0 | 0
7682 | 1136.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1136.8 | 0 | 0
7683 | 1080.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1080.8 | 0 | 0
7684 | 1034.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1034.4 | 0 | 0
7685 | 1055.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1055.2 | 0 | 0
7686 | 1076 | 0 | 0 | 0 | 0 | 0 | 0 | 1076 | 0 | 0
7687 | 886.193 | 139.28 | 509.1837 | 509.1837 | 0 | 0 | 0 | 0 | 0 | 411.3978
7688 | 293.458 | 392 | 1778.3579 | 304.8456 | -614.9724 | 0 | 858.5399 | 0 | 0 | 0
7689 | 141.382 | 624.3 | 2785.4344 | 146.8683 | -423.0387 | 0 | 2215.5274 | 0 | 0 | 0
7690 | 225.957 | 810.13 | 3463.2202 | 234.7252 | 0 | 0 | 3228.495 | 0 | 0 | 0
7691 | 173.99 | 929.74 | 3875.687 | 180.7416 | 0 | 0 | 3694.9454 | 0 | 0 | 0
7692 | 186.914 | 623.61 | 2674.5005 | 194.1672 | 0 | 0 | 2480.3333 | 0 | 0 | 0
7693 | 144.11 | 809.19 | 3432.616 | 149.7022 | 0 | 0 | 3282.9139 | 0 | 0 | 0
7694 | 135.505 | 755.01 | 3256.2602 | 140.7632 | 0 | 0 | 3115.497 | 0 | 0 | 0
7695 | 194.577 | 667.13 | 2943.0492 | 202.1275 | 0 | 0 | 2740.9216 | 0 | 0 | 0
7696 | 215.288 | 293.06 | 1322.0868 | 223.6422 | 0 | 0 | 1098.4446 | 0 | 0 | 0
7697 | 184.122 | 193.22 | 784.871 | 191.2668 | 0 | 0 | 593.6042 | 0 | 0 | 0
7698 | 203.03 | 5.61 | 0 | 0 | 0 | 0 | 0 | 151.556 | 0 | 53.4714
7699 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 145.4327
7700 | 197.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205.2678
7701 | 199.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 206.9299
7702 | 108.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.022
7703 | 98.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.2184
7704 | 102.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.3736
7705 | 92.8 | 0 | 0 | 0 | 0 | 0 | 0 | 92.8 | 0 | 0
7706 | 99.2 | 0 | 0 | 0 | 0 | 0 | 0 | 99.2 | 0 | 0
7707 | 94.4 | 0 | 0 | 0 | 0 | 0 | 0 | 94.4 | 0 | 0
7708 | 98.4 | 0 | 0 | 0 | 0 | 0 | 0 | 98.4 | 0 | 0
7709 | 92.8 | 0 | 0 | 0 | 0 | 0 | 0 | 92.8 | 0 | 0
7710 | 93.6 | 0 | 0 | 0 | 0 | 0 | 0 | 93.6 | 0 | 0
7711 | 80.485 | 126.51 | 467.0695 | 83.6082 | -383.4613 | 0 | 0 | 0 | 0 | 0
7712 | 100.984 | 376.18 | 1707.1707 | 104.9027 | -614.9724 | 0 | 987.2956 | 0 | 0 | 0
7713 | 679.251 | 610.68 | 2730.8016 | 705.6092 | -39.5774 | 0 | 1985.615 | 0 | 0 | 0
7714 | 1271.683 | 795.57 | 3422.7806 | 1321.0303 | 0 | 0 | 2101.7503 | 0 | 0 | 0
7715 | 1286.429 | 881.81 | 3713.1286 | 1336.3486 | 0 | 0 | 2376.7801 | 0 | 0 | 0
7716 | 1324.926 | 623.57 | 2658.8395 | 1376.3394 | 0 | 0 | 1282.5 | 0 | 0 | 0
7717 | 1133.191 | 389.92 | 1681.0718 | 1177.1642 | 0 | 0 | 503.9076 | 0 | 0 | 0
7718 | 1217.422 | 419.19 | 1819.4187 | 1264.6638 | 0 | 0 | 554.755 | 0 | 0 | 0
7719 | 1214.924 | 125.91 | 531.8576 | 531.8576 | 0 | 0 | 0 | 702.934 | 0 | 0
7720 | 1286.664 | 55.89 | 219.9773 | 219.9773 | 0 | 0 | 0 | 1074.904 | 0 | 0
7721 | 1421.989 | 7.83 | 7.6227 | 7.6227 | 0 | 0 | 0 | 1414.651 | 0 | 0
7722 | 1335.966 | 0 | 0 | 0 | 0 | 0 | 0 | 1335.966 | 0 | 0
7723 | 1252.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1252.8 | 0 | 0
7724 | 1186.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1186.4 | 0 | 0
7725 | 1470.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1470.4 | 0 | 0
7726 | 1188.8 | 0 | 0 | 0 | 0 | 0 | 0 | 882.926 | 0 | 317.7434
7727 | 779.2 | 0 | 0 | 0 | 0 | 0 | 0 | 187.2 | 0 | 614.9724
7728 | 1133.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1133.6 | 0 | 0
7729 | 877.6 | 0 | 0 | 0 | 0 | 0 | 0 | 877.6 | 0 | 0
7730 | 888 | 0 | 0 | 0 | 0 | 0 | 0 | 888 | 0 | 0
7731 | 992 | 0 | 0 | 0 | 0 | 0 | 0 | 992 | 0 | 0
7732 | 1028 | 0 | 0 | 0 | 0 | 0 | 0 | 1028 | 0 | 0
7733 | 1020 | 0 | 0 | 0 | 0 | 0 | 0 | 1020 | 0 | 0
7734 | 988.8 | 0 | 0 | 0 | 0 | 0 | 0 | 988.8 | 0 | 0
7735 | 1027.129 | 117.48 | 435.4597 | 435.4597 | 0 | 0 | 0 | 607.936 | 0 | 0
7736 | 958.726 | 364.69 | 1636.2504 | 995.9291 | -614.9724 | 0 | 25.3489 | 0 | 0 | 0
7737 | 1015.72 | 596.79 | 2629.8911 | 1055.1348 | -423.0387 | 0 | 1151.7176 | 0 | 0 | 0
7738 | 1081.252 | 779.99 | 3275.8116 | 1123.2097 | 0 | 0 | 2152.6019 | 0 | 0 | 0
7739 | 1456.647 | 894.58 | 3662.5222 | 1513.1718 | 0 | 0 | 2149.3504 | 0 | 0 | 0
7740 | 1355.634 | 554.75 | 2371.6795 | 1408.239 | 0 | 0 | 963.4405 | 0 | 0 | 0
7741 | 1091.508 | 604.52 | 2574.9196 | 1133.8637 | 0 | 0 | 1441.0559 | 0 | 0 | 0
7742 | 1198.058 | 435.42 | 1894.9939 | 1244.5483 | 0 | 0 | 650.4455 | 0 | 0 | 0
7743 | 1592.282 | 120.78 | 509.9233 | 509.9233 | 0 | 0 | 0 | 1101.407 | 0 | 0
7744 | 1106.455 | 40.19 | 149.8019 | 149.8019 | 0 | 0 | 0 | 962.249 | 0 | 0
7745 | 1246.387 | 10.77 | 20.2079 | 20.2079 | 0 | 0 | 0 | 1226.934 | 0 | 0
7746 | 1322.503 | 0 | 0 | 0 | 0 | 0 | 0 | 1322.503 | 0 | 0
7747 | 1121.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1121.6 | 0 | 0
7748 | 1195.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1195.2 | 0 | 0
7749 | 1380 | 0 | 0 | 0 | 0 | 0 | 0 | 1380 | 0 | 0
7750 | 1388 | 0 | 0 | 0 | 0 | 0 | 0 | 1082.126 | 0 | 317.7434
7751 | 1431.2 | 0 | 0 | 0 | 0 | 0 | 0 | 839.2 | 0 | 614.9724
7752 | 1104 | 0 | 0 | 0 | 0 | 0 | 0 | 1104 | 0 | 0
7753 | 1285.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1285.6 | 0 | 0
7754 | 1016 | 0 | 0 | 0 | 0 | 0 | 0 | 1016 | 0 | 0
7755 | 1193.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1193.6 | 0 | 0
7756 | 1489.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1489.6 | 0 | 0
7757 | 1088.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1088.8 | 0 | 0
7758 | 1126.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1126.4 | 0 | 0
7759 | 799.087 | 64.69 | 238.4109 | 238.4109 | 0 | 0 | 0 | 569.582 | 0 | 0
7760 | 933.699 | 308.85 | 1409.0638 | 969.931 | -439.1329 | 0 | 0 | 0 | 0 | 0
7761 | 1028.874 | 602.87 | 2733.0787 | 1068.8002 | -598.8782 | 0 | 1065.4002 | 0 | 0 | 0
7762 | 1429.183 | 472.01 | 2086.2877 | 1484.6421 | 0 | 0 | 601.6456 | 0 | 0 | 0
7763 | 1309.361 | 513.96 | 2239.9217 | 1360.1704 | 0 | 0 | 879.7513 | 0 | 0 | 0
7764 | 1273.22 | 350.39 | 1522.2344 | 1322.627 | 0 | 0 | 199.6074 | 0 | 0 | 0
7765 | 1283.758 | 733.54 | 3154.3742 | 1333.5739 | 0 | 0 | 1820.8003 | 0 | 0 | 0
7766 | 1017.049 | 585.26 | 2568.8291 | 1056.5153 | 0 | 0 | 1512.3138 | 0 | 0 | 0
7767 | 1569.862 | 353.69 | 1573.8868 | 1573.8868 | 0 | 0 | 0 | 54.768 | 0 | 0
7768 | 1212.909 | 32.34 | 114.844 | 114.844 | 0 | 0 | 0 | 1102.355 | 0 | 0
7769 | 1407.813 | 94.44 | 389.7917 | 389.7917 | 0 | 0 | 0 | 1032.582 | 0 | 0
7770 | 1339.188 | 1.96 | 0 | 0 | 0 | 0 | 0 | 1339.188 | 0 | 0
7771 | 1444 | 0 | 0 | 0 | 0 | 0 | 0 | 1444 | 0 | 0
7772 | 1498.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1498.4 | 0 | 0
7773 | 1683.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1683.2 | 0 | 0
7774 | 1572 | 0 | 0 | 0 | 0 | 0 | 0 | 1266.126 | 0 | 317.7434
7775 | 1266.4 | 0 | 0 | 0 | 0 | 0 | 0 | 674.4 | 0 | 614.9724
7776 | 1252.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1252.8 | 0 | 0
7777 | 1118.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1118.4 | 0 | 0
7778 | 1283.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1283.2 | 0 | 0
7779 | 1369.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1369.6 | 0 | 0
7780 | 1394.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1394.4 | 0 | 0
7781 | 1285.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1285.6 | 0 | 0
7782 | 1056 | 0 | 0 | 0 | 0 | 0 | 0 | 1056 | 0 | 0
7783 | 1040.324 | 63.84 | 236.7675 | 236.7675 | 0 | 0 | 0 | 812.401 | 0 | 0
7784 | 869.633 | 359.38 | 1618.946 | 903.3789 | -614.9724 | 0 | 100.5947 | 0 | 0 | 0
7785 | 1098.227 | 594.32 | 2648.1294 | 1140.8434 | -423.0387 | 0 | 1084.2473 | 0 | 0 | 0
7786 | 1314.622 | 782.4 | 3383.654 | 1365.6356 | 0 | 0 | 2018.0185 | 0 | 0 | 0
7787 | 1099.177 | 803.6 | 3447.3411 | 1141.8303 | 0 | 0 | 2305.5108 | 0 | 0 | 0
7788 | 1346.221 | 536.56 | 2317.643 | 1398.4608 | 0 | 0 | 919.1822 | 0 | 0 | 0
7789 | 1404.829 | 373.71 | 1627.8579 | 1459.343 | 0 | 0 | 168.5149 | 0 | 0 | 0
7790 | 1166.196 | 610.85 | 2669.8518 | 1211.4499 | 0 | 0 | 1458.4019 | 0 | 0 | 0
7791 | 1431.156 | 537.16 | 2391.7399 | 1486.6916 | 0 | 0 | 905.0482 | 0 | 0 | 0
7792 | 1408.691 | 120.59 | 519.3556 | 519.3556 | 0 | 0 | 0 | 908.736 | 0 | 0
7793 | 1490.436 | 51.15 | 200.2836 | 200.2836 | 0 | 0 | 0 | 1297.634 | 0 | 0
7794 | 1393.933 | 0.98 | 0 | 0 | 0 | 0 | 0 | 1393.933 | 0 | 0
7795 | 1680.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1680.8 | 0 | 0
7796 | 1324.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1324.8 | 0 | 0
7797 | 1534.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1534.4 | 0 | 0
7798 | 1571.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1265.326 | 0 | 317.7434
7799 | 1176.8 | 0 | 0 | 0 | 0 | 0 | 0 | 584.8 | 0 | 614.9724
7800 | 1416.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1416.8 | 0 | 0
7801 | 1240 | 0 | 0 | 0 | 0 | 0 | 0 | 1240 | 0 | 0
7802 | 1348.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1348.8 | 0 | 0
7803 | 1515.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1515.2 | 0 | 0
7804 | 1366.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1366.4 | 0 | 0
7805 | 1381.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1381.6 | 0 | 0
7806 | 1362.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1362.4 | 0 | 0
7807 | 679.439 | 71.28 | 266.9406 | 266.9406 | 0 | 0 | 0 | 422.47 | 0 | 0
7808 | 1137.376 | 376.76 | 1719.2644 | 1181.5116 | -537.7529 | 0 | 0 | 0 | 0 | 0
7809 | 882.651 | 612.48 | 2770.0051 | 916.902 | -500.2582 | 0 | 1352.8448 | 0 | 0 | 0
7810 | 432.662 | 631.13 | 2773.8788 | 449.4513 | 0 | 0 | 2324.4274 | 0 | 0 | 0
7811 | 389.328 | 804.02 | 3422.3786 | 404.4358 | 0 | 0 | 3017.9428 | 0 | 0 | 0
7812 | 396.46 | 966.5 | 3997.7694 | 411.8445 | 0 | 0 | 3585.9249 | 0 | 0 | 0
7813 | 851.215 | 627.74 | 2671.1877 | 884.2462 | 0 | 0 | 1786.9415 | 0 | 0 | 0
7814 | 1358.284 | 715.37 | 3046.1536 | 1410.9919 | 0 | 0 | 1635.1618 | 0 | 0 | 0
7815 | 1653.136 | 569.12 | 2480.5504 | 1717.2855 | 0 | 0 | 763.2649 | 0 | 0 | 0
7816 | 1480.775 | 340.36 | 1520.004 | 1520.004 | 0 | 0 | 0 | 17.551 | 0 | 0
7817 | 1522.428 | 169.07 | 686.8577 | 686.8577 | 0 | 0 | 0 | 861.228 | 0 | 0
7818 | 1682.404 | 1.96 | 0 | 0 | 0 | 0 | 0 | 1682.404 | 0 | 0
7819 | 1758.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1758.4 | 0 | 0
7820 | 1597.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1597.6 | 0 | 0
7821 | 1777.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1777.6 | 0 | 0
7822 | 1849.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1543.726 | 0 | 317.7434
7823 | 1356 | 0 | 0 | 0 | 0 | 0 | 0 | 764 | 0 | 614.9724
7824 | 1280.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1280.8 | 0 | 0
7825 | 1248.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1248.8 | 0 | 0
7826 | 1583.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1583.2 | 0 | 0
7827 | 1660 | 0 | 0 | 0 | 0 | 0 | 0 | 1660 | 0 | 0
7828 | 981.6 | 0 | 0 | 0 | 0 | 0 | 0 | 981.6 | 0 | 0
7829 | 1345.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1345.6 | 0 | 0
7830 | 1347.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1347.2 | 0 | 0
7831 | 1080.957 | 108.86 | 400.3128 | 400.3128 | 0 | 0 | 0 | 695.598 | 0 | 0
7832 | 1190.482 | 356.7 | 1611.6297 | 1236.6784 | -374.9514 | 0 | 0 | 0 | 0 | 0
7833 | 1061.094 | 591.64 | 2644.1549 | 1102.2695 | -614.9724 | 0 | 926.913 | 0 | 0 | 0
7834 | 1659.705 | 785.14 | 3367.189 | 1724.1094 | -48.0873 | 0 | 1594.9922 | 0 | 0 | 0
7835 | 1735.038 | 912.36 | 3802.7671 | 1802.3657 | 0 | 0 | 2000.4014 | 0 | 0 | 0
7836 | 1837.293 | 919.47 | 3813.2943 | 1908.5887 | 0 | 0 | 1904.7056 | 0 | 0 | 0
7837 | 1536.804 | 581.86 | 2493.8741 | 1596.4393 | 0 | 0 | 897.4348 | 0 | 0 | 0
7838 | 1437.913 | 239.86 | 1034.3763 | 1034.3763 | 0 | 0 | 0 | 442.176 | 0 | 0
7839 | 1704.969 | 391.2 | 1723.215 | 1723.215 | 0 | 0 | 0 | 46.125 | 0 | 0
7840 | 1445.753 | 176.08 | 774.001 | 774.001 | 0 | 0 | 0 | 700.665 | 0 | 0
7841 | 1513.323 | 98.64 | 398.8699 | 398.8699 | 0 | 0 | 0 | 1129.353 | 0 | 0
7842 | 1805.698 | 0.98 | 0 | 0 | 0 | 0 | 0 | 1805.698 | 0 | 0
7843 | 1423.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1423.2 | 0 | 0
7844 | 1600 | 0 | 0 | 0 | 0 | 0 | 0 | 1600 | 0 | 0
7845 | 1737.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1737.6 | 0 | 0
7846 | 1408 | 0 | 0 | 0 | 0 | 0 | 0 | 1408 | 0 | 0
7847 | 1577.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1577.6 | 0 | 0
7848 | 1420.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1052.144 | 0 | 382.9616
7849 | 1040 | 0 | 0 | 0 | 0 | 0 | 0 | 1040 | 0 | 0
7850 | 1061.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1061.6 | 0 | 0
7851 | 848 | 0 | 0 | 0 | 0 | 0 | 0 | 848 | 0 | 0
7852 | 1101.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1101.6 | 0 | 0
7853 | 727.2 | 0 | 0 | 0 | 0 | 0 | 0 | 727.2 | 0 | 0
7854 | 904 | 0 | 0 | 0 | 0 | 0 | 0 | 904 | 0 | 0
7855 | 917.901 | 110.21 | 403.7668 | 403.7668 | 0 | 0 | 0 | 0 | 0 | 549.7531
7856 | 910.899 | 277.58 | 1269.9783 | 946.2462 | -323.7321 | 0 | 0 | 0 | 0 | 0
7857 | 920.17 | 488.17 | 2229.2937 | 955.877 | -614.9724 | 0 | 658.4443 | 0 | 0 | 0
7858 | 1061.386 | 662.69 | 2946.9405 | 1102.5728 | -99.3066 | 0 | 1745.0611 | 0 | 0 | 0
7859 | 1019.092 | 795.05 | 3465.3851 | 1058.6376 | 0 | 0 | 2406.7475 | 0 | 0 | 0
7860 | 991.068 | 526.18 | 2304.1718 | 1029.5261 | 0 | 0 | 1274.6456 | 0 | 0 | 0
7861 | 1143.278 | 568.94 | 2484.8262 | 1187.6426 | 0 | 0 | 1297.1835 | 0 | 0 | 0
7862 | 1101.732 | 603.96 | 2656.3266 | 1144.4844 | 0 | 0 | 1511.8422 | 0 | 0 | 0
7863 | 1117.132 | 348.72 | 1548.7644 | 1160.482 | 0 | 0 | 388.2824 | 0 | 0 | 0
7864 | 520.632 | 232.91 | 1040.178 | 540.835 | 0 | 0 | 499.3431 | 0 | 0 | 0
7865 | 192.296 | 119.16 | 490.5132 | 199.758 | 0 | 0 | 290.7552 | 0 | 0 | 0
7866 | 257.187 | 1.96 | 0 | 0 | 0 | 0 | 0 | 144.913 | 0 | 116.6308
7867 | 150.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156.2362
7868 | 158.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 164.5467
7869 | 125.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 130.4739
7870 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124.6566
7871 | 115.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 119.6703
7872 | 116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.5014
7873 | 107.2 | 0 | 0 | 0 | 0 | 0 | 0 | 107.2 | 0 | 0
7874 | 117.6 | 0 | 0 | 0 | 0 | 0 | 0 | 117.6 | 0 | 0
7875 | 96.8 | 0 | 0 | 0 | 0 | 0 | 0 | 96.8 | 0 | 0
7876 | 103.2 | 0 | 0 | 0 | 0 | 0 | 0 | 103.2 | 0 | 0
7877 | 96.8 | 0 | 0 | 0 | 0 | 0 | 0 | 96.8 | 0 | 0
7878 | 101.6 | 0 | 0 | 0 | 0 | 0 | 0 | 101.6 | 0 | 0
7879 | 87.682 | 65.93 | 249.2342 | 91.0845 | -158.1497 | 0 | 0 | 0 | 0 | 0
7880 | 158.372 | 268.55 | 1226.0316 | 164.5176 | -614.9724 | 0 | 446.5416 | 0 | 0 | 0
7881 | 720.376 | 495.91 | 2252.8849 | 748.33 | -264.89 | 0 | 1239.6649 | 0 | 0 | 0
7882 | 958.609 | 763.61 | 3373.9838 | 995.8076 | 0 | 0 | 2378.1762 | 0 | 0 | 0
7883 | 1110.708 | 835.07 | 3624.1228 | 1153.8087 | 0 | 0 | 2470.314 | 0 | 0 | 0
7884 | 1168.124 | 777.04 | 3363.8596 | 1213.4528 | 0 | 0 | 2150.4069 | 0 | 0 | 0
7885 | 1171.326 | 739.34 | 3207.7418 | 1216.779 | 0 | 0 | 1990.9628 | 0 | 0 | 0
7886 | 1171.349 | 656.01 | 2880.0643 | 1216.8029 | 0 | 0 | 1663.2614 | 0 | 0 | 0
7887 | 1266.465 | 542.99 | 2423.3092 | 1315.6099 | 0 | 0 | 1107.6993 | 0 | 0 | 0
7888 | 1231.431 | 392.08 | 1781.6395 | 1279.2164 | 0 | 0 | 502.4231 | 0 | 0 | 0
7889 | 1227.897 | 143.34 | 590.0868 | 590.0868 | 0 | 0 | 0 | 659.853 | 0 | 0
7890 | 1118.58 | 1.96 | 0 | 0 | 0 | 0 | 0 | 1118.58 | 0 | 0
7891 | 1358.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1358.4 | 0 | 0
7892 | 1066.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1066.4 | 0 | 0
7893 | 1076 | 0 | 0 | 0 | 0 | 0 | 0 | 1076 | 0 | 0
7894 | 1006.4 | 0 | 0 | 0 | 0 | 0 | 0 | 700.526 | 0 | 317.7434
7895 | 1079.2 | 0 | 0 | 0 | 0 | 0 | 0 | 487.2 | 0 | 614.9724
7896 | 1528 | 0 | 0 | 0 | 0 | 0 | 0 | 1528 | 0 | 0
7897 | 1220.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1220.8 | 0 | 0
7898 | 923.2 | 0 | 0 | 0 | 0 | 0 | 0 | 923.2 | 0 | 0
7899 | 1218.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1218.4 | 0 | 0
7900 | 1200.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1200.8 | 0 | 0
7901 | 896 | 0 | 0 | 0 | 0 | 0 | 0 | 896 | 0 | 0
7902 | 1284 | 0 | 0 | 0 | 0 | 0 | 0 | 1284 | 0 | 0
7903 | 1092.491 | 85.42 | 318.0664 | 318.0664 | 0 | 0 | 0 | 786.306 | 0 | 0
7904 | 1306.162 | 326.51 | 1498.0936 | 1356.8473 | -141.2463 | 0 | 0 | 0 | 0 | 0
7905 | 1409.71 | 476.59 | 2175.3288 | 1464.4134 | -614.9724 | 0 | 95.943 | 0 | 0 | 0
7906 | 984.961 | 437.73 | 1950.0879 | 1023.1811 | -281.7934 | 0 | 645.1133 | 0 | 0 | 0
7907 | 1372.328 | 625.86 | 2740.8552 | 1425.5808 | 0 | 0 | 1315.2743 | 0 | 0 | 0
7908 | 1453.632 | 681.93 | 2956.1485 | 1510.0398 | 0 | 0 | 1446.1087 | 0 | 0 | 0
7909 | 1182.818 | 696.11 | 3016.4116 | 1228.717 | 0 | 0 | 1787.6947 | 0 | 0 | 0
7910 | 1278.412 | 513.5 | 2253.4584 | 1328.0205 | 0 | 0 | 925.4379 | 0 | 0 | 0
7911 | 1247.998 | 385.39 | 1711.275 | 1296.4262 | 0 | 0 | 414.8488 | 0 | 0 | 0
7912 | 1086.354 | 96.5 | 406.9123 | 406.9123 | 0 | 0 | 0 | 694.642 | 0 | 0
7913 | 1467.39 | 100.6 | 416.2688 | 416.2688 | 0 | 0 | 0 | 1066.671 | 0 | 0
7914 | 1410.488 | 1.96 | 0 | 0 | 0 | 0 | 0 | 1410.488 | 0 | 0
7915 | 1142.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1142.4 | 0 | 0
7916 | 984.8 | 0 | 0 | 0 | 0 | 0 | 0 | 984.8 | 0 | 0
7917 | 1211.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1211.2 | 0 | 0
7918 | 1125.6 | 0 | 0 | 0 | 0 | 0 | 0 | 819.726 | 0 | 317.7434
7919 | 1388.8 | 0 | 0 | 0 | 0 | 0 | 0 | 796.8 | 0 | 614.9724
7920 | 985.6 | 0 | 0 | 0 | 0 | 0 | 0 | 985.6 | 0 | 0
7921 | 1293.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1293.6 | 0 | 0
7922 | 1131.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1131.2 | 0 | 0
7923 | 1264.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1264.8 | 0 | 0
7924 | 774.4 | 0 | 0 | 0 | 0 | 0 | 0 | 774.4 | 0 | 0
7925 | 1108.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1108.8 | 0 | 0
7926 | 734.4 | 0 | 0 | 0 | 0 | 0 | 0 | 734.4 | 0 | 0
7927 | 812.644 | 96.12 | 352.9059 | 352.9059 | 0 | 0 | 0 | 472.921 | 0 | 0
7928 | 1161.248 | 291.99 | 1333.3526 | 1206.3099 | -127.0427 | 0 | 0 | 0 | 0 | 0
7929 | 1243.412 | 497.21 | 2259.2777 | 1291.6623 | -614.9724 | 0 | 352.643 | 0 | 0 | 0
7930 | 1326.775 | 660.35 | 2924.0764 | 1378.2602 | -295.996 | 0 | 1249.8203 | 0 | 0 | 0
7931 | 1621.135 | 674.42 | 2946.4315 | 1684.0427 | 0 | 0 | 1262.3888 | 0 | 0 | 0
7932 | 1251.306 | 746.52 | 3231.4151 | 1299.8626 | 0 | 0 | 1931.5525 | 0 | 0 | 0
7933 | 1349.218 | 744.64 | 3214.5491 | 1401.5741 | 0 | 0 | 1812.975 | 0 | 0 | 0
7934 | 1331.273 | 572.41 | 2505.3301 | 1382.9327 | 0 | 0 | 1122.3974 | 0 | 0 | 0
7935 | 1282.735 | 456.68 | 2030.9152 | 1332.5112 | 0 | 0 | 698.404 | 0 | 0 | 0
7936 | 1437.172 | 163.39 | 715.3573 | 715.3573 | 0 | 0 | 0 | 748.537 | 0 | 0
7937 | 1620.088 | 34.3 | 123.5253 | 123.5253 | 0 | 0 | 0 | 1501.177 | 0 | 0
7938 | 1488.651 | 0.98 | 0 | 0 | 0 | 0 | 0 | 1488.651 | 0 | 0
7939 | 1304.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1304.8 | 0 | 0
7940 | 1217.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1217.6 | 0 | 0
7941 | 1169.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1169.6 | 0 | 0
7942 | 1280 | 0 | 0 | 0 | 0 | 0 | 0 | 974.126 | 0 | 317.7434
7943 | 1238.4 | 0 | 0 | 0 | 0 | 0 | 0 | 646.4 | 0 | 614.9724
7944 | 1456 | 0 | 0 | 0 | 0 | 0 | 0 | 1456 | 0 | 0
7945 | 1352 | 0 | 0 | 0 | 0 | 0 | 0 | 1352 | 0 | 0
7946 | 1226.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1226.4 | 0 | 0
7947 | 1184 | 0 | 0 | 0 | 0 | 0 | 0 | 1184 | 0 | 0
7948 | 1292 | 0 | 0 | 0 | 0 | 0 | 0 | 1292 | 0 | 0
7949 | 1500 | 0 | 0 | 0 | 0 | 0 | 0 | 1500 | 0 | 0
7950 | 1428.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1428.8 | 0 | 0
7951 | 1297.339 | 100.63 | 361.2568 | 361.2568 | 0 | 0 | 0 | 949.577 | 0 | 0
7952 | 1310.033 | 290.99 | 1331.1826 | 1331.1826 | 0 | 0 | 0 | 28.577 | 0 | 0
7953 | 994.134 | 485.44 | 2209.6592 | 1032.7111 | -614.9724 | 0 | 561.9757 | 0 | 0 | 0
7954 | 1147.17 | 589.71 | 2613.9994 | 1191.6856 | -423.0387 | 0 | 999.2751 | 0 | 0 | 0
7955 | 1266.559 | 668.44 | 2899.25 | 1315.7075 | 0 | 0 | 1583.5425 | 0 | 0 | 0
7956 | 1524.5 | 787.11 | 3367.3957 | 1583.6578 | 0 | 0 | 1783.7379 | 0 | 0 | 0
7957 | 1553.979 | 698.75 | 3002.7036 | 1614.2808 | 0 | 0 | 1388.4228 | 0 | 0 | 0
7958 | 1388.914 | 527.29 | 2300.351 | 1442.8105 | 0 | 0 | 857.5406 | 0 | 0 | 0
7959 | 1652.723 | 276.03 | 1215.6104 | 1215.6104 | 0 | 0 | 0 | 482.522 | 0 | 0
7960 | 1570.274 | 285.47 | 1285.8751 | 1285.8751 | 0 | 0 | 0 | 332.433 | 0 | 0
7961 | 1459.662 | 166.4 | 687.7448 | 687.7448 | 0 | 0 | 0 | 797.608 | 0 | 0
7962 | 1449.583 | 1.96 | 0 | 0 | 0 | 0 | 0 | 1449.583 | 0 | 0
7963 | 1372.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1372.8 | 0 | 0
7964 | 1579.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1579.2 | 0 | 0
7965 | 1569.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1569.6 | 0 | 0
7966 | 1548.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1242.926 | 0 | 317.7434
7967 | 1433.6 | 0 | 0 | 0 | 0 | 0 | 0 | 841.6 | 0 | 614.9724
7968 | 1310.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1310.4 | 0 | 0
7969 | 1088 | 0 | 0 | 0 | 0 | 0 | 0 | 1088 | 0 | 0
7970 | 1392 | 0 | 0 | 0 | 0 | 0 | 0 | 1392 | 0 | 0
7971 | 1436.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1436.8 | 0 | 0
7972 | 1538.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1538.4 | 0 | 0
7973 | 1468 | 0 | 0 | 0 | 0 | 0 | 0 | 1468 | 0 | 0
7974 | 1324 | 0 | 0 | 0 | 0 | 0 | 0 | 1324 | 0 | 0
7975 | 916 | 11.75 | 23.7388 | 23.7388 | 0 | 0 | 0 | 893.148 | 0 | 0
7976 | 1538.833 | 91.68 | 395.2091 | 395.2091 | 0 | 0 | 0 | 1158.387 | 0 | 0
7977 | 1337.062 | 222.19 | 996.5566 | 996.5566 | 0 | 0 | 0 | 377.732 | 0 | 0
7978 | 1341.153 | 392.25 | 1755.1448 | 1393.1961 | -361.9487 | 0 | 0 | 0 | 0 | 0
7979 | 1403.197 | 419.54 | 1859.2849 | 1457.6477 | -401.6372 | 0 | 0 | 0 | 0 | 0
7980 | 1495.022 | 546.54 | 2404.4902 | 1553.036 | -274.4252 | 0 | 577.029 | 0 | 0 | 0
7981 | 1415.791 | 412.68 | 1825.0491 | 1470.7304 | 0 | 0 | 354.3186 | 0 | 0 | 0
7982 | 1603.039 | 402.26 | 1790.0195 | 1665.2445 | 0 | 0 | 124.775 | 0 | 0 | 0
7983 | 1305.477 | 384.97 | 1731.6782 | 1356.1357 | 0 | 0 | 375.5425 | 0 | 0 | 0
7984 | 1797.5 | 105.05 | 452.119 | 452.119 | 0 | 0 | 0 | 1362.27 | 0 | 0
7985 | 1690.399 | 8.81 | 12.3306 | 12.3306 | 0 | 0 | 0 | 1678.529 | 0 | 0
7986 | 1741.499 | 0.98 | 0 | 0 | 0 | 0 | 0 | 1741.499 | 0 | 0
7987 | 1718.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1718.4 | 0 | 0
7988 | 1222.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1222.4 | 0 | 0
7989 | 1288 | 0 | 0 | 0 | 0 | 0 | 0 | 1288 | 0 | 0
7990 | 1320.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1014.926 | 0 | 317.7434
7991 | 1376 | 0 | 0 | 0 | 0 | 0 | 0 | 784 | 0 | 614.9724
7992 | 1328.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1328.8 | 0 | 0
7993 | 1398.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1398.4 | 0 | 0
7994 | 1504 | 0 | 0 | 0 | 0 | 0 | 0 | 1504 | 0 | 0
7995 | 1284 | 0 | 0 | 0 | 0 | 0 | 0 | 1284 | 0 | 0
7996 | 1360.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1360.8 | 0 | 0
7997 | 1429.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1429.6 | 0 | 0
7998 | 1222.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1222.4 | 0 | 0
7999 | 1190.56 | 41.64 | 147.0698 | 147.0698 | 0 | 0 | 0 | 1048.984 | 0 | 0
8000 | 1232.152 | 232.13 | 1061.0487 | 1061.0487 | 0 | 0 | 0 | 210.739 | 0 | 0
8001 | 1245.954 | 374.31 | 1712.801 | 1294.3029 | -418.4981 | 0 | 0 | 0 | 0 | 0
8002 | 1352.375 | 574.57 | 2579.5392 | 1404.8536 | -614.9724 | 0 | 559.7132 | 0 | 0 | 0
8003 | 1036.347 | 716.75 | 3172.9616 | 1076.5622 | -4.5406 | 0 | 2091.8588 | 0 | 0 | 0
8004 | 1453.973 | 658.75 | 2915.4782 | 1510.3941 | 0 | 0 | 1405.0842 | 0 | 0 | 0
8005 | 1380.768 | 679.22 | 3010.9475 | 1434.3484 | 0 | 0 | 1576.5992 | 0 | 0 | 0
8006 | 1648.157 | 536.4 | 2400.014 | 1712.1133 | 0 | 0 | 687.9007 | 0 | 0 | 0
8007 | 1281.294 | 408.96 | 1847.2732 | 1331.0143 | 0 | 0 | 516.259 | 0 | 0 | 0
8008 | 1404.316 | 146.09 | 644.7092 | 644.7092 | 0 | 0 | 0 | 783.69 | 0 | 0
8009 | 1308.225 | 63.76 | 260.2455 | 260.2455 | 0 | 0 | 0 | 1057.701 | 0 | 0
8010 | 1254.291 | 1.96 | 0 | 0 | 0 | 0 | 0 | 1254.291 | 0 | 0
8011 | 1336 | 0 | 0 | 0 | 0 | 0 | 0 | 1336 | 0 | 0
8012 | 854.4 | 0 | 0 | 0 | 0 | 0 | 0 | 854.4 | 0 | 0
8013 | 1313.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1313.6 | 0 | 0
8014 | 1232 | 0 | 0 | 0 | 0 | 0 | 0 | 1232 | 0 | 0
8015 | 1172.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1172.8 | 0 | 0
8016 | 1341.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1341.6 | 0 | 0
8017 | 1092 | 0 | 0 | 0 | 0 | 0 | 0 | 1092 | 0 | 0
8018 | 1248 | 0 | 0 | 0 | 0 | 0 | 0 | 1248 | 0 | 0
8019 | 1142.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1142.4 | 0 | 0
8020 | 1088.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1088.8 | 0 | 0
8021 | 978.4 | 0 | 0 | 0 | 0 | 0 | 0 | 978.4 | 0 | 0
8022 | 1040.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1040.8 | 0 | 0
8023 | 858.4 | 32.66 | 112.3073 | 112.3073 | 0 | 0 | 0 | 750.288 | 0 | 0
8024 | 1146.178 | 117.95 | 518.1787 | 518.1787 | 0 | 0 | 0 | 105.633 | 0 | 562.7444
8025 | 1191.895 | 194.12 | 868.1748 | 868.1748 | 0 | 0 | 0 | 0 | 0 | 369.9713
8026 | 1166.901 | 400.97 | 1798.6073 | 1212.1823 | -586.425 | 0 | 0 | 0 | 0 | 0
8027 | 1126.266 | 571.69 | 2542.7302 | 1169.9705 | -451.5861 | 0 | 921.1736 | 0 | 0 | 0
8028 | 1448.14 | 612.78 | 2713.1835 | 1504.3347 | 0 | 0 | 1208.8488 | 0 | 0 | 0
8029 | 920.542 | 591.4 | 2622.8469 | 956.2634 | 0 | 0 | 1666.5835 | 0 | 0 | 0
8030 | 997.387 | 513.27 | 2295.1643 | 1036.0904 | 0 | 0 | 1259.0739 | 0 | 0 | 0
8031 | 860.713 | 410.99 | 1858.67 | 894.1128 | 0 | 0 | 964.5572 | 0 | 0 | 0
8032 | 234.947 | 192.64 | 864.3375 | 244.0641 | 0 | 0 | 620.2734 | 0 | 0 | 0
8033 | 183.063 | 154.71 | 647.2751 | 190.1667 | 0 | 0 | 457.1084 | 0 | 0 | 0
8034 | 137.552 | 2.94 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142.8897
8035 | 148 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 153.7431
8036 | 100.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 104.7115
8037 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 99.7253
8038 | 102.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 106.3736
8039 | 91.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 94.739
8040 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.8805
8041 | 89.6 | 0 | 0 | 0 | 0 | 0 | 0 | 89.6 | 0 | 0
8042 | 96 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0
8043 | 89.6 | 0 | 0 | 0 | 0 | 0 | 0 | 89.6 | 0 | 0
8044 | 89.6 | 0 | 0 | 0 | 0 | 0 | 0 | 89.6 | 0 | 0
8045 | 91.2 | 0 | 0 | 0 | 0 | 0 | 0 | 61.278 | 0 | 31.0831
8046 | 92 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95.57
8047 | 72.8 | 51.18 | 185.2739 | 75.625 | -109.649 | 0 | 0 | 0 | 0 | 0
8048 | 89.61 | 235.03 | 1066.8971 | 93.0873 | -614.9724 | 0 | 358.8374 | 0 | 0 | 0
8049 | 636.197 | 483.61 | 2215.7861 | 660.8845 | -313.3897 | 0 | 1241.5119 | 0 | 0 | 0
8050 | 1258.648 | 772.15 | 3450.4814 | 1307.4895 | 0 | 0 | 2142.9919 | 0 | 0 | 0
8051 | 1251.361 | 895.29 | 3927.2626 | 1299.9197 | 0 | 0 | 2627.3429 | 0 | 0 | 0
8052 | 1077.291 | 947.58 | 4111.9746 | 1119.095 | 0 | 0 | 2992.8796 | 0 | 0 | 0
8053 | 1356.354 | 780.71 | 3424.6972 | 1408.987 | 0 | 0 | 2015.7102 | 0 | 0 | 0
8054 | 1104.063 | 792.86 | 3494.5059 | 1146.9059 | 0 | 0 | 2347.6 | 0 | 0 | 0
8055 | 1125.992 | 546.94 | 2462.7318 | 1169.6858 | 0 | 0 | 1293.046 | 0 | 0 | 0
8056 | 1050.113 | 137.56 | 601.4534 | 601.4534 | 0 | 0 | 0 | 471.127 | 0 | 0
8057 | 951.408 | 90.75 | 364.8469 | 364.8469 | 0 | 0 | 0 | 600.19 | 0 | 0
8058 | 1136.61 | 1.96 | 0 | 0 | 0 | 0 | 0 | 1136.61 | 0 | 0
8059 | 1047.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1047.2 | 0 | 0
8060 | 1128.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1128.8 | 0 | 0
8061 | 778.4 | 0 | 0 | 0 | 0 | 0 | 0 | 778.4 | 0 | 0
8062 | 1089.6 | 0 | 0 | 0 | 0 | 0 | 0 | 783.726 | 0 | 317.7434
8063 | 952.8 | 0 | 0 | 0 | 0 | 0 | 0 | 360.8 | 0 | 614.9724
8064 | 999.2 | 0 | 0 | 0 | 0 | 0 | 0 | 999.2 | 0 | 0
8065 | 960 | 0 | 0 | 0 | 0 | 0 | 0 | 960 | 0 | 0
8066 | 1305.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1305.6 | 0 | 0
8067 | 1168.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1168.8 | 0 | 0
8068 | 1358.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1358.4 | 0 | 0
8069 | 1282.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1282.4 | 0 | 0
8070 | 1162.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1162.4 | 0 | 0
8071 | 1039.2 | 112.19 | 387.7806 | 387.7806 | 0 | 0 | 0 | 665.905 | 0 | 0
8072 | 1081.05 | 362.36 | 1658.5048 | 1122.9999 | -535.5049 | 0 | 0 | 0 | 0 | 0
8073 | 811.981 | 597.57 | 2732.9249 | 843.4897 | -502.5073 | 0 | 1386.928 | 0 | 0 | 0
8074 | 1146.669 | 786.7 | 3461.3816 | 1191.1652 | 0 | 0 | 2270.2164 | 0 | 0 | 0
8075 | 1380.393 | 913.49 | 3921.9284 | 1433.9588 | 0 | 0 | 2487.9696 | 0 | 0 | 0
8076 | 1173.817 | 968.94 | 4104.9492 | 1219.3667 | 0 | 0 | 2885.5825 | 0 | 0 | 0
8077 | 1141.587 | 944.63 | 4009.9224 | 1185.886 | 0 | 0 | 2824.0364 | 0 | 0 | 0
8078 | 1217.119 | 844.32 | 3641.9238 | 1264.349 | 0 | 0 | 2377.5748 | 0 | 0 | 0
8079 | 1621.666 | 678.3 | 3003.8151 | 1684.5943 | 0 | 0 | 1319.2207 | 0 | 0 | 0
8080 | 617.579 | 458.62 | 2088.3403 | 641.544 | 0 | 0 | 1446.7964 | 0 | 0 | 0
8081 | 1446.565 | 209.28 | 861.6221 | 861.6221 | 0 | 0 | 0 | 617.129 | 0 | 0
8082 | 1314.233 | 5.5 | 0 | 0 | 0 | 0 | 0 | 1314.233 | 0 | 0
8083 | 1122.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1122.4 | 0 | 0
8084 | 976.8 | 0 | 0 | 0 | 0 | 0 | 0 | 976.8 | 0 | 0
8085 | 1206.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1206.4 | 0 | 0
8086 | 1304 | 0 | 0 | 0 | 0 | 0 | 0 | 998.126 | 0 | 317.7434
8087 | 1134.4 | 0 | 0 | 0 | 0 | 0 | 0 | 542.4 | 0 | 614.9724
8088 | 949.6 | 0 | 0 | 0 | 0 | 0 | 0 | 949.6 | 0 | 0
8089 | 1222.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1222.4 | 0 | 0
8090 | 851.2 | 0 | 0 | 0 | 0 | 0 | 0 | 851.2 | 0 | 0
8091 | 1256.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1256.8 | 0 | 0
8092 | 1092.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1092.8 | 0 | 0
8093 | 1028.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1028.8 | 0 | 0
8094 | 1088.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1088.8 | 0 | 0
8095 | 1353.6 | 105.13 | 371.1275 | 371.1275 | 0 | 0 | 0 | 996.336 | 0 | 0
8096 | 697.26 | 300.53 | 1387.8026 | 724.317 | -614.9724 | 0 | 48.5132 | 0 | 0 | 0
8097 | 894.813 | 593.81 | 2736.7747 | 929.536 | -423.0387 | 0 | 1384.2001 | 0 | 0 | 0
8098 | 1264.732 | 788.49 | 3485.2502 | 1313.8096 | 0 | 0 | 2171.4406 | 0 | 0 | 0
8099 | 1241.914 | 915.74 | 3904.4401 | 1290.1062 | 0 | 0 | 2614.3339 | 0 | 0 | 0
8100 | 1308.586 | 972.72 | 4041.8459 | 1359.3654 | 0 | 0 | 2682.4806 | 0 | 0 | 0
8101 | 1086.618 | 947.83 | 3915.494 | 1128.7839 | 0 | 0 | 2786.7101 | 0 | 0 | 0
8102 | 1312.456 | 846.4 | 3565.2309 | 1363.3855 | 0 | 0 | 2201.8454 | 0 | 0 | 0
8103 | 1471.833 | 681.53 | 2975.8359 | 1528.9471 | 0 | 0 | 1446.8888 | 0 | 0 | 0
8104 | 1659.084 | 444.82 | 2010.6004 | 1723.4643 | 0 | 0 | 287.136 | 0 | 0 | 0
8105 | 1382.135 | 174 | 721.4904 | 721.4904 | 0 | 0 | 0 | 687.596 | 0 | 0
8106 | 1357.739 | 3.91 | 0 | 0 | 0 | 0 | 0 | 1357.739 | 0 | 0
8107 | 1292 | 0 | 0 | 0 | 0 | 0 | 0 | 1292 | 0 | 0
8108 | 1217.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1217.6 | 0 | 0
8109 | 1288 | 0 | 0 | 0 | 0 | 0 | 0 | 1288 | 0 | 0
8110 | 1356 | 0 | 0 | 0 | 0 | 0 | 0 | 1050.126 | 0 | 317.7434
8111 | 968.8 | 0 | 0 | 0 | 0 | 0 | 0 | 376.8 | 0 | 614.9724
8112 | 1264 | 0 | 0 | 0 | 0 | 0 | 0 | 1264 | 0 | 0
8113 | 1316.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1316.8 | 0 | 0
8114 | 1169.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1169.6 | 0 | 0
8115 | 1160.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1160.8 | 0 | 0
8116 | 1196 | 0 | 0 | 0 | 0 | 0 | 0 | 1196 | 0 | 0
8117 | 840 | 0 | 0 | 0 | 0 | 0 | 0 | 840 | 0 | 0
8118 | 1152.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1152.8 | 0 | 0
8119 | 706.4 | 100.89 | 349.7479 | 349.7479 | 0 | 0 | 0 | 369.717 | 0 | 0
8120 | 959.437 | 346.95 | 1601.1918 | 996.6677 | -604.5241 | 0 | 0 | 0 | 0 | 0
8121 | 900.079 | 581.47 | 2685.6302 | 935.0063 | -433.487 | 0 | 1317.1369 | 0 | 0 | 0
8122 | 1146.42 | 766.82 | 3390.7325 | 1190.9065 | 0 | 0 | 2199.8259 | 0 | 0 | 0
8123 | 1422.593 | 892.33 | 3819.202 | 1477.7964 | 0 | 0 | 2341.4057 | 0 | 0 | 0
8124 | 1547.461 | 949.31 | 4007.2911 | 1607.5098 | 0 | 0 | 2399.7813 | 0 | 0 | 0
8125 | 1494.729 | 893.54 | 3798.9993 | 1552.7316 | 0 | 0 | 2246.2678 | 0 | 0 | 0
8126 | 1257.696 | 828.67 | 3579.5664 | 1306.5006 | 0 | 0 | 2273.0658 | 0 | 0 | 0
8127 | 1228.071 | 554.73 | 2472.5132 | 1275.726 | 0 | 0 | 1196.7872 | 0 | 0 | 0
8128 | 1769.154 | 422.01 | 1925.2792 | 1837.8056 | 0 | 0 | 87.4736 | 0 | 0 | 0
8129 | 1953.371 | 181.6 | 756.4067 | 756.4067 | 0 | 0 | 0 | 1225.22 | 0 | 0
8130 | 1544.713 | 3.91 | 0 | 0 | 0 | 0 | 0 | 1544.713 | 0 | 0
8131 | 1589.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1589.6 | 0 | 0
8132 | 1320 | 0 | 0 | 0 | 0 | 0 | 0 | 1320 | 0 | 0
8133 | 1744 | 0 | 0 | 0 | 0 | 0 | 0 | 1744 | 0 | 0
8134 | 1516.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1210.926 | 0 | 317.7434
8135 | 1599.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1007.2 | 0 | 614.9724
8136 | 1542.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1542.4 | 0 | 0
8137 | 1434.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1434.4 | 0 | 0
8138 | 1324 | 0 | 0 | 0 | 0 | 0 | 0 | 1324 | 0 | 0
8139 | 1325.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1325.6 | 0 | 0
8140 | 1516.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1516.8 | 0 | 0
8141 | 1291.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1291.2 | 0 | 0
8142 | 1542.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1542.4 | 0 | 0
8143 | 1000.8 | 103.27 | 353.3442 | 353.3442 | 0 | 0 | 0 | 660.655 | 0 | 0
8144 | 828.43 | 349.15 | 1606.8159 | 860.577 | -614.9724 | 0 | 131.2665 | 0 | 0 | 0
8145 | 1062.166 | 583.77 | 2694.271 | 1103.3841 | -423.0387 | 0 | 1167.8482 | 0 | 0 | 0
8146 | 1354.15 | 770.94 | 3416.6537 | 1406.6974 | 0 | 0 | 2009.9563 | 0 | 0 | 0
8147 | 1544.599 | 894.11 | 3829.4862 | 1604.5368 | 0 | 0 | 2224.9494 | 0 | 0 | 0
8148 | 1620.767 | 950.48 | 4001.2411 | 1683.6605 | 0 | 0 | 2317.5807 | 0 | 0 | 0
8149 | 936.447 | 904.46 | 3807.7346 | 972.7856 | 0 | 0 | 2834.9491 | 0 | 0 | 0
8150 | 1379.589 | 559.44 | 2431.8367 | 1433.1236 | 0 | 0 | 998.7131 | 0 | 0 | 0
8151 | 1282.753 | 527.73 | 2332.6942 | 1332.5299 | 0 | 0 | 1000.1643 | 0 | 0 | 0
8152 | 1281.053 | 350.61 | 1583.9581 | 1330.7639 | 0 | 0 | 253.1941 | 0 | 0 | 0
8153 | 1015.736 | 174.98 | 725.7246 | 725.7246 | 0 | 0 | 0 | 317.121 | 0 | 0
8154 | 1172.039 | 4.6 | 0 | 0 | 0 | 0 | 0 | 1172.039 | 0 | 0
8155 | 1207.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1207.2 | 0 | 0
8156 | 1226.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1226.4 | 0 | 0
8157 | 1287.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1287.2 | 0 | 0
8158 | 1448.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1142.926 | 0 | 317.7434
8159 | 1248.8 | 0 | 0 | 0 | 0 | 0 | 0 | 656.8 | 0 | 614.9724
8160 | 1272.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1272.8 | 0 | 0
8161 | 1412 | 0 | 0 | 0 | 0 | 0 | 0 | 1412 | 0 | 0
8162 | 1366.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1366.4 | 0 | 0
8163 | 1345.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1345.6 | 0 | 0
8164 | 1445.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1445.6 | 0 | 0
8165 | 1436 | 0 | 0 | 0 | 0 | 0 | 0 | 1436 | 0 | 0
8166 | 1366.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1366.4 | 0 | 0
8167 | 1041.6 | 37.71 | 131.5802 | 131.5802 | 0 | 0 | 0 | 914.935 | 0 | 0
8168 | 1319.128 | 221.91 | 1014.1383 | 1014.1383 | 0 | 0 | 0 | 342.873 | 0 | 0
8169 | 889.005 | 398.78 | 1835.1317 | 923.5026 | -614.9724 | 0 | 296.6567 | 0 | 0 | 0
8170 | 1469.341 | 480.48 | 2158.4794 | 1526.3584 | -423.0387 | 0 | 209.0823 | 0 | 0 | 0
8171 | 1714.76 | 640.26 | 2818.6128 | 1781.3008 | 0 | 0 | 1037.312 | 0 | 0 | 0
8172 | 1647.544 | 652.97 | 2848.8742 | 1711.4765 | 0 | 0 | 1137.3977 | 0 | 0 | 0
8173 | 1465.729 | 439.97 | 1927.9645 | 1522.6062 | 0 | 0 | 405.3582 | 0 | 0 | 0
8174 | 1506.159 | 300.74 | 1320.2533 | 1320.2533 | 0 | 0 | 0 | 235.224 | 0 | 0
8175 | 1621.22 | 255.6 | 1128.5388 | 1128.5388 | 0 | 0 | 0 | 534.838 | 0 | 0
8176 | 1662.845 | 330.02 | 1496.3785 | 1496.3785 | 0 | 0 | 0 | 222.364 | 0 | 0
8177 | 1580.403 | 85.58 | 355.2837 | 355.2837 | 0 | 0 | 0 | 1238.391 | 0 | 0
8178 | 1155.725 | 2.94 | 0 | 0 | 0 | 0 | 0 | 1155.725 | 0 | 0
8179 | 1545.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1545.6 | 0 | 0
8180 | 1300 | 0 | 0 | 0 | 0 | 0 | 0 | 1300 | 0 | 0
8181 | 1517.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1517.6 | 0 | 0
8182 | 1541.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1541.6 | 0 | 0
8183 | 1264.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1264.8 | 0 | 0
8184 | 1515.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1226.128 | 0 | 300.2894
8185 | 1142.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1142.4 | 0 | 0
8186 | 1111.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1111.2 | 0 | 0
8187 | 1584.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1584.8 | 0 | 0
8188 | 1384 | 0 | 0 | 0 | 0 | 0 | 0 | 1384 | 0 | 0
8189 | 1290.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1290.4 | 0 | 0
8190 | 1424 | 0 | 0 | 0 | 0 | 0 | 0 | 1424 | 0 | 0
8191 | 1168.8 | 85.77 | 285.8832 | 285.8832 | 0 | 0 | 0 | 301.596 | 0 | 614.9724
8192 | 1085.638 | 243.67 | 1110.3119 | 1110.3119 | 0 | 0 | 0 | 0 | 0 | 17.454
8193 | 1060.777 | 492.06 | 2259.1417 | 1101.9402 | -614.9724 | 0 | 542.2291 | 0 | 0 | 0
8194 | 1138.269 | 616.22 | 2735.8346 | 1182.4403 | -423.0387 | 0 | 1130.3556 | 0 | 0 | 0
8195 | 1033.825 | 757.41 | 3280.4426 | 1073.9423 | 0 | 0 | 2206.5002 | 0 | 0 | 0
8196 | 1090.429 | 813.17 | 3476.705 | 1132.7428 | 0 | 0 | 2343.9622 | 0 | 0 | 0
8197 | 1135.24 | 719.85 | 3101.0649 | 1179.2927 | 0 | 0 | 1921.7722 | 0 | 0 | 0
8198 | 1171.847 | 530.58 | 2328.62 | 1217.3202 | 0 | 0 | 1111.2998 | 0 | 0 | 0
8199 | 1104.482 | 256.09 | 1132.7148 | 1132.7148 | 0 | 0 | 0 | 0 | 0 | 14.6264
8200 | 224.458 | 175.92 | 780.0208 | 233.168 | -16.2781 | 0 | 530.5747 | 0 | 0 | 0
8201 | 183.44 | 85.9 | 359.9614 | 190.5583 | 0 | 0 | 169.4031 | 0 | 0 | 0
8202 | 160.064 | 2.94 | 0 | 0 | 0 | 0 | 0 | 51.79 | 0 | 112.4755
8203 | 206.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 214.4093
8204 | 149.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 155.4052
8205 | 116 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 120.5014
8206 | 109.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.853
8207 | 99.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 103.0494
8208 | 108.8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.022
8209 | 100.8 | 0 | 0 | 0 | 0 | 0 | 0 | 100.8 | 0 | 0
8210 | 109.6 | 0 | 0 | 0 | 0 | 0 | 0 | 109.6 | 0 | 0
8211 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 0 | 0
8212 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 104 | 0 | 0
8213 | 93.6 | 0 | 0 | 0 | 0 | 0 | 0 | 93.6 | 0 | 0
8214 | 101.6 | 0 | 0 | 0 | 0 | 0 | 0 | 101.6 | 0 | 0
8215 | 93.6 | 60.06 | 207.7236 | 97.2321 | -110.4914 | 0 | 0 | 0 | 0 | 0
8216 | 100.012 | 103.92 | 454.7565 | 103.8929 | -350.8636 | 0 | 0 | 0 | 0 | 0
8217 | 218.574 | 360.99 | 1640.7983 | 227.0557 | -576.6561 | 0 | 837.0865 | 0 | 0 | 0
8218 | 955.563 | 592.93 | 2609.2033 | 992.6434 | 0 | 0 | 1616.5599 | 0 | 0 | 0
8219 | 1162.174 | 506.07 | 2195.4245 | 1207.2719 | 0 | 0 | 988.1526 | 0 | 0 | 0
8220 | 1591.079 | 506.03 | 2184.1649 | 1652.8204 | 0 | 0 | 531.3445 | 0 | 0 | 0
8221 | 1379.816 | 617.47 | 2656.3557 | 1433.3594 | 0 | 0 | 1222.9963 | 0 | 0 | 0
8222 | 1610.809 | 601.56 | 2614.0057 | 1673.316 | 0 | 0 | 940.6896 | 0 | 0 | 0
8223 | 1808.052 | 294.51 | 1302.6414 | 1302.6414 | 0 | 0 | 0 | 554.071 | 0 | 0
8224 | 2055.558 | 289.04 | 1301.6244 | 1301.6244 | 0 | 0 | 0 | 802.556 | 0 | 0
8225 | 1608.955 | 108.6 | 451.2381 | 451.2381 | 0 | 0 | 0 | 1174.573 | 0 | 0
8226 | 1527.332 | 1.96 | 0 | 0 | 0 | 0 | 0 | 1527.332 | 0 | 0
8227 | 1779.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1779.2 | 0 | 0
8228 | 1836.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1836.8 | 0 | 0
8229 | 1579.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1579.2 | 0 | 0
8230 | 1553.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1247.726 | 0 | 317.7434
8231 | 1396 | 0 | 0 | 0 | 0 | 0 | 0 | 804 | 0 | 614.9724
8232 | 1387.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1387.2 | 0 | 0
8233 | 1321.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1321.6 | 0 | 0
8234 | 1526.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1526.4 | 0 | 0
8235 | 1572 | 0 | 0 | 0 | 0 | 0 | 0 | 1572 | 0 | 0
8236 | 1433.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1433.6 | 0 | 0
8237 | 1316 | 0 | 0 | 0 | 0 | 0 | 0 | 1316 | 0 | 0
8238 | 1384.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1384.8 | 0 | 0
8239 | 1184.8 | 31.38 | 102.8448 | 102.8448 | 0 | 0 | 0 | 1085.797 | 0 | 0
8240 | 1308.643 | 156.67 | 702.4647 | 702.4647 | 0 | 0 | 0 | 632.419 | 0 | 0
8241 | 1418.787 | 465.11 | 2130.7849 | 1473.8427 | -614.9724 | 0 | 41.9698 | 0 | 0 | 0
8242 | 1582.275 | 730.82 | 3237.4651 | 1643.6748 | -423.0387 | 0 | 1170.7516 | 0 | 0 | 0
8243 | 1549.679 | 872.74 | 3749.4525 | 1609.8139 | 0 | 0 | 2139.6386 | 0 | 0 | 0
8244 | 1523.622 | 601.51 | 2614.4202 | 1582.7458 | 0 | 0 | 1031.6744 | 0 | 0 | 0
8245 | 1514.182 | 365.97 | 1589.8138 | 1572.9395 | 0 | 0 | 16.8743 | 0 | 0 | 0
8246 | 1331.149 | 221.47 | 964.5146 | 964.5146 | 0 | 0 | 0 | 402.664 | 0 | 0
8247 | 1245.736 | 39.23 | 143.4319 | 143.4319 | 0 | 0 | 0 | 1107.662 | 0 | 0
8248 | 1236.827 | 50.98 | 199.1835 | 199.1835 | 0 | 0 | 0 | 1045.084 | 0 | 0
8249 | 1300.328 | 66.5 | 270.7904 | 270.7904 | 0 | 0 | 0 | 1039.653 | 0 | 0
8250 | 1367.211 | 2.94 | 0 | 0 | 0 | 0 | 0 | 1367.211 | 0 | 0
8251 | 1213.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1213.6 | 0 | 0
8252 | 1144.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1144.8 | 0 | 0
8253 | 1432 | 0 | 0 | 0 | 0 | 0 | 0 | 1432 | 0 | 0
8254 | 1488.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1182.926 | 0 | 317.7434
8255 | 1432.8 | 0 | 0 | 0 | 0 | 0 | 0 | 840.8 | 0 | 614.9724
8256 | 1107.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1107.2 | 0 | 0
8257 | 1325.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1325.6 | 0 | 0
8258 | 1274.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.4 | 0 | 0
8259 | 1459.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1459.2 | 0 | 0
8260 | 1384.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1384.8 | 0 | 0
8261 | 1256 | 0 | 0 | 0 | 0 | 0 | 0 | 1256 | 0 | 0
8262 | 1425.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1425.6 | 0 | 0
8263 | 991.2 | 57.91 | 194.0622 | 194.0622 | 0 | 0 | 0 | 804.387 | 0 | 0
8264 | 982.402 | 226.07 | 1020.5727 | 1020.5239 | -0.048824 | 0 | 0 | 0 | 0 | 0
8265 | 1106.567 | 526.87 | 2396.5298 | 1149.5071 | -614.9724 | 0 | 632.0504 | 0 | 0 | 0
8266 | 1162.384 | 476.21 | 2104.9114 | 1207.49 | -422.9899 | 0 | 474.4315 | 0 | 0 | 0
8267 | 957.501 | 501.36 | 2185.8436 | 994.6566 | 0 | 0 | 1191.187 | 0 | 0 | 0
8268 | 1301.609 | 616.41 | 2662.3766 | 1352.1176 | 0 | 0 | 1310.259 | 0 | 0 | 0
8269 | 1278.001 | 532.39 | 2315.313 | 1327.5935 | 0 | 0 | 987.7194 | 0 | 0 | 0
8270 | 1638.085 | 396.68 | 1745.1328 | 1701.6505 | 0 | 0 | 43.4823 | 0 | 0 | 0
8271 | 1340.07 | 34.32 | 122.2902 | 122.2902 | 0 | 0 | 0 | 1222.348 | 0 | 0
8272 | 1262.195 | 96.5 | 409.3493 | 409.3493 | 0 | 0 | 0 | 868.137 | 0 | 0
8273 | 1317.571 | 8.81 | 12.207 | 12.207 | 0 | 0 | 0 | 1305.82 | 0 | 0
8274 | 1073.537 | 0.98 | 0 | 0 | 0 | 0 | 0 | 1073.537 | 0 | 0
8275 | 968 | 0 | 0 | 0 | 0 | 0 | 0 | 968 | 0 | 0
8276 | 1704.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1704.8 | 0 | 0
8277 | 1280 | 0 | 0 | 0 | 0 | 0 | 0 | 1280 | 0 | 0
8278 | 953.6 | 0 | 0 | 0 | 0 | 0 | 0 | 647.726 | 0 | 317.7434
8279 | 1074.4 | 0 | 0 | 0 | 0 | 0 | 0 | 482.4 | 0 | 614.9724
8280 | 1128 | 0 | 0 | 0 | 0 | 0 | 0 | 1128 | 0 | 0
8281 | 1326.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1326.4 | 0 | 0
8282 | 1213.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1213.6 | 0 | 0
8283 | 932 | 0 | 0 | 0 | 0 | 0 | 0 | 932 | 0 | 0
8284 | 1318.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1318.4 | 0 | 0
8285 | 1150.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1150.4 | 0 | 0
8286 | 1121.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1121.6 | 0 | 0
8287 | 1252.8 | 68.6 | 226.902 | 226.902 | 0 | 0 | 0 | 1034.374 | 0 | 0
8288 | 1217.408 | 233.01 | 1041.2657 | 1041.2657 | 0 | 0 | 0 | 215.039 | 0 | 0
8289 | 1302.102 | 513.36 | 2299.7589 | 1352.6297 | -614.9724 | 0 | 332.1568 | 0 | 0 | 0
8290 | 1274.013 | 414.65 | 1815.7756 | 1323.4508 | -423.0387 | 0 | 69.2862 | 0 | 0 | 0
8291 | 1359.024 | 381.27 | 1669.1619 | 1411.7606 | 0 | 0 | 257.4013 | 0 | 0 | 0
8292 | 1360.939 | 722.65 | 3055.3138 | 1413.7499 | 0 | 0 | 1641.5639 | 0 | 0 | 0
8293 | 1309.39 | 448.95 | 1946.9247 | 1360.2005 | 0 | 0 | 586.7242 | 0 | 0 | 0
8294 | 1346.761 | 484.61 | 2120.1153 | 1399.0217 | 0 | 0 | 721.0936 | 0 | 0 | 0
8295 | 1666.961 | 261.88 | 1159.3217 | 1159.3217 | 0 | 0 | 0 | 550.946 | 0 | 0
8296 | 1629.508 | 95.6 | 406.5581 | 406.5581 | 0 | 0 | 0 | 1238.137 | 0 | 0
8297 | 1510.972 | 9.79 | 16.329 | 16.329 | 0 | 0 | 0 | 1495.253 | 0 | 0
8298 | 1715.055 | 0.98 | 0 | 0 | 0 | 0 | 0 | 1715.055 | 0 | 0
8299 | 1569.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1569.6 | 0 | 0
8300 | 1138.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1138.4 | 0 | 0
8301 | 1421.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1421.6 | 0 | 0
8302 | 1424.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1118.926 | 0 | 317.7434
8303 | 1243.2 | 0 | 0 | 0 | 0 | 0 | 0 | 651.2 | 0 | 614.9724
8304 | 1226.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1226.4 | 0 | 0
8305 | 871.2 | 0 | 0 | 0 | 0 | 0 | 0 | 871.2 | 0 | 0
8306 | 1341.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1341.6 | 0 | 0
8307 | 1340 | 0 | 0 | 0 | 0 | 0 | 0 | 1340 | 0 | 0
8308 | 1356 | 0 | 0 | 0 | 0 | 0 | 0 | 1356 | 0 | 0
8309 | 1612 | 0 | 0 | 0 | 0 | 0 | 0 | 1612 | 0 | 0
8310 | 1690.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1690.4 | 0 | 0
8311 | 1544.8 | 74.93 | 243.1063 | 243.1063 | 0 | 0 | 0 | 1310.775 | 0 | 0
8312 | 1215.149 | 309.6 | 1387.7974 | 1262.3026 | -125.4949 | 0 | 0 | 0 | 0 | 0
8313 | 1492.134 | 543.38 | 2445.0784 | 1550.0359 | -614.9724 | 0 | 280.0701 | 0 | 0 | 0
8314 | 1882.658 | 634.12 | 2757.0117 | 1955.713 | -297.5448 | 0 | 503.7538 | 0 | 0 | 0
8315 | 1450.765 | 581.55 | 2500.3324 | 1507.0616 | 0 | 0 | 993.2708 | 0 | 0 | 0
8316 | 1737.05 | 438.67 | 1884.4957 | 1804.4558 | 0 | 0 | 80.0399 | 0 | 0 | 0
8317 | 1360.505 | 569.12 | 2412.7528 | 1413.2991 | 0 | 0 | 999.4538 | 0 | 0 | 0
8318 | 1346.552 | 600.16 | 2554.3035 | 1398.8046 | 0 | 0 | 1155.4989 | 0 | 0 | 0
8319 | 1602.583 | 201.37 | 873.3086 | 873.3086 | 0 | 0 | 0 | 761.897 | 0 | 0
8320 | 1371.928 | 125.3 | 538.3574 | 538.3574 | 0 | 0 | 0 | 853.681 | 0 | 0
8321 | 1617.23 | 59.24 | 237.3284 | 237.3284 | 0 | 0 | 0 | 1388.767 | 0 | 0
8322 | 1416.264 | 2.94 | 0 | 0 | 0 | 0 | 0 | 1416.264 | 0 | 0
8323 | 1540.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1540.8 | 0 | 0
8324 | 1249.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1249.6 | 0 | 0
8325 | 1344 | 0 | 0 | 0 | 0 | 0 | 0 | 1344 | 0 | 0
8326 | 1529.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1223.726 | 0 | 317.7434
8327 | 1204 | 0 | 0 | 0 | 0 | 0 | 0 | 612 | 0 | 614.9724
8328 | 1254.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1254.4 | 0 | 0
8329 | 1176.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1176.8 | 0 | 0
8330 | 1458.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1458.4 | 0 | 0
8331 | 1106.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1106.4 | 0 | 0
8332 | 1453.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1453.6 | 0 | 0
8333 | 1477.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1477.6 | 0 | 0
8334 | 1080 | 0 | 0 | 0 | 0 | 0 | 0 | 1080 | 0 | 0
8335 | 1225.6 | 66.12 | 215.4585 | 215.4585 | 0 | 0 | 0 | 1018.19 | 0 | 0
8336 | 918.666 | 238.97 | 1074.6747 | 954.3146 | -120.3601 | 0 | 0 | 0 | 0 | 0
8337 | 1374.39 | 543.91 | 2485.3528 | 1427.7229 | -614.9724 | 0 | 442.6576 | 0 | 0 | 0
8338 | 1560.354 | 637.58 | 2839.0336 | 1620.9031 | -302.6797 | 0 | 915.4508 | 0 | 0 | 0
8339 | 1797.136 | 656.57 | 2869.1413 | 1866.8734 | 0 | 0 | 1002.2679 | 0 | 0 | 0
8340 | 1185.147 | 689.88 | 2983.8846 | 1231.1363 | 0 | 0 | 1752.7482 | 0 | 0 | 0
8341 | 1448.412 | 626.36 | 2716.892 | 1504.6173 | 0 | 0 | 1212.2748 | 0 | 0 | 0
8342 | 1481.714 | 581.63 | 2547.2542 | 1539.2115 | 0 | 0 | 1008.0426 | 0 | 0 | 0
8343 | 915.477 | 459.11 | 2042.9207 | 951.0019 | 0 | 0 | 1091.9188 | 0 | 0 | 0
8344 | 1225.411 | 307.24 | 1391.6524 | 1272.9628 | 0 | 0 | 118.6897 | 0 | 0 | 0
8345 | 1517.155 | 100.11 | 420.9943 | 420.9943 | 0 | 0 | 0 | 1111.887 | 0 | 0
8346 | 1563.602 | 3.91 | 0 | 0 | 0 | 0 | 0 | 1563.602 | 0 | 0
8347 | 1392 | 0 | 0 | 0 | 0 | 0 | 0 | 1392 | 0 | 0
8348 | 1641.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1641.6 | 0 | 0
8349 | 1546.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1546.4 | 0 | 0
8350 | 1494.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1494.4 | 0 | 0
8351 | 1361.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1361.6 | 0 | 0
8352 | 1280.8 | 0 | 0 | 0 | 0 | 0 | 0 | 974.926 | 0 | 317.7434
8353 | 1408 | 0 | 0 | 0 | 0 | 0 | 0 | 1408 | 0 | 0
8354 | 1036.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1036.8 | 0 | 0
8355 | 1119.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1119.2 | 0 | 0
8356 | 1168 | 0 | 0 | 0 | 0 | 0 | 0 | 1168 | 0 | 0
8357 | 1204.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1204.8 | 0 | 0
8358 | 1127.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1127.2 | 0 | 0
8359 | 1190.4 | 81.32 | 259.2815 | 259.2815 | 0 | 0 | 0 | 348.804 | 0 | 614.9724
8360 | 210.344 | 321.55 | 1435.2095 | 218.5063 | -614.9724 | 0 | 601.7308 | 0 | 0 | 0
8361 | 101.182 | 556.12 | 2523.8291 | 105.1083 | -423.0387 | 0 | 1995.6821 | 0 | 0 | 0
8362 | 0 | 529.89 | 2354.559 | 0 | 0 | 0 | 2354.559 | 0 | 0 | 0
8363 | 0 | 333.11 | 1460.5449 | 0 | 0 | 0 | 1460.5449 | 0 | 0 | 0
8364 | 0 | 452.11 | 1978.3039 | 0 | 0 | 0 | 1978.3039 | 0 | 0 | 0
8365 | 0 | 454.25 | 1992.7641 | 0 | 0 | 0 | 1992.7641 | 0 | 0 | 0
8366 | 0 | 689.65 | 3020.4162 | 0 | 0 | 0 | 3020.4162 | 0 | 0 | 0
8367 | 0 | 498.07 | 2222.6349 | 0 | 0 | 0 | 2222.6349 | 0 | 0 | 0
8368 | 0 | 266.17 | 1197.7564 | 0 | 0 | 0 | 1197.7564 | 0 | 0 | 0
8369 | 0 | 97.58 | 409.6568 | 0 | 0 | 0 | 409.6568 | 0 | 0 | 0
8370 | 0 | 3.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8373 | 137.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 142.9395
8374 | 224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 232.6923
8375 | 279.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290.0343
8376 | 275.2 | 0 | 0 | 0 | 0 | 0 | 0 | 170.51 | 0 | 108.7525
8377 | 272 | 0 | 0 | 0 | 0 | 0 | 0 | 272 | 0 | 0
8378 | 291.2 | 0 | 0 | 0 | 0 | 0 | 0 | 291.2 | 0 | 0
8379 | 199.2 | 0 | 0 | 0 | 0 | 0 | 0 | 199.2 | 0 | 0
8380 | 207.2 | 0 | 0 | 0 | 0 | 0 | 0 | 207.2 | 0 | 0
8381 | 285.6 | 0 | 0 | 0 | 0 | 0 | 0 | 285.6 | 0 | 0
8382 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 264 | 0 | 0
8383 | 318.4 | 52.93 | 172.4582 | 172.4582 | 0 | 0 | 0 | 0 | 0 | 158.2972
8384 | 138.494 | 323.49 | 1447.4394 | 143.8682 | -614.9724 | 0 | 688.5987 | 0 | 0 | 0
8385 | 740.535 | 559.43 | 2545.0779 | 769.2713 | -423.0387 | 0 | 1352.7679 | 0 | 0 | 0
8386 | 1328.616 | 648.88 | 2854.0901 | 1380.1726 | 0 | 0 | 1473.9175 | 0 | 0 | 0
8387 | 1321.969 | 852.48 | 3644.8573 | 1373.2677 | 0 | 0 | 2271.5897 | 0 | 0 | 0
8388 | 1360.73 | 842.42 | 3585.1198 | 1413.5328 | 0 | 0 | 2171.587 | 0 | 0 | 0
8389 | 1345.146 | 660.2 | 2862.0982 | 1397.3441 | 0 | 0 | 1464.7542 | 0 | 0 | 0
8390 | 1049.667 | 540.38 | 2368.2494 | 1090.3991 | 0 | 0 | 1277.8503 | 0 | 0 | 0
8391 | 978.516 | 479.21 | 2141.6425 | 1016.4871 | 0 | 0 | 1125.1554 | 0 | 0 | 0
8392 | 1113.713 | 151.87 | 663.4503 | 663.4503 | 0 | 0 | 0 | 475.046 | 0 | 0
8393 | 1271.929 | 33.31 | 119.9653 | 119.9653 | 0 | 0 | 0 | 1156.445 | 0 | 0
8394 | 1081.973 | 1.96 | 0 | 0 | 0 | 0 | 0 | 1081.973 | 0 | 0
8395 | 1176.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1176.8 | 0 | 0
8396 | 942.4 | 0 | 0 | 0 | 0 | 0 | 0 | 942.4 | 0 | 0
8397 | 892.8 | 0 | 0 | 0 | 0 | 0 | 0 | 892.8 | 0 | 0
8398 | 998.4 | 0 | 0 | 0 | 0 | 0 | 0 | 692.526 | 0 | 317.7434
8399 | 1292 | 0 | 0 | 0 | 0 | 0 | 0 | 700 | 0 | 614.9724
8400 | 1080.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1080.8 | 0 | 0
8401 | 1272.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1272.8 | 0 | 0
8402 | 1246.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1246.4 | 0 | 0
8403 | 1290.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1290.4 | 0 | 0
8404 | 856 | 0 | 0 | 0 | 0 | 0 | 0 | 856 | 0 | 0
8405 | 1009.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1009.6 | 0 | 0
8406 | 1304.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1304.8 | 0 | 0
8407 | 1032.8 | 61.69 | 197.0072 | 197.0072 | 0 | 0 | 0 | 843.152 | 0 | 0
8408 | 1361.032 | 275.11 | 1238.865 | 1238.865 | 0 | 0 | 0 | 168.445 | 0 | 0
8409 | 1132.013 | 420.5 | 1921.2694 | 1175.9405 | -614.9724 | 0 | 130.3565 | 0 | 0 | 0
8410 | 1598.971 | 593.45 | 2646.0715 | 1661.0187 | -423.0387 | 0 | 562.0141 | 0 | 0 | 0
8411 | 1537.183 | 859.91 | 3753.3906 | 1596.833 | 0 | 0 | 2156.5576 | 0 | 0 | 0
8412 | 1425.846 | 940.51 | 4067.011 | 1481.1756 | 0 | 0 | 2585.8354 | 0 | 0 | 0
8413 | 1392.659 | 892.95 | 3866.7325 | 1446.7008 | 0 | 0 | 2420.0317 | 0 | 0 | 0
8414 | 1295.781 | 487.18 | 2165.9962 | 1346.0635 | 0 | 0 | 819.9327 | 0 | 0 | 0
8415 | 1618.778 | 555.6 | 2473.0929 | 1681.5943 | 0 | 0 | 791.4986 | 0 | 0 | 0
8416 | 1607.397 | 350.06 | 1585.5256 | 1585.5256 | 0 | 0 | 0 | 81.099 | 0 | 0
8417 | 1627.259 | 46.07 | 177.6917 | 177.6917 | 0 | 0 | 0 | 1456.205 | 0 | 0
8418 | 1365.124 | 2.94 | 0 | 0 | 0 | 0 | 0 | 1365.124 | 0 | 0
8419 | 1428 | 0 | 0 | 0 | 0 | 0 | 0 | 1428 | 0 | 0
8420 | 1173.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1173.6 | 0 | 0
8421 | 1508 | 0 | 0 | 0 | 0 | 0 | 0 | 1508 | 0 | 0
8422 | 1451.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1145.326 | 0 | 317.7434
8423 | 1724 | 0 | 0 | 0 | 0 | 0 | 0 | 1132 | 0 | 614.9724
8424 | 1598.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1598.4 | 0 | 0
8425 | 1463.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1463.2 | 0 | 0
8426 | 1581.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1581.6 | 0 | 0
8427 | 1542.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1542.4 | 0 | 0
8428 | 1321.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1321.6 | 0 | 0
8429 | 1266.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1266.4 | 0 | 0
8430 | 1100 | 0 | 0 | 0 | 0 | 0 | 0 | 1100 | 0 | 0
8431 | 1120 | 66.76 | 212.4782 | 212.4782 | 0 | 0 | 0 | 915.459 | 0 | 0
8432 | 977.25 | 253.67 | 1149.1965 | 1015.1719 | -134.0245 | 0 | 0 | 0 | 0 | 0
8433 | 1164.458 | 446.58 | 2050.4312 | 1209.6445 | -614.9724 | 0 | 225.8143 | 0 | 0 | 0
8434 | 1811.107 | 594.87 | 2651.9563 | 1881.3866 | -289.0142 | 0 | 481.5556 | 0 | 0 | 0
8435 | 1589.091 | 731.6 | 3189.462 | 1650.7553 | 0 | 0 | 1538.7067 | 0 | 0 | 0
8436 | 1463.659 | 720.34 | 3123.7337 | 1520.4559 | 0 | 0 | 1603.2777 | 0 | 0 | 0
8437 | 1438.004 | 638.71 | 2777.6756 | 1493.8054 | 0 | 0 | 1283.8702 | 0 | 0 | 0
8438 | 1439.024 | 509.14 | 2236.8281 | 1494.865 | 0 | 0 | 741.9632 | 0 | 0 | 0
8439 | 1791.185 | 237.81 | 1044.9856 | 1044.9856 | 0 | 0 | 0 | 785.235 | 0 | 0
8440 | 1612.223 | 143.15 | 622.7385 | 622.7385 | 0 | 0 | 0 | 1012.747 | 0 | 0
8441 | 1277.059 | 24.49 | 80.5957 | 80.5957 | 0 | 0 | 0 | 1199.474 | 0 | 0
8442 | 1399.92 | 1.96 | 0 | 0 | 0 | 0 | 0 | 1399.92 | 0 | 0
8443 | 1373.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1373.6 | 0 | 0
8444 | 1170.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1170.4 | 0 | 0
8445 | 1194.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1194.4 | 0 | 0
8446 | 1397.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1091.726 | 0 | 317.7434
8447 | 1476 | 0 | 0 | 0 | 0 | 0 | 0 | 884 | 0 | 614.9724
8448 | 1419.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1419.2 | 0 | 0
8449 | 1497.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1497.6 | 0 | 0
8450 | 1310.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1310.4 | 0 | 0
8451 | 1341.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1341.6 | 0 | 0
8452 | 1416 | 0 | 0 | 0 | 0 | 0 | 0 | 1416 | 0 | 0
8453 | 957.6 | 0 | 0 | 0 | 0 | 0 | 0 | 957.6 | 0 | 0
8454 | 1168 | 0 | 0 | 0 | 0 | 0 | 0 | 1168 | 0 | 0
8455 | 1116.8 | 70.85 | 227.1565 | 227.1565 | 0 | 0 | 0 | 898.129 | 0 | 0
8456 | 1100.114 | 267.27 | 1209.4658 | 1142.8036 | -66.6622 | 0 | 0 | 0 | 0 | 0
8457 | 1505.134 | 451.1 | 2075.0925 | 1563.5403 | -511.5521 | 0 | 0 | 0 | 0 | 0
8458 | 1372.623 | 595.54 | 2663.6595 | 1425.8873 | -459.7968 | 0 | 777.9754 | 0 | 0 | 0
8459 | 1730.814 | 676.3 | 2964.5576 | 1797.9778 | 0 | 0 | 1166.5798 | 0 | 0 | 0
8460 | 1451.75 | 672.88 | 2930.3217 | 1508.0848 | 0 | 0 | 1422.2369 | 0 | 0 | 0
8461 | 1419.609 | 485.51 | 2127.9759 | 1474.6966 | 0 | 0 | 653.2794 | 0 | 0 | 0
8462 | 1566.858 | 594.47 | 2602.9642 | 1627.6595 | 0 | 0 | 975.3047 | 0 | 0 | 0
8463 | 1497.729 | 440.64 | 1959.7696 | 1555.848 | 0 | 0 | 403.9216 | 0 | 0 | 0
8464 | 1156.838 | 303.14 | 1369.7648 | 1201.7288 | 0 | 0 | 168.036 | 0 | 0 | 0
8465 | 1305.359 | 102.76 | 436.0217 | 436.0217 | 0 | 0 | 0 | 885.625 | 0 | 0
8466 | 1419.829 | 4.89 | 0 | 0 | 0 | 0 | 0 | 1419.829 | 0 | 0
8467 | 1196 | 0 | 0 | 0 | 0 | 0 | 0 | 1196 | 0 | 0
8468 | 1183.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1183.2 | 0 | 0
8469 | 1408.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1408.8 | 0 | 0
8470 | 1412 | 0 | 0 | 0 | 0 | 0 | 0 | 1106.126 | 0 | 317.7434
8471 | 1347.2 | 0 | 0 | 0 | 0 | 0 | 0 | 755.2 | 0 | 614.9724
8472 | 1276 | 0 | 0 | 0 | 0 | 0 | 0 | 1276 | 0 | 0
8473 | 1184 | 0 | 0 | 0 | 0 | 0 | 0 | 1184 | 0 | 0
8474 | 1453.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1453.6 | 0 | 0
8475 | 1312.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1312.8 | 0 | 0
8476 | 1127.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1127.2 | 0 | 0
8477 | 1457.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1457.6 | 0 | 0
8478 | 1394.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1394.4 | 0 | 0
8479 | 1288.8 | 23.71 | 68.5258 | 68.5258 | 0 | 0 | 0 | 1222.834 | 0 | 0
8480 | 1161.104 | 129.81 | 582.0859 | 582.0859 | 0 | 0 | 0 | 600.762 | 0 | 0
8481 | 829.113 | 369.2 | 1714.433 | 861.2865 | -614.9724 | 0 | 238.174 | 0 | 0 | 0
8482 | 1028.635 | 464.6 | 2116.4546 | 1068.5509 | -423.0387 | 0 | 624.8649 | 0 | 0 | 0
8483 | 1605.522 | 693.3 | 3118.2394 | 1667.8239 | 0 | 0 | 1450.4155 | 0 | 0 | 0
8484 | 1388.834 | 730.33 | 3265.8286 | 1442.7274 | 0 | 0 | 1823.1013 | 0 | 0 | 0
8485 | 1422.415 | 605.67 | 2718.3349 | 1477.6115 | 0 | 0 | 1240.7235 | 0 | 0 | 0
8486 | 1624.992 | 608.7 | 2754.4573 | 1688.0494 | 0 | 0 | 1066.4079 | 0 | 0 | 0
8487 | 1558.054 | 391.85 | 1791.5216 | 1618.5139 | 0 | 0 | 173.0077 | 0 | 0 | 0
8488 | 1796.174 | 67.67 | 280.3298 | 280.3298 | 0 | 0 | 0 | 1526.316 | 0 | 0
8489 | 1733.951 | 53.03 | 214.1049 | 214.1049 | 0 | 0 | 0 | 1527.844 | 0 | 0
8490 | 1379.821 | 2.94 | 0 | 0 | 0 | 0 | 0 | 1379.821 | 0 | 0
8491 | 1425.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1425.6 | 0 | 0
8492 | 1449.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1449.6 | 0 | 0
8493 | 1551.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1551.2 | 0 | 0
8494 | 1432.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1126.926 | 0 | 317.7434
8495 | 1576.8 | 0 | 0 | 0 | 0 | 0 | 0 | 984.8 | 0 | 614.9724
8496 | 1746.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1746.4 | 0 | 0
8497 | 704 | 0 | 0 | 0 | 0 | 0 | 0 | 704 | 0 | 0
8498 | 883.2 | 0 | 0 | 0 | 0 | 0 | 0 | 883.2 | 0 | 0
8499 | 1075.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1075.2 | 0 | 0
8500 | 876.8 | 0 | 0 | 0 | 0 | 0 | 0 | 876.8 | 0 | 0
8501 | 927.2 | 0 | 0 | 0 | 0 | 0 | 0 | 927.2 | 0 | 0
8502 | 720.8 | 0 | 0 | 0 | 0 | 0 | 0 | 720.8 | 0 | 0
8503 | 638.4 | 49.89 | 157.5368 | 157.5368 | 0 | 0 | 0 | 486.748 | 0 | 0
8504 | 622.722 | 247.18 | 1138.4864 | 646.8866 | -491.5998 | 0 | 0 | 0 | 0 | 0
8505 | 603.316 | 547.64 | 2598.8184 | 626.7275 | -546.4113 | 0 | 1425.6795 | 0 | 0 | 0
8506 | 1098.458 | 740.78 | 3416.7015 | 1141.0834 | 0 | 0 | 2275.6181 | 0 | 0 | 0
8507 | 979.053 | 763.01 | 3443.2316 | 1017.0449 | 0 | 0 | 2426.1867 | 0 | 0 | 0
8508 | 716.923 | 797.18 | 3554.527 | 744.743 | 0 | 0 | 2809.784 | 0 | 0 | 0
8509 | 680.172 | 770.89 | 3430.7763 | 706.5659 | 0 | 0 | 2724.2104 | 0 | 0 | 0
8510 | 780.334 | 676.96 | 3037.8505 | 810.6147 | 0 | 0 | 2227.2358 | 0 | 0 | 0
8511 | 882.579 | 501.56 | 2281.7045 | 916.8273 | 0 | 0 | 1364.8772 | 0 | 0 | 0
8512 | 842.753 | 451.72 | 2104.071 | 875.4558 | 0 | 0 | 1228.6152 | 0 | 0 | 0
8513 | 490.41 | 208.07 | 898.1475 | 509.4402 | 0 | 0 | 388.7072 | 0 | 0 | 0
8514 | 678.563 | 8.66 | 0 | 0 | 0 | 0 | 0 | 678.563 | 0 | 0
8515 | 853.6 | 0 | 0 | 0 | 0 | 0 | 0 | 853.6 | 0 | 0
8516 | 705.6 | 0 | 0 | 0 | 0 | 0 | 0 | 705.6 | 0 | 0
8517 | 828.8 | 0 | 0 | 0 | 0 | 0 | 0 | 828.8 | 0 | 0
8518 | 820 | 0 | 0 | 0 | 0 | 0 | 0 | 820 | 0 | 0
8519 | 755.2 | 0 | 0 | 0 | 0 | 0 | 0 | 755.2 | 0 | 0
8520 | 697.6 | 0 | 0 | 0 | 0 | 0 | 0 | 391.726 | 0 | 317.7434
8521 | 1381.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1381.6 | 0 | 0
8522 | 1472 | 0 | 0 | 0 | 0 | 0 | 0 | 1472 | 0 | 0
8523 | 1526.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1526.4 | 0 | 0
8524 | 1505.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1505.6 | 0 | 0
8525 | 1336.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1336.8 | 0 | 0
8526 | 1504 | 0 | 0 | 0 | 0 | 0 | 0 | 1504 | 0 | 0
8527 | 1156.8 | 16.65 | 38.9967 | 38.9967 | 0 | 0 | 0 | 527.26 | 0 | 614.9724
8528 | 151.282 | 92.09 | 408.5868 | 157.1525 | -251.4344 | 0 | 0 | 0 | 0 | 0
8529 | 203.767 | 276.79 | 1301.0739 | 211.6741 | -614.9724 | 0 | 474.4273 | 0 | 0 | 0
8530 | 271.406 | 441.18 | 2061.4021 | 281.9378 | -171.6054 | 0 | 1607.8589 | 0 | 0 | 0
8531 | 225.678 | 633.7 | 2923.7399 | 234.4354 | 0 | 0 | 2689.3045 | 0 | 0 | 0
8532 | 210.894 | 642.07 | 2932.764 | 219.0777 | 0 | 0 | 2713.6863 | 0 | 0 | 0
8533 | 235.761 | 515.84 | 2347.5325 | 244.9096 | 0 | 0 | 2102.6229 | 0 | 0 | 0
8534 | 236.032 | 340.14 | 1541.3774 | 245.1912 | 0 | 0 | 1296.1863 | 0 | 0 | 0
8535 | 258.885 | 255 | 1153.0826 | 268.931 | 0 | 0 | 884.1517 | 0 | 0 | 0
8536 | 263.906 | 127.75 | 563.9349 | 274.1468 | 0 | 0 | 289.7881 | 0 | 0 | 0
8537 | 505.286 | 60.13 | 247.6365 | 247.6365 | 0 | 0 | 0 | 266.9 | 0 | 0
8538 | 457.786 | 4.89 | 0 | 0 | 0 | 0 | 0 | 457.786 | 0 | 0
8539 | 296 | 0 | 0 | 0 | 0 | 0 | 0 | 296 | 0 | 0
8540 | 264.8 | 0 | 0 | 0 | 0 | 0 | 0 | 126.126 | 0 | 144.0552
8541 | 239.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 248.4821
8542 | 282.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 293.3585
8543 | 237.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 246.82
8544 | 223.2 | 0 | 0 | 0 | 0 | 0 | 0 | 223.2 | 0 | 0
8545 | 259.2 | 0 | 0 | 0 | 0 | 0 | 0 | 259.2 | 0 | 0
8546 | 218.4 | 0 | 0 | 0 | 0 | 0 | 0 | 218.4 | 0 | 0
8547 | 200 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 0 | 0
8548 | 210.4 | 0 | 0 | 0 | 0 | 0 | 0 | 210.4 | 0 | 0
8549 | 123.2 | 0 | 0 | 0 | 0 | 0 | 0 | 123.2 | 0 | 0
8550 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 180 | 0 | 0
8551 | 153.6 | 27.04 | 78.7393 | 78.7393 | 0 | 0 | 0 | 77.802 | 0 | 0
8552 | 243.992 | 184.91 | 846.3766 | 253.46 | -592.9165 | 0 | 0 | 0 | 0 | 0
8553 | 437.884 | 326.66 | 1535.1322 | 454.8749 | -445.0956 | 0 | 635.1616 | 0 | 0 | 0
8554 | 969.506 | 436.8 | 2024.9359 | 1007.1274 | 0 | 0 | 1017.8084 | 0 | 0 | 0
8555 | 1470.638 | 524.69 | 2402.5507 | 1527.7057 | 0 | 0 | 874.845 | 0 | 0 | 0
8556 | 1520.337 | 639.45 | 2895.1873 | 1579.3333 | 0 | 0 | 1315.854 | 0 | 0 | 0
8557 | 1436.091 | 646.24 | 2911.9349 | 1491.8181 | 0 | 0 | 1420.1167 | 0 | 0 | 0
8558 | 1653.246 | 503.83 | 2277.9191 | 1717.3998 | 0 | 0 | 560.5193 | 0 | 0 | 0
8559 | 1597.991 | 424.73 | 1938.2954 | 1660.0006 | 0 | 0 | 278.2948 | 0 | 0 | 0
8560 | 1630.98 | 73.56 | 307.8124 | 307.8124 | 0 | 0 | 0 | 1334.666 | 0 | 0
8561 | 1716.665 | 137.19 | 596.598 | 596.598 | 0 | 0 | 0 | 1142.353 | 0 | 0
8562 | 1572.735 | 9.08 | 0 | 0 | 0 | 0 | 0 | 1572.735 | 0 | 0
8563 | 1589.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1589.6 | 0 | 0
8564 | 1557.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1557.6 | 0 | 0
8565 | 1602.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1602.4 | 0 | 0
8566 | 1444 | 0 | 0 | 0 | 0 | 0 | 0 | 1138.126 | 0 | 317.7434
8567 | 1375.2 | 0 | 0 | 0 | 0 | 0 | 0 | 783.2 | 0 | 614.9724
8568 | 1093.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1093.6 | 0 | 0
8569 | 1228 | 0 | 0 | 0 | 0 | 0 | 0 | 1228 | 0 | 0
8570 | 1288 | 0 | 0 | 0 | 0 | 0 | 0 | 1288 | 0 | 0
8571 | 1141.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1141.6 | 0 | 0
8572 | 1294.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1294.4 | 0 | 0
8573 | 1065.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1065.6 | 0 | 0
8574 | 829.6 | 0 | 0 | 0 | 0 | 0 | 0 | 829.6 | 0 | 0
8575 | 1029.6 | 74.81 | 214.8435 | 214.8435 | 0 | 0 | 0 | 822.782 | 0 | 0
8576 | 822.307 | 308.38 | 1382.4746 | 854.2164 | -528.2582 | 0 | 0 | 0 | 0 | 0
8577 | 592.193 | 545.42 | 2531.8954 | 615.1729 | -509.7529 | 0 | 1406.9696 | 0 | 0 | 0
8578 | 240.544 | 733.07 | 3316.701 | 249.8782 | 0 | 0 | 3066.8227 | 0 | 0 | 0
8579 | 160.732 | 636.27 | 2862.0982 | 166.9692 | 0 | 0 | 2695.1291 | 0 | 0 | 0
8580 | 234.455 | 607.99 | 2722.2678 | 243.553 | 0 | 0 | 2478.7149 | 0 | 0 | 0
8581 | 799.112 | 800.44 | 3543.7868 | 830.1213 | 0 | 0 | 2713.6655 | 0 | 0 | 0
8582 | 1280.093 | 635.65 | 2857.7217 | 1329.7667 | 0 | 0 | 1527.9551 | 0 | 0 | 0
8583 | 1234.242 | 429.79 | 1961.9459 | 1282.1365 | 0 | 0 | 679.8094 | 0 | 0 | 0
8584 | 1396.75 | 206.02 | 935.2048 | 935.2048 | 0 | 0 | 0 | 496.48 | 0 | 0
8585 | 1167.432 | 109.53 | 461.463 | 461.463 | 0 | 0 | 0 | 723.207 | 0 | 0
8586 | 1508.661 | 12.86 | 5.033 | 5.033 | 0 | 0 | 0 | 1503.816 | 0 | 0
8587 | 1127.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1127.2 | 0 | 0
8588 | 1019.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1019.2 | 0 | 0
8589 | 1018.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1018.4 | 0 | 0
8590 | 1072 | 0 | 0 | 0 | 0 | 0 | 0 | 766.126 | 0 | 317.7434
8591 | 1246.4 | 0 | 0 | 0 | 0 | 0 | 0 | 654.4 | 0 | 614.9724
8592 | 1248 | 0 | 0 | 0 | 0 | 0 | 0 | 1248 | 0 | 0
8593 | 1350.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1350.4 | 0 | 0
8594 | 1180.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1180.8 | 0 | 0
8595 | 1263.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1263.2 | 0 | 0
8596 | 924 | 0 | 0 | 0 | 0 | 0 | 0 | 924 | 0 | 0
8597 | 1158.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1158.4 | 0 | 0
8598 | 944.8 | 0 | 0 | 0 | 0 | 0 | 0 | 944.8 | 0 | 0
8599 | 1162.4 | 66.24 | 190.8918 | 190.8918 | 0 | 0 | 0 | 978.639 | 0 | 0
8600 | 1102.325 | 281.69 | 1261.3146 | 1145.1004 | -116.2142 | 0 | 0 | 0 | 0 | 0
8601 | 1299.188 | 407.08 | 1874.9927 | 1349.6027 | -525.39 | 0 | 0 | 0 | 0 | 0
8602 | 1255.151 | 603.92 | 2723.0895 | 1303.8568 | -396.4079 | 0 | 1022.8248 | 0 | 0 | 0
8603 | 1741.645 | 624.67 | 2773.8788 | 1809.2291 | 0 | 0 | 964.6497 | 0 | 0 | 0
8604 | 1714.976 | 729.44 | 3201.2368 | 1781.5252 | 0 | 0 | 1419.7116 | 0 | 0 | 0
8605 | 1914.011 | 932.68 | 4068.2939 | 1988.2837 | 0 | 0 | 2080.0102 | 0 | 0 | 0
8606 | 1870.71 | 637.72 | 2820.8421 | 1943.3024 | 0 | 0 | 877.5397 | 0 | 0 | 0
8607 | 1783.81 | 436.5 | 1955.6715 | 1853.0303 | 0 | 0 | 102.6412 | 0 | 0 | 0
8608 | 2019.637 | 332.48 | 1511.9086 | 1511.9086 | 0 | 0 | 0 | 564.206 | 0 | 0
8609 | 1410.31 | 67.73 | 277.3609 | 277.3609 | 0 | 0 | 0 | 1143.31 | 0 | 0
8610 | 1651.085 | 5.87 | 0 | 0 | 0 | 0 | 0 | 1651.085 | 0 | 0
8611 | 1632 | 0 | 0 | 0 | 0 | 0 | 0 | 1632 | 0 | 0
8612 | 1364.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1364.8 | 0 | 0
8613 | 1691.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1691.2 | 0 | 0
8614 | 1349.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1043.726 | 0 | 317.7434
8615 | 1433.6 | 0 | 0 | 0 | 0 | 0 | 0 | 841.6 | 0 | 614.9724
8616 | 1556 | 0 | 0 | 0 | 0 | 0 | 0 | 1556 | 0 | 0
8617 | 1457.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1457.6 | 0 | 0
8618 | 1494.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1494.4 | 0 | 0
8619 | 1759.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1759.2 | 0 | 0
8620 | 1729.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1729.6 | 0 | 0
8621 | 1414.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1414.4 | 0 | 0
8622 | 1408.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1408.8 | 0 | 0
8623 | 1471.2 | 56.27 | 161.1093 | 161.1093 | 0 | 0 | 0 | 1316.109 | 0 | 0
8624 | 1645.752 | 247.81 | 1105.3682 | 1105.3682 | 0 | 0 | 0 | 581.675 | 0 | 0
8625 | 1196.191 | 461.73 | 2119.0568 | 1242.6089 | -614.9724 | 0 | 261.4755 | 0 | 0 | 0
8626 | 1139.333 | 582.02 | 2603.9282 | 1183.5445 | -423.0387 | 0 | 997.345 | 0 | 0 | 0
8627 | 1201.095 | 702.42 | 3069.0053 | 1247.7032 | 0 | 0 | 1821.3021 | 0 | 0 | 0
8628 | 1464.687 | 776.49 | 3343.5032 | 1521.5238 | 0 | 0 | 1821.9794 | 0 | 0 | 0
8629 | 1491.287 | 528.51 | 2290.7463 | 1549.156 | 0 | 0 | 741.5902 | 0 | 0 | 0
8630 | 1221.935 | 643.19 | 2762.1631 | 1269.3519 | 0 | 0 | 1492.8112 | 0 | 0 | 0
8631 | 1440.758 | 328.34 | 1442.9808 | 1442.9808 | 0 | 0 | 0 | 0 | 0 | 53.6854
8632 | 1143.128 | 397.39 | 1783.4553 | 1187.4858 | -59.7469 | 0 | 536.2227 | 0 | 0 | 0
8633 | 1279.819 | 160.67 | 687.7926 | 687.7926 | 0 | 0 | 0 | 617.719 | 0 | 0
8634 | 1197.79 | 12.35 | 6.1861 | 6.1861 | 0 | 0 | 0 | 1191.835 | 0 | 0
8635 | 973.6 | 0 | 0 | 0 | 0 | 0 | 0 | 973.6 | 0 | 0
8636 | 1392 | 0 | 0 | 0 | 0 | 0 | 0 | 1392 | 0 | 0
8637 | 827.2 | 0 | 0 | 0 | 0 | 0 | 0 | 827.2 | 0 | 0
8638 | 1307.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1001.326 | 0 | 317.7434
8639 | 978.4 | 0 | 0 | 0 | 0 | 0 | 0 | 386.4 | 0 | 614.9724
8640 | 1164.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1164.8 | 0 | 0
8641 | 1192 | 0 | 0 | 0 | 0 | 0 | 0 | 1192 | 0 | 0
8642 | 1257.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1257.6 | 0 | 0
8643 | 1376.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1376.8 | 0 | 0
8644 | 1199.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1199.2 | 0 | 0
8645 | 1092.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1092.8 | 0 | 0
8646 | 1172.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1172.8 | 0 | 0
8647 | 1270.4 | 54.68 | 159.0566 | 159.0566 | 0 | 0 | 0 | 1117.285 | 0 | 0
8648 | 1082.229 | 284.49 | 1253.5548 | 1124.2246 | -129.3302 | 0 | 0 | 0 | 0 | 0
8649 | 1267.43 | 526.46 | 2371.3305 | 1316.6123 | -614.9724 | 0 | 439.7458 | 0 | 0 | 0
8650 | 1460.39 | 723.24 | 3137.6017 | 1517.0601 | -293.7085 | 0 | 1326.8331 | 0 | 0 | 0
8651 | 1254.555 | 746.92 | 3174.1739 | 1303.2377 | 0 | 0 | 1870.9362 | 0 | 0 | 0
8652 | 1447.708 | 913.06 | 3771.0503 | 1503.8859 | 0 | 0 | 2267.1644 | 0 | 0 | 0
8653 | 1292.068 | 714.55 | 3006.1576 | 1342.2064 | 0 | 0 | 1663.9512 | 0 | 0 | 0
8654 | 1332.407 | 650.88 | 2765.3211 | 1384.1107 | 0 | 0 | 1381.2104 | 0 | 0 | 0
8655 | 1699.676 | 502.92 | 2188.665 | 1765.6315 | 0 | 0 | 423.0335 | 0 | 0 | 0
8656 | 1738.895 | 387.32 | 1727.0472 | 1727.0472 | 0 | 0 | 0 | 76.362 | 0 | 0
8657 | 1656.8 | 159.55 | 681.7364 | 681.7364 | 0 | 0 | 0 | 1000.53 | 0 | 0
8658 | 1844.457 | 14.14 | 10.7277 | 10.7277 | 0 | 0 | 0 | 1834.13 | 0 | 0
8659 | 1589.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1589.6 | 0 | 0
8660 | 1539.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1539.2 | 0 | 0
8661 | 1721.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1721.6 | 0 | 0
8662 | 1580 | 0 | 0 | 0 | 0 | 0 | 0 | 1274.126 | 0 | 317.7434
8663 | 1633.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1041.6 | 0 | 614.9724
8664 | 1402.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1402.4 | 0 | 0
8665 | 1166.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1166.4 | 0 | 0
8666 | 950.4 | 0 | 0 | 0 | 0 | 0 | 0 | 950.4 | 0 | 0
8667 | 1228.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1228.8 | 0 | 0
8668 | 1433.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1433.6 | 0 | 0
8669 | 1112.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1112.8 | 0 | 0
8670 | 1390.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1390.4 | 0 | 0
8671 | 1300 | 46.7 | 132.539 | 132.539 | 0 | 0 | 0 | 1172.412 | 0 | 0
8672 | 1239.89 | 230.23 | 1022.2057 | 1022.2057 | 0 | 0 | 0 | 255.869 | 0 | 0
8673 | 1372.872 | 450.55 | 2042.7431 | 1426.146 | -614.9724 | 0 | 1.6247 | 0 | 0 | 0
8674 | 1438.053 | 726.67 | 3169.5969 | 1493.8573 | -423.0387 | 0 | 1252.7009 | 0 | 0 | 0
8675 | 1474.877 | 768.95 | 3292.5955 | 1532.1092 | 0 | 0 | 1760.4863 | 0 | 0 | 0
8676 | 1655.249 | 806.67 | 3419.7058 | 1719.4805 | 0 | 0 | 1700.2252 | 0 | 0 | 0
8677 | 1465.832 | 918.93 | 3870.7184 | 1522.7132 | 0 | 0 | 2348.0052 | 0 | 0 | 0
8678 | 1372.877 | 845.68 | 3612.3064 | 1426.1511 | 0 | 0 | 2186.1552 | 0 | 0 | 0
8679 | 1501.38 | 595.16 | 2626.4069 | 1559.6407 | 0 | 0 | 1066.7663 | 0 | 0 | 0
8680 | 1727.807 | 326.7 | 1470.2681 | 1470.2681 | 0 | 0 | 0 | 312.461 | 0 | 0
8681 | 1880.42 | 196.69 | 844.1109 | 844.1109 | 0 | 0 | 0 | 1067.841 | 0 | 0
8682 | 1581.08 | 15.03 | 13.5959 | 13.5959 | 0 | 0 | 0 | 1567.992 | 0 | 0
8683 | 1718.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1718.4 | 0 | 0
8684 | 1398.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1398.4 | 0 | 0
8685 | 1615.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1615.2 | 0 | 0
8686 | 1388 | 0 | 0 | 0 | 0 | 0 | 0 | 1388 | 0 | 0
8687 | 1260 | 0 | 0 | 0 | 0 | 0 | 0 | 1260 | 0 | 0
8688 | 1138.4 | 0 | 0 | 0 | 0 | 0 | 0 | 856.244 | 0 | 293.105
8689 | 1516 | 0 | 0 | 0 | 0 | 0 | 0 | 1516 | 0 | 0
8690 | 1427.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1427.2 | 0 | 0
8691 | 1350.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1350.4 | 0 | 0
8692 | 1424.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1424.8 | 0 | 0
8693 | 1365.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1365.6 | 0 | 0
8694 | 1286.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1286.4 | 0 | 0
8695 | 1076.8 | 34.35 | 91.8501 | 91.8501 | 0 | 0 | 0 | 396.381 | 0 | 614.9724
8696 | 900.697 | 205.48 | 911.0099 | 911.0099 | 0 | 0 | 0 | 0 | 0 | 24.6384
8697 | 1097.2 | 432.49 | 1969.5925 | 1139.7766 | -614.9724 | 0 | 214.8435 | 0 | 0 | 0
8698 | 1366.655 | 723.64 | 3207.8426 | 1419.6877 | -423.0387 | 0 | 1365.1162 | 0 | 0 | 0
8699 | 1227.291 | 778.47 | 3401.3958 | 1274.9157 | 0 | 0 | 2126.4801 | 0 | 0 | 0
8700 | 1383.572 | 926.88 | 3985.2082 | 1437.2612 | 0 | 0 | 2547.947 | 0 | 0 | 0
8701 | 1468.257 | 763.02 | 3315.6954 | 1525.2323 | 0 | 0 | 1790.4631 | 0 | 0 | 0
8702 | 1027.48 | 624.11 | 2741.896 | 1067.3511 | 0 | 0 | 1674.5449 | 0 | 0 | 0
8703 | 1438.064 | 297.18 | 1319.4607 | 1319.4607 | 0 | 0 | 0 | 0 | 0 | 174.407
8704 | 621.669 | 231.91 | 1037.1084 | 645.7917 | -194.0965 | 0 | 197.2202 | 0 | 0 | 0
8705 | 592.386 | 111.31 | 475.7165 | 475.7165 | 0 | 0 | 0 | 134.44 | 0 | 0
8706 | 255.342 | 7.83 | 0 | 0 | 0 | 0 | 0 | 255.342 | 0 | 0
8707 | 254.4 | 0 | 0 | 0 | 0 | 0 | 0 | 159.726 | 0 | 98.3478
8708 | 272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 282.5549
8709 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186.9849
8710 | 245.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 255.1304
8711 | 105.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109.6978
8712 | 99.2 | 0 | 0 | 0 | 0 | 0 | 0 | 99.2 | 0 | 0
8713 | 91.2 | 0 | 0 | 0 | 0 | 0 | 0 | 91.2 | 0 | 0
8714 | 98.4 | 0 | 0 | 0 | 0 | 0 | 0 | 98.4 | 0 | 0
8715 | 89.6 | 0 | 0 | 0 | 0 | 0 | 0 | 89.6 | 0 | 0
8716 | 95.2 | 0 | 0 | 0 | 0 | 0 | 0 | 95.2 | 0 | 0
8717 | 91.2 | 0 | 0 | 0 | 0 | 0 | 0 | 91.2 | 0 | 0
8718 | 96.8 | 0 | 0 | 0 | 0 | 0 | 0 | 96.8 | 0 | 0
8719 | 77.6 | 17.63 | 37.6546 | 37.6546 | 0 | 0 | 0 | 41.352 | 0 | 0
8720 | 94.05 | 173.11 | 773.3559 | 97.6996 | -614.9724 | 0 | 60.6839 | 0 | 0 | 0
8721 | 825.915 | 401.95 | 1857.2271 | 857.9655 | -423.0387 | 0 | 576.2229 | 0 | 0 | 0
8722 | 1285.579 | 455.66 | 2052.4424 | 1335.4656 | 0 | 0 | 716.9768 | 0 | 0 | 0
8723 | 1403.535 | 247.62 | 1090.0978 | 1090.0978 | 0 | 0 | 0 | 0 | 0 | 367.901
8724 | 1280.109 | 334.47 | 1474.2364 | 1329.7833 | -144.4531 | 0 | 0 | 0 | 0 | 0
8725 | 1122.521 | 491.87 | 2163.6901 | 1166.0801 | -264.9814 | 0 | 732.6285 | 0 | 0 | 0
8726 | 1380.964 | 307.57 | 1355.9446 | 1355.9446 | 0 | 0 | 0 | 75.671 | 0 | 0
8727 | 1395.618 | 297.17 | 1319.4254 | 1319.4254 | 0 | 0 | 0 | 125.48 | 0 | 0
8728 | 1382.822 | 125.62 | 544.6671 | 544.6671 | 0 | 0 | 0 | 858.501 | 0 | 0
8729 | 1035.196 | 61.03 | 248.6836 | 248.6836 | 0 | 0 | 0 | 795.802 | 0 | 0
8730 | 1041.064 | 6.85 | 0 | 0 | 0 | 0 | 0 | 1041.064 | 0 | 0
8731 | 1022.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1022.4 | 0 | 0
8732 | 1182.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1182.4 | 0 | 0
8733 | 1686.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1686.4 | 0 | 0
8734 | 897.6 | 0 | 0 | 0 | 0 | 0 | 0 | 591.726 | 0 | 317.7434
8735 | 1217.6 | 0 | 0 | 0 | 0 | 0 | 0 | 625.6 | 0 | 614.9724
8736 | 1290.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1290.4 | 0 | 0
8737 | 1120 | 0 | 0 | 0 | 0 | 0 | 0 | 1120 | 0 | 0
8738 | 1036.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1036.8 | 0 | 0
8739 | 1090.4 | 0 | 0 | 0 | 0 | 0 | 0 | 1090.4 | 0 | 0
8740 | 1088 | 0 | 0 | 0 | 0 | 0 | 0 | 1088 | 0 | 0
8741 | 1287.2 | 0 | 0 | 0 | 0 | 0 | 0 | 1287.2 | 0 | 0
8742 | 1304.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1304.8 | 0 | 0
8743 | 1274.4 | 31.55 | 78.9284 | 78.9284 | 0 | 0 | 0 | 1198.42 | 0 | 0
8744 | 1022.55 | 173.95 | 782.0673 | 782.0673 | 0 | 0 | 0 | 269.697 | 0 | 0
8745 | 1026.462 | 426.19 | 1986.873 | 1066.2936 | -614.9724 | 0 | 305.607 | 0 | 0 | 0
8746 | 1278.239 | 612.41 | 2790.6212 | 1327.8407 | -423.0387 | 0 | 1039.7418 | 0 | 0 | 0
8747 | 1288.464 | 578.91 | 2599.0022 | 1338.4625 | 0 | 0 | 1260.5397 | 0 | 0 | 0
8748 | 1351.624 | 594.51 | 2654.25 | 1404.0734 | 0 | 0 | 1250.1766 | 0 | 0 | 0
8749 | 1146.697 | 414.4 | 1855.4705 | 1191.1943 | 0 | 0 | 664.2762 | 0 | 0 | 0
8750 | 1487.273 | 393.74 | 1775.3173 | 1544.9863 | 0 | 0 | 230.3311 | 0 | 0 | 0
8751 | 1161.038 | 453.65 | 2076.5177 | 1206.0918 | 0 | 0 | 870.4259 | 0 | 0 | 0
8752 | 1604.111 | 362.16 | 1687.8022 | 1666.3581 | 0 | 0 | 21.444 | 0 | 0 | 0
8753 | 1704.867 | 64.06 | 267.6917 | 267.6917 | 0 | 0 | 0 | 1447.175 | 0 | 0
8754 | 1368.022 | 7.83 | 0 | 0 | 0 | 0 | 0 | 1368.022 | 0 | 0
8755 | 1372.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1372.8 | 0 | 0
8756 | 1204.8 | 0 | 0 | 0 | 0 | 0 | 0 | 1204.8 | 0 | 0
8757 | 1449.6 | 0 | 0 | 0 | 0 | 0 | 0 | 1449.6 | 0 | 0
8758 | 1340 | 0 | 0 | 0 | 0 | 0 | 0 | 1034.126 | 0 | 317.7434
8759 | 1208 | 0 | 0 | 0 | 0 | 0 | 0 | 616 | 0 | 614.9724
8760 | 1216 | 0 | 0 | 0 | 0 | 0 | 0 | 1216 | 0 | 0

## Load Duration
Rank | Load (kW) | Net Load (kW)
1 | 2428 | 2428
2 | 2418.5558 | 2418.556
3 | 2414.4 | 2414.4
4 | 2405.0087 | 2405.009
5 | 2390.381 | 2389.6
6 | 2389.6 | 2380.305
7 | 2387.844 | 2379.2
8 | 2381.0831 | 2369.946
9 | 2380.3051 | 2341.932
10 | 2379.2 | 2330.4
11 | 2378.556 | 2321.335
12 | 2369.9456 | 2227.969
13 | 2352 | 2208.8
14 | 2342.8514 | 2200.208
15 | 2335.268 | 2172.8
16 | 2330.4 | 2164.348
17 | 2326.1845 | 2156.812
18 | 2321.3354 | 2156.8
19 | 2297.304 | 2148.423
20 | 2295.2 | 2148.411
21 | 2288.3681 | 2129.6
22 | 2286.452 | 2121.316
23 | 2286.2723 | 2091.708
24 | 2279.797 | 2075.2
25 | 2277.5584 | 2067.128
26 | 2270.9292 | 2057.6
27 | 2261.298 | 2057.6
28 | 2256.255 | 2049.597
29 | 2252.5022 | 2041.861
30 | 2247.4788 | 2028.8
31 | 2215.2 | 2020.909
32 | 2208.8 | 2011.798
33 | 2206.5835 | 2004
34 | 2200.2084 | 2000
35 | 2188.553 | 1998.992
36 | 2181.431 | 1998.285
37 | 2180.0402 | 1998.01
38 | 2172.9459 | 1996.205
39 | 2172.8 | 1992.221
40 | 2168.745 | 1969.358
41 | 2164.3484 | 1956
42 | 2160.3092 | 1954.45
43 | 2156.812 | 1948.392
44 | 2156.8 | 1940.8
45 | 2148.4226 | 1932.118
46 | 2148.4107 | 1928.21
47 | 2138.256 | 1925.6
48 | 2137.608 | 1924
49 | 2133.191 | 1915.2
50 | 2129.6 | 1913.6
51 | 2121.3165 | 1911.297
52 | 2117.631 | 1909.326
53 | 2116.262 | 1900.71
54 | 2112.8 | 1896.8
55 | 2098.686 | 1894.924
56 | 2095.805 | 1894.377
57 | 2091.005 | 1889.669
58 | 2089.833 | 1889.422
59 | 2088.377 | 1888
60 | 2087.6529 | 1887.87
61 | 2076.6159 | 1884.852
62 | 2075.2 | 1880.8
63 | 2071.826 | 1880.656
64 | 2071.6969 | 1875.873
65 | 2067.1281 | 1866.297
66 | 2067.103 | 1863.839
67 | 2057.6 | 1859.99
68 | 2057.6 | 1858.436
69 | 2055.558 | 1857.119
70 | 2055.2559 | 1850.4
71 | 2055.2 | 1849.113
72 | 2055.08 | 1847.2
73 | 2051.354 | 1846.4
74 | 2049.5965 | 1845.6
75 | 2047.677 | 1843.247
76 | 2043.3748 | 1843.202
77 | 2041.861 | 1842.4
78 | 2040.8 | 1838.421
79 | 2035.7422 | 1836.8
80 | 2033.628 | 1835.234
81 | 2032.8619 | 1834.13
82 | 2028.8 | 1832.8
83 | 2027.2 | 1827.535
84 | 2026.099 | 1825.671
85 | 2025.649 | 1824.8
86 | 2020.9085 | 1823.205
87 | 2019.637 | 1820
88 | 2017.7698 | 1819.672
89 | 2013.4594 | 1817.683
90 | 2012.075 | 1812.776
91 | 2008.054 | 1812.497
92 | 2004 | 1812
93 | 2003.2 | 1808.8
94 | 2003.2 | 1806.926
95 | 2001.861 | 1806.403
96 | 2000 | 1805.698
97 | 1998.4 | 1805.209
98 | 1998.285 | 1804.952
99 | 1998.015 | 1803.183
100 | 1998.0095 | 1799.377
101 | 1996.523 | 1798.4
102 | 1996.205 | 1796.795
103 | 1995.8376 | 1793.95
104 | 1992.2206 | 1793.173
105 | 1991.36 | 1791.405
106 | 1988.333 | 1789.099
107 | 1976.8 | 1785.434
108 | 1975.004 | 1784.8
109 | 1973.613 | 1784.013
110 | 1972.895 | 1783.629
111 | 1972.144 | 1780
112 | 1969.563 | 1779.2
113 | 1969.1108 | 1778.59
114 | 1967.7386 | 1777.858
115 | 1965.9362 | 1777.6
116 | 1962.7917 | 1775.2
117 | 1959.966 | 1773.255
118 | 1956.792 | 1772.851
119 | 1956 | 1770.4
120 | 1955.911 | 1765.955
121 | 1954.45 | 1765.6
122 | 1953.371 | 1763.2
123 | 1953.342 | 1762.4
124 | 1952.3423 | 1761.6
125 | 1951.2 | 1760.002
126 | 1950.329 | 1760
127 | 1950.1673 | 1760
128 | 1950.1113 | 1759.2
129 | 1948.3917 | 1759.2
130 | 1948.007 | 1758.4
131 | 1945.9424 | 1756
132 | 1945.081 | 1755.881
133 | 1943.684 | 1755.545
134 | 1940.862 | 1754.748
135 | 1940.8 | 1753.156
136 | 1940.7916 | 1750.851
137 | 1940.668 | 1749.326
138 | 1937.529 | 1749.17
139 | 1936.4576 | 1748.8
140 | 1936.1236 | 1748
141 | 1935.979 | 1746.4
142 | 1933.3126 | 1745.6
143 | 1931.97 | 1745.249
144 | 1931.9585 | 1744
145 | 1931.914 | 1743.613
146 | 1931.871 | 1742.4
147 | 1931.0148 | 1741.978
148 | 1925.6 | 1741.725
149 | 1925.128 | 1741.499
150 | 1924.839 | 1741.232
151 | 1924 | 1740.8
152 | 1921.03 | 1738.4
153 | 1920 | 1737.6
154 | 1918.198 | 1736.8
155 | 1917.6398 | 1736.253
156 | 1916.994 | 1734.029
157 | 1916.271 | 1732.913
158 | 1916.0218 | 1732.8
159 | 1916 | 1732.345
160 | 1916 | 1730.86
161 | 1915.2 | 1730.074
162 | 1914.4 | 1729.658
163 | 1914.011 | 1729.6
164 | 1913.6 | 1728.579
165 | 1909.872 | 1726.439
166 | 1908.6882 | 1725.6
167 | 1907.596 | 1725.6
168 | 1906.9535 | 1723.985
169 | 1905.103 | 1723.168
170 | 1904.871 | 1721.6
171 | 1904.751 | 1718.888
172 | 1903.518 | 1718.4
173 | 1902.457 | 1718.4
174 | 1902.362 | 1717.6
175 | 1901.1918 | 1716.596
176 | 1900.996 | 1715.857
177 | 1900.383 | 1715.055
178 | 1900.048 | 1715.024
179 | 1899.5274 | 1714.703
180 | 1899.267 | 1712.774
181 | 1896.8 | 1711.2
182 | 1895.8186 | 1711.2
183 | 1895.057 | 1709.264
184 | 1894.9522 | 1708
185 | 1894.24 | 1707.2
186 | 1892.738 | 1706.4
187 | 1892.5228 | 1705.62
188 | 1891.8794 | 1705.6
189 | 1889.882 | 1705.486
190 | 1889.88 | 1704.8
191 | 1889.839 | 1704.544
192 | 1889.422 | 1704.336
193 | 1888 | 1704.071
194 | 1887.87 | 1704
195 | 1886.909 | 1703.54
196 | 1884.852 | 1703.2
197 | 1884.7238 | 1702.4
198 | 1884.636 | 1702.4
199 | 1882.658 | 1702.112
200 | 1880.8 | 1701.6
201 | 1880.6562 | 1701.356
202 | 1880.42 | 1701.086
203 | 1880.17 | 1700.8
204 | 1876.2766 | 1698.633
205 | 1876.2222 | 1698.4
206 | 1876.1804 | 1698.4
207 | 1874.444 | 1698.387
208 | 1873.143 | 1697.326
209 | 1870.71 | 1697.326
210 | 1870.3575 | 1696.179
211 | 1870.1756 | 1696
212 | 1870.081 | 1695.279
213 | 1870.011 | 1695.2
214 | 1869.6654 | 1694.447
215 | 1869.297 | 1694.272
216 | 1867.076 | 1693.027
217 | 1866.297 | 1692.171
218 | 1865.857 | 1691.516
219 | 1864.668 | 1691.2
220 | 1863.8394 | 1690.454
221 | 1863.569 | 1690.4
222 | 1862.9184 | 1689.671
223 | 1862.026 | 1688.8
224 | 1860.7669 | 1688.8
225 | 1860.7669 | 1688.754
226 | 1859.99 | 1688.399
227 | 1859.743 | 1688
228 | 1859.685 | 1687.2
229 | 1859.342 | 1686.4
230 | 1859.284 | 1686.4
231 | 1858.4361 | 1685.6
232 | 1857.995 | 1684.73
233 | 1857.415 | 1684.618
234 | 1857.159 | 1683.2
235 | 1857.119 | 1682.848
236 | 1854.487 | 1682.578
237 | 1853.049 | 1682.404
238 | 1852.086 | 1682.4
239 | 1851.263 | 1681.652
240 | 1851.2 | 1681.348
241 | 1851.164 | 1680.964
242 | 1850.4 | 1680.8
243 | 1849.9352 | 1680.637
244 | 1849.8422 | 1678.529
245 | 1849.735 | 1675.856
246 | 1849.6 | 1675.433
247 | 1849.1134 | 1673.812
248 | 1849.064 | 1672.005
249 | 1847.2 | 1668.8
250 | 1846.4 | 1666.4
251 | 1845.8412 | 1665.6
252 | 1845.6 | 1665.051
253 | 1845.2748 | 1664
254 | 1844.8819 | 1663.509
255 | 1844.457 | 1661.6
256 | 1843.247 | 1661.6
257 | 1843.2025 | 1660.8
258 | 1842.5401 | 1660.195
259 | 1842.4 | 1660.195
260 | 1842.205 | 1660
261 | 1841.9829 | 1659.2
262 | 1840 | 1658.946
263 | 1839.549 | 1657.129
264 | 1839.255 | 1656.321
265 | 1838.59 | 1656
266 | 1838.4211 | 1655.205
267 | 1838.145 | 1655.137
268 | 1837.293 | 1653.652
269 | 1836.8 | 1653.6
270 | 1836.767 | 1652.834
271 | 1835.767 | 1652.548
272 | 1835.337 | 1651.771
273 | 1835.2336 | 1651.22
274 | 1835.131 | 1651.085
275 | 1834.925 | 1648
276 | 1832.8 | 1647.927
277 | 1832.523 | 1647.2
278 | 1832.1434 | 1647.109
279 | 1832.064 | 1647.101
280 | 1831.647 | 1645.6
281 | 1831.384 | 1644.762
282 | 1830.4 | 1642.4
283 | 1830.371 | 1642.014
284 | 1829.581 | 1641.6
285 | 1829.403 | 1640
286 | 1829.242 | 1639.34
287 | 1829.06 | 1637.6
288 | 1828.904 | 1637.295
289 | 1828.8 | 1636
290 | 1827.8498 | 1636
291 | 1826.7294 | 1636
292 | 1825.6709 | 1635.796
293 | 1825.482 | 1634.4
294 | 1825.298 | 1634.4
295 | 1824.8 | 1634.325
296 | 1824.781 | 1632.361
297 | 1824.597 | 1632
298 | 1823.532 | 1631.36
299 | 1823.2803 | 1629.6
300 | 1823.205 | 1628.8
301 | 1822.657 | 1628.348
302 | 1822.4 | 1627.726
303 | 1822.304 | 1625.028
304 | 1821.112 | 1624.8
305 | 1820.422 | 1624.116
306 | 1820 | 1624
307 | 1819.6715 | 1624
308 | 1818.1981 | 1623.798
309 | 1818.0358 | 1623.321
310 | 1817.6831 | 1622.464
311 | 1816.85 | 1622.4
312 | 1814.753 | 1622.4
313 | 1814.4 | 1621.6
314 | 1812.7762 | 1620
315 | 1812.4967 | 1619.476
316 | 1812 | 1619.2
317 | 1811.107 | 1617.657
318 | 1811.042 | 1617.6
319 | 1808.8 | 1616.8
320 | 1808.052 | 1616.673
321 | 1807.6941 | 1616.357
322 | 1807.633 | 1616.032
323 | 1806.403 | 1616
324 | 1805.698 | 1615.555
325 | 1805.6859 | 1615.2
326 | 1804.9518 | 1613.6
327 | 1804.4341 | 1613.039
328 | 1803.338 | 1612.924
329 | 1802.673 | 1612
330 | 1801.945 | 1612
331 | 1801.825 | 1611.083
332 | 1799.841 | 1610.935
333 | 1799.821 | 1610.307
334 | 1799.3766 | 1610.126
335 | 1798.4 | 1610.07
336 | 1798.158 | 1609.714
337 | 1797.835 | 1609.6
338 | 1797.6 | 1605.842
339 | 1797.5 | 1605.584
340 | 1797.136 | 1605.271
341 | 1796.832 | 1603.62
342 | 1796.545 | 1603.434
343 | 1796.174 | 1603.201
344 | 1796.019 | 1603.2
345 | 1796.006 | 1602.4
346 | 1795.9293 | 1601.6
347 | 1793.9503 | 1601.6
348 | 1793.298 | 1601.6
349 | 1793.1733 | 1600.335
350 | 1792.2 | 1600
351 | 1791.4047 | 1600
352 | 1791.185 | 1599.716
353 | 1790.369 | 1599.2
354 | 1789.8428 | 1598.4
355 | 1789.557 | 1598.4
356 | 1789.0993 | 1597.6
357 | 1788.7211 | 1597.596
358 | 1788.565 | 1597.549
359 | 1788 | 1597.412
360 | 1787.689 | 1595.586
361 | 1787.216 | 1595.37
362 | 1786.9578 | 1595.054
363 | 1786.904 | 1594.407
364 | 1786.454 | 1592.239
365 | 1786.4 | 1591.361
366 | 1786.2343 | 1591.2
367 | 1786.232 | 1590.4
368 | 1785.6 | 1589.6
369 | 1785.434 | 1589.6
370 | 1784.8 | 1589.6
371 | 1784.662 | 1589.6
372 | 1783.81 | 1588.8
373 | 1783.629 | 1588.775
374 | 1783.2 | 1588.245
375 | 1782.499 | 1588.205
376 | 1782.3192 | 1587.563
377 | 1782.2292 | 1587.285
378 | 1780.7354 | 1587.285
379 | 1780.377 | 1587.2
380 | 1780 | 1587.2
381 | 1779.2506 | 1585.966
382 | 1779.2 | 1585.772
383 | 1779.002 | 1585.6
384 | 1778.9231 | 1585.6
385 | 1778.711 | 1584.954
386 | 1778.5902 | 1584.8
387 | 1778.4 | 1584.06
388 | 1777.8576 | 1583.958
389 | 1777.6 | 1583.2
390 | 1776.413 | 1583.2
391 | 1776.0807 | 1582.623
392 | 1775.2 | 1582.537
393 | 1775.2 | 1582.4
394 | 1773.524 | 1581.6
395 | 1773.4518 | 1580.8
396 | 1773.255 | 1580.8
397 | 1772.851 | 1580.477
398 | 1772.4797 | 1579.897
399 | 1772.2558 | 1579.2
400 | 1772.0822 | 1579.2
401 | 1771.9988 | 1579.039
402 | 1771.2 | 1578.4
403 | 1771.2 | 1577.961
404 | 1770.4 | 1577.6
405 | 1769.154 | 1577.6
406 | 1768.6143 | 1577.55
407 | 1766.78 | 1576
408 | 1766.438 | 1575.959
409 | 1766.248 | 1575.2
410 | 1765.9551 | 1574.858
411 | 1765.931 | 1574.854
412 | 1765.6 | 1574.4
413 | 1764.8544 | 1574.4
414 | 1764.8 | 1573.3
415 | 1764.516 | 1572.791
416 | 1763.69 | 1572.735
417 | 1763.437 | 1572.368
418 | 1763.2 | 1572
419 | 1763.062 | 1571.869
420 | 1762.864 | 1571.869
421 | 1762.66 | 1571.414
422 | 1762.4 | 1571.306
423 | 1761.6 | 1571.051
424 | 1760.002 | 1569.708
425 | 1760 | 1569.6
426 | 1759.2 | 1569.6
427 | 1759.2 | 1569.6
428 | 1759.08 | 1568.995
429 | 1758.8346 | 1568.8
430 | 1758.4 | 1568.598
431 | 1757.0441 | 1568
432 | 1756.931 | 1567.992
433 | 1756 | 1567.849
434 | 1755.972 | 1567.2
435 | 1755.8808 | 1567.084
436 | 1755.8511 | 1566.4
437 | 1755.7039 | 1565.6
438 | 1755.5448 | 1565.326
439 | 1755.5239 | 1565.326
440 | 1754.8452 | 1564.834
441 | 1754.7479 | 1564.005
442 | 1753.4948 | 1564
443 | 1753.2821 | 1564
444 | 1753.1561 | 1563.602
445 | 1751.451 | 1563.495
446 | 1751.3527 | 1562.698
447 | 1751.2 | 1562.4
448 | 1751.14 | 1561.823
449 | 1751.024 | 1561.284
450 | 1750.511 | 1560.8
451 | 1750.4 | 1559.602
452 | 1750.351 | 1558.4
453 | 1749.963 | 1557.921
454 | 1749.959 | 1557.6
455 | 1749.6223 | 1556.957
456 | 1749.1697 | 1556.8
457 | 1749.1418 | 1556.11
458 | 1748.8 | 1556
459 | 1748 | 1556
460 | 1748 | 1555.512
461 | 1747.764 | 1555.43
462 | 1747.615 | 1555.2
463 | 1746.4 | 1554.893
464 | 1746.298 | 1554.4
465 | 1745.7801 | 1554.202
466 | 1745.6 | 1553.876
467 | 1745.249 | 1553.095
468 | 1744.6384 | 1551.423
469 | 1744.337 | 1551.421
470 | 1744.2447 | 1551.363
471 | 1744 | 1551.2
472 | 1744 | 1551.2
473 | 1743.702 | 1550.4
474 | 1743.6635 | 1549.6
475 | 1743.6133 | 1548.97
476 | 1743.462 | 1548.8
477 | 1743.337 | 1547.534
478 | 1742.4091 | 1547.415
479 | 1742.4 | 1546.516
480 | 1742.288 | 1546.4
481 | 1741.9777 | 1546.4
482 | 1741.725 | 1546.02
483 | 1741.645 | 1545.6
484 | 1741.499 | 1545.6
485 | 1740.9657 | 1545.328
486 | 1740.8 | 1545.326
487 | 1740.399 | 1544.8
488 | 1740.14 | 1544.713
489 | 1739.825 | 1544.063
490 | 1738.997 | 1544.063
491 | 1738.895 | 1543.726
492 | 1738.664 | 1543.2
493 | 1738.4 | 1542.975
494 | 1738.3935 | 1542.776
495 | 1737.954 | 1542.4
496 | 1737.8885 | 1542.4
497 | 1737.852 | 1542.4
498 | 1737.845 | 1541.6
499 | 1737.6 | 1540.8
500 | 1737.0911 | 1540.8
501 | 1737.05 | 1540.8
502 | 1737.0055 | 1540.524
503 | 1736.8 | 1539.891
504 | 1736.2529 | 1539.509
505 | 1735.3911 | 1539.2
506 | 1735.168 | 1539.2
507 | 1735.038 | 1538.4
508 | 1734.369 | 1537.6
509 | 1734.126 | 1537.6
510 | 1734.0288 | 1537.561
511 | 1733.951 | 1537.377
512 | 1733.837 | 1537.263
513 | 1733.618 | 1536.917
514 | 1732.8 | 1536.8
515 | 1731.7952 | 1536.546
516 | 1731.41 | 1536
517 | 1730.896 | 1535.885
518 | 1730.86 | 1535.23
519 | 1730.814 | 1534.807
520 | 1729.6 | 1534.4
521 | 1729.544 | 1534.4
522 | 1729.469 | 1534.4
523 | 1728.951 | 1533.6
524 | 1728.8 | 1533.521
525 | 1728.169 | 1532.8
526 | 1727.807 | 1532.8
527 | 1727.6442 | 1532.498
528 | 1727.174 | 1532.303
529 | 1727.078 | 1532
530 | 1726.744 | 1532
531 | 1726.4389 | 1531.353
532 | 1726.438 | 1531.2
533 | 1726.378 | 1531.2
534 | 1726.1516 | 1531.013
535 | 1726.047 | 1530.978
536 | 1725.917 | 1529.6
537 | 1725.6 | 1528.006
538 | 1725.6 | 1528
539 | 1725.6 | 1527.844
540 | 1724.6753 | 1527.706
541 | 1724.16 | 1527.332
542 | 1724.006 | 1526.888
543 | 1724 | 1526.838
544 | 1724 | 1526.416
545 | 1723.9854 | 1526.4
546 | 1723.893 | 1526.4
547 | 1723.786 | 1526.316
548 | 1723.1676 | 1526.204
549 | 1722.687 | 1525.6
550 | 1722.516 | 1524.526
551 | 1722.0755 | 1524
552 | 1721.903 | 1524
553 | 1721.6 | 1522.926
554 | 1718.8879 | 1522.828
555 | 1718.738 | 1522.799
556 | 1718.709 | 1522.4
557 | 1718.665 | 1522.062
558 | 1718.45 | 1521.981
559 | 1718.4 | 1521.981
560 | 1718.4 | 1521.976
561 | 1718.381 | 1521.6
562 | 1718.3751 | 1521.6
563 | 1718.2943 | 1521.6
564 | 1717.6 | 1521.164
565 | 1717.571 | 1519.789
566 | 1717.536 | 1519.235
567 | 1717.427 | 1519.2
568 | 1717.3001 | 1518.914
569 | 1717.244 | 1518.814
570 | 1717.081 | 1518.814
571 | 1716.665 | 1518.71
572 | 1716.587 | 1518.4
573 | 1715.3512 | 1518.4
574 | 1715.266 | 1518.4
575 | 1715.058 | 1517.6
576 | 1715.055 | 1517.6
577 | 1715.024 | 1517.6
578 | 1714.976 | 1517.527
579 | 1714.76 | 1517.407
580 | 1714.7026 | 1517.36
581 | 1714.1715 | 1516.8
582 | 1714.12 | 1516.478
583 | 1713.845 | 1516
584 | 1713.488 | 1515.679
585 | 1713.281 | 1515.2
586 | 1712.8476 | 1515.2
587 | 1712.774 | 1514.4
588 | 1712.2377 | 1513.803
589 | 1711.846 | 1513.697
590 | 1711.478 | 1513.476
591 | 1711.452 | 1512.8
592 | 1711.2 | 1512.8
593 | 1711.2 | 1512.8
594 | 1710.5644 | 1512.494
595 | 1710.5127 | 1512.162
596 | 1710.031 | 1511.922
597 | 1709.965 | 1511.533
598 | 1709.264 | 1511.252
599 | 1708.9138 | 1510.4
600 | 1708.3705 | 1510.4
601 | 1708.11 | 1510.368
602 | 1708 | 1509.998
603 | 1707.886 | 1509.872
604 | 1707.2 | 1509.591
605 | 1706.823 | 1509.144
606 | 1706.4 | 1508.8
607 | 1706.4 | 1508.526
608 | 1706.4 | 1508.509
609 | 1705.6 | 1508
610 | 1705.486 | 1508
611 | 1704.969 | 1508
612 | 1704.867 | 1507.763
613 | 1704.8 | 1507.651
614 | 1704.5439 | 1507.2
615 | 1704.422 | 1506.995
616 | 1704.336 | 1506.916
617 | 1704 | 1506.4
618 | 1703.789 | 1505.613
619 | 1703.5397 | 1505.6
620 | 1703.159 | 1504
621 | 1702.904 | 1504
622 | 1702.841 | 1504
623 | 1702.6602 | 1504
624 | 1702.4 | 1503.816
625 | 1702.4 | 1503.2
626 | 1701.8192 | 1503.171
627 | 1701.6 | 1503.171
628 | 1701.586 | 1502.4
629 | 1701.5656 | 1502.364
630 | 1701.3564 | 1501.822
631 | 1701.0862 | 1501.177
632 | 1700.8 | 1500.8
633 | 1700.6594 | 1500.541
634 | 1700.6118 | 1500.486
635 | 1700.5223 | 1500.268
636 | 1700.494 | 1500.228
637 | 1700.252 | 1500
638 | 1700.026 | 1500
639 | 1700 | 1500
640 | 1699.7626 | 1499.082
641 | 1699.676 | 1498.714
642 | 1699.22 | 1498.4
643 | 1698.6327 | 1498.264
644 | 1698.4 | 1497.6
645 | 1698.4 | 1497.6
646 | 1698.3869 | 1497.593
647 | 1698.036 | 1497.353
648 | 1697.6099 | 1496.8
649 | 1697.557 | 1496
650 | 1697.546 | 1495.253
651 | 1697.236 | 1495.2
652 | 1696.775 | 1494.829
653 | 1696.1792 | 1494.4
654 | 1696 | 1494.4
655 | 1696 | 1494.4
656 | 1695.2791 | 1494.4
657 | 1695.2 | 1494.198
658 | 1695.2 | 1494.165
659 | 1694.447 | 1494.165
660 | 1693.969 | 1494.002
661 | 1693.945 | 1493.766
662 | 1693.6 | 1493.6
663 | 1693.5468 | 1493.357
664 | 1693.54 | 1493.259
665 | 1693.198 | 1492.8
666 | 1692.649 | 1492.54
667 | 1692.1714 | 1492.378
668 | 1692 | 1492.252
669 | 1691.5158 | 1492
670 | 1691.2 | 1492
671 | 1691.064 | 1491.961
672 | 1691.038 | 1491.722
673 | 1690.754 | 1491.722
674 | 1690.4544 | 1491.721
675 | 1690.426 | 1490.738
676 | 1690.4 | 1490.434
677 | 1690.399 | 1490.4
678 | 1689.979 | 1490.167
679 | 1689.6706 | 1489.818
680 | 1689.2072 | 1489.6
681 | 1688.8665 | 1489.39
682 | 1688.8 | 1489.142
683 | 1688.8 | 1488.8
684 | 1688.7539 | 1488.8
685 | 1688.6062 | 1488.8
686 | 1688.5431 | 1488.8
687 | 1688.519 | 1488.8
688 | 1688 | 1488.651
689 | 1687.8042 | 1488.614
690 | 1687.35 | 1488.587
691 | 1687.2 | 1488
692 | 1687.1831 | 1488
693 | 1686.4 | 1487.837
694 | 1686.4 | 1486.352
695 | 1686.0651 | 1485.876
696 | 1685.6 | 1485.6
697 | 1685.3849 | 1484
698 | 1685.353 | 1484
699 | 1685.1478 | 1483.589
700 | 1685.004 | 1483.234
701 | 1684.8217 | 1483.2
702 | 1684.745 | 1483.009
703 | 1684.7296 | 1483.009
704 | 1684 | 1482.479
705 | 1684 | 1482.4
706 | 1683.9117 | 1482.212
707 | 1683.2 | 1482.151
708 | 1682.8481 | 1482.126
709 | 1682.404 | 1481.681
710 | 1682.4 | 1480.8
711 | 1682.4 | 1480.8
712 | 1681.4818 | 1480.701
713 | 1681.412 | 1480.273
714 | 1681.075 | 1480.067
715 | 1680.964 | 1479.726
716 | 1680.912 | 1479.454
717 | 1680.833 | 1479.2
718 | 1680.8 | 1479.2
719 | 1680.8 | 1478.4
720 | 1680.6373 | 1478.228
721 | 1680.269 | 1477.6
722 | 1679.1101 | 1477.6
723 | 1678.349 | 1477.326
724 | 1677.954 | 1476.806
725 | 1677.484 | 1476.634
726 | 1677.3843 | 1476.183
727 | 1677.291 | 1476
728 | 1676.9667 | 1475.897
729 | 1676.943 | 1475.406
730 | 1676.8 | 1475.2
731 | 1676.6695 | 1475.2
732 | 1675.929 | 1475.2
733 | 1675.8559 | 1475.04
734 | 1675.8557 | 1474.4
735 | 1675.433 | 1473.306
736 | 1675.2 | 1473.034
737 | 1674.824 | 1472.8
738 | 1674.4572 | 1472.8
739 | 1674.2622 | 1472.526
740 | 1673.787 | 1472
741 | 1673.4272 | 1472
742 | 1673.221 | 1472
743 | 1673.0266 | 1472
744 | 1672.8606 | 1471.956
745 | 1672.28 | 1471.853
746 | 1672.005 | 1471.847
747 | 1671.964 | 1471.2
748 | 1671.8876 | 1471.04
749 | 1671.8207 | 1470.4
750 | 1671.773 | 1470.4
751 | 1671.657 | 1470.4
752 | 1670.927 | 1470.4
753 | 1668.96 | 1470.4
754 | 1668.8448 | 1470.207
755 | 1668.8 | 1469.775
756 | 1668.541 | 1469.775
757 | 1668.373 | 1469.6
758 | 1667.2764 | 1469.462
759 | 1667.2 | 1469.462
760 | 1666.961 | 1468.833
761 | 1666.4 | 1468.526
762 | 1666.1761 | 1468.005
763 | 1665.9839 | 1468
764 | 1665.983 | 1467.65
765 | 1665.6 | 1467.2
766 | 1664.717 | 1467.071
767 | 1664.7066 | 1466.981
768 | 1664.469 | 1466.4
769 | 1664.4276 | 1466.4
770 | 1664.173 | 1466.369
771 | 1664.025 | 1466.274
772 | 1664 | 1465.6
773 | 1663.649 | 1465.6
774 | 1663.536 | 1465.477
775 | 1663.509 | 1465.326
776 | 1663.487 | 1464.8
777 | 1663.2 | 1464.528
778 | 1662.845 | 1464.528
779 | 1662.323 | 1464.087
780 | 1661.8303 | 1464.006
781 | 1661.6 | 1464
782 | 1661.6 | 1463.752
783 | 1661.6 | 1463.2
784 | 1661.105 | 1463.2
785 | 1660.8 | 1462.4
786 | 1660.7151 | 1462.273
787 | 1660.537 | 1461.6
788 | 1660.1947 | 1461.478
789 | 1660.1947 | 1461.462
790 | 1660.1947 | 1460.8
791 | 1660.1588 | 1460.8
792 | 1660 | 1460.644
793 | 1660 | 1460.106
794 | 1659.929 | 1460
795 | 1659.705 | 1460
796 | 1659.288 | 1459.826
797 | 1659.2 | 1459.415
798 | 1659.084 | 1459.2
799 | 1658.966 | 1459.2
800 | 1658.8698 | 1459.2
801 | 1658.613 | 1459.2
802 | 1658.559 | 1459.2
803 | 1657.388 | 1459.2
804 | 1657.048 | 1459.102
805 | 1656.929 | 1458.926
806 | 1656.806 | 1458.4
807 | 1656.8 | 1458.4
808 | 1656.7966 | 1458.305
809 | 1656.662 | 1458.236
810 | 1656.625 | 1457.6
811 | 1656.3215 | 1457.6
812 | 1656 | 1457.6
813 | 1655.249 | 1457.536
814 | 1655.2046 | 1457.423
815 | 1655.173 | 1457.065
816 | 1655.1368 | 1456.8
817 | 1654.093 | 1456.677
818 | 1653.7527 | 1456.398
819 | 1653.652 | 1456.205
820 | 1653.6 | 1456
821 | 1653.6 | 1455.962
822 | 1653.5431 | 1455.594
823 | 1653.246 | 1455.483
824 | 1653.202 | 1455.323
825 | 1653.136 | 1454.364
826 | 1652.92 | 1453.6
827 | 1652.8342 | 1453.6
828 | 1652.807 | 1453.6
829 | 1652.723 | 1453.284
830 | 1652.685 | 1452.727
831 | 1652.6215 | 1452.603
832 | 1652.5475 | 1452.169
833 | 1652.4707 | 1451.916
834 | 1652.413 | 1451.916
835 | 1651.7706 | 1450.041
836 | 1651.22 | 1449.737
837 | 1651.085 | 1449.6
838 | 1651.0189 | 1449.6
839 | 1650.484 | 1449.6
840 | 1650.4 | 1449.583
841 | 1649.699 | 1448.8
842 | 1648.641 | 1447.967
843 | 1648.157 | 1447.946
844 | 1648.072 | 1447.559
845 | 1648 | 1447.2
846 | 1647.9272 | 1447.2
847 | 1647.8616 | 1447.175
848 | 1647.588 | 1446.9
849 | 1647.544 | 1446.723
850 | 1647.2 | 1446.52
851 | 1647.2 | 1446.4
852 | 1647.1089 | 1446.4
853 | 1647.1089 | 1446.4
854 | 1646.336 | 1446.201
855 | 1646.173 | 1446.081
856 | 1645.765 | 1445.923
857 | 1645.752 | 1445.882
858 | 1645.6 | 1445.6
859 | 1645.065 | 1445.326
860 | 1644.823 | 1445.105
861 | 1644.797 | 1444.8
862 | 1644.762 | 1444.8
863 | 1644.1407 | 1444.748
864 | 1643.977 | 1444.526
865 | 1643.7 | 1444.312
866 | 1643.485 | 1444
867 | 1643.2243 | 1444
868 | 1643.0203 | 1444
869 | 1642.84 | 1444
870 | 1642.4999 | 1443.788
871 | 1642.4 | 1443.534
872 | 1642.3118 | 1443.444
873 | 1642.0142 | 1443.122
874 | 1641.988 | 1443.09
875 | 1641.6575 | 1443.042
876 | 1641.6 | 1442.4
877 | 1641.378 | 1442.126
878 | 1641.186 | 1441.4
879 | 1640.8 | 1441.018
880 | 1640.668 | 1440.8
881 | 1640 | 1440.8
882 | 1639.9322 | 1440.774
883 | 1639.3396 | 1440.767
884 | 1638.9311 | 1440.565
885 | 1638.7226 | 1440.139
886 | 1638.605 | 1440
887 | 1638.537 | 1439.865
888 | 1638.403 | 1439.53
889 | 1638.3992 | 1439.316
890 | 1638.085 | 1438.563
891 | 1638.025 | 1438.539
892 | 1637.9753 | 1437.6
893 | 1637.6 | 1436.8
894 | 1637.5824 | 1436.8
895 | 1637.2954 | 1436.559
896 | 1637.1595 | 1436.559
897 | 1637.0923 | 1436
898 | 1636.944 | 1436
899 | 1636.7689 | 1436
900 | 1636.574 | 1436
901 | 1636.4498 | 1435.771
902 | 1636.443 | 1435.366
903 | 1636.4299 | 1435.2
904 | 1636.1784 | 1434.4
905 | 1636 | 1434.4
906 | 1636 | 1434.298
907 | 1636 | 1433.6
908 | 1635.7965 | 1433.6
909 | 1635.582 | 1433.6
910 | 1635.438 | 1432.8
911 | 1635.414 | 1432.02
912 | 1635.2 | 1432.015
913 | 1634.626 | 1432.008
914 | 1634.4 | 1432
915 | 1634.4 | 1431.211
916 | 1634.3255 | 1431.202
917 | 1634.306 | 1431.2
918 | 1634.053 | 1431.133
919 | 1633.953 | 1430.414
920 | 1633.6 | 1430.4
921 | 1633.544 | 1430.4
922 | 1633.042 | 1430.141
923 | 1633.019 | 1430.093
924 | 1632.9415 | 1429.6
925 | 1632.862 | 1429.6
926 | 1632.697 | 1429.6
927 | 1632.597 | 1429.566
928 | 1632.0301 | 1429.474
929 | 1632 | 1428.8
930 | 1632 | 1428.252
931 | 1631.553 | 1428.024
932 | 1631.387 | 1428.012
933 | 1631.193 | 1428
934 | 1630.98 | 1428
935 | 1630.578 | 1428
936 | 1629.851 | 1428
937 | 1629.663 | 1428
938 | 1629.66 | 1427.235
939 | 1629.6 | 1427.2
940 | 1629.559 | 1427.2
941 | 1629.508 | 1425.922
942 | 1629.2201 | 1425.6
943 | 1628.8 | 1425.6
944 | 1628.7921 | 1425.478
945 | 1628.745 | 1425.064
946 | 1628.6735 | 1424.8
947 | 1628.6013 | 1424.522
948 | 1628.348 | 1424
949 | 1628.2678 | 1424
950 | 1628 | 1423.842
951 | 1627.857 | 1423.358
952 | 1627.7258 | 1423.351
953 | 1627.697 | 1423.2
954 | 1627.379 | 1423.2
955 | 1627.268 | 1423.2
956 | 1627.259 | 1423.2
957 | 1627.187 | 1422.926
958 | 1626.909 | 1422.4
959 | 1626.9086 | 1422.4
960 | 1626.609 | 1421.649
961 | 1626.5602 | 1421.6
962 | 1626.32 | 1421.6
963 | 1625.792 | 1421.025
964 | 1625.6 | 1421.02
965 | 1625.599 | 1420.356
966 | 1625.402 | 1420.243
967 | 1625.359 | 1420
968 | 1625.121 | 1420
969 | 1625.028 | 1419.829
970 | 1624.992 | 1419.466
971 | 1624.8 | 1419.2
972 | 1624.8 | 1418.689
973 | 1624.376 | 1418.435
974 | 1624.258 | 1418.083
975 | 1624.0727 | 1418.083
976 | 1624 | 1417.664
977 | 1624 | 1417.299
978 | 1624 | 1417.283
979 | 1623.7979 | 1417.135
980 | 1623.593 | 1416.8
981 | 1623.5803 | 1416.8
982 | 1623.5477 | 1416.8
983 | 1623.4698 | 1416.481
984 | 1623.432 | 1416.264
985 | 1623.3211 | 1416.202
986 | 1623.245 | 1416
987 | 1623.038 | 1416
988 | 1622.9691 | 1416
989 | 1622.4644 | 1415.902
990 | 1622.4 | 1415.2
991 | 1622.4 | 1415.073
992 | 1622.4 | 1414.804
993 | 1622.298 | 1414.653
994 | 1622.297 | 1414.651
995 | 1621.666 | 1414.405
996 | 1621.6 | 1414.4
997 | 1621.58 | 1414.4
998 | 1621.22 | 1414.4
999 | 1621.135 | 1413.61
1000 | 1620.881 | 1413.6
1001 | 1620.8484 | 1412.8
1002 | 1620.767 | 1412.8
1003 | 1620.676 | 1412.179
1004 | 1620.5808 | 1412
1005 | 1620.4415 | 1411.664
1006 | 1620.387 | 1411.574
1007 | 1620.241 | 1411.574
1008 | 1620.088 | 1411.289
1009 | 1620 | 1411.2
1010 | 1619.476 | 1410.727
1011 | 1619.2759 | 1410.488
1012 | 1619.2 | 1410.4
1013 | 1618.778 | 1409.602
1014 | 1617.9573 | 1409.6
1015 | 1617.9401 | 1409.584
1016 | 1617.779 | 1408.995
1017 | 1617.657 | 1408.898
1018 | 1617.6 | 1408.8
1019 | 1617.23 | 1408.8
1020 | 1616.8 | 1408.8
1021 | 1616.673 | 1408.521
1022 | 1616.357 | 1408.111
1023 | 1616.041 | 1408
1024 | 1616.0319 | 1408
1025 | 1616 | 1408
1026 | 1615.953 | 1408
1027 | 1615.8908 | 1408
1028 | 1615.5546 | 1407.738
1029 | 1615.2725 | 1407.485
1030 | 1615.258 | 1407.2
1031 | 1615.2545 | 1407.2
1032 | 1615.2 | 1407.035
1033 | 1615.0866 | 1406.667
1034 | 1615.041 | 1406.4
1035 | 1614.836 | 1405.711
1036 | 1614.825 | 1405.6
1037 | 1614.354 | 1404.843
1038 | 1614.236 | 1404.8
1039 | 1614.058 | 1404.8
1040 | 1613.967 | 1404.704
1041 | 1613.9387 | 1404.394
1042 | 1613.7006 | 1404.292
1043 | 1613.6 | 1403.2
1044 | 1613.6 | 1403.15
1045 | 1613.5784 | 1402.523
1046 | 1612.9237 | 1402.523
1047 | 1612.774 | 1402.519
1048 | 1612.223 | 1402.4
1049 | 1612.0778 | 1402.4
1050 | 1612 | 1402.373
1051 | 1612 | 1402.262
1052 | 1611.558 | 1402.198
1053 | 1611.083 | 1401.76
1054 | 1610.935 | 1401.083
1055 | 1610.809 | 1401.076
1056 | 1610.3071 | 1400.8
1057 | 1610.257 | 1400.8
1058 | 1610.0698 | 1400.707
1059 | 1610.063 | 1400.526
1060 | 1609.8915 | 1400.332
1061 | 1609.75 | 1400
1062 | 1609.7142 | 1400
1063 | 1609.6674 | 1399.936
1064 | 1609.6 | 1399.92
1065 | 1609.349 | 1399.336
1066 | 1609.172 | 1399.307
1067 | 1609.0448 | 1398.549
1068 | 1608.955 | 1398.489
1069 | 1608.8247 | 1398.4
1070 | 1608.786 | 1398.4
1071 | 1608.759 | 1398.4
1072 | 1608.7589 | 1398.4
1073 | 1608.326 | 1397.6
1074 | 1608.296 | 1397.6
1075 | 1608.087 | 1396.8
1076 | 1607.9571 | 1396.794
1077 | 1607.7798 | 1396.203
1078 | 1607.6891 | 1396
1079 | 1607.655 | 1395.281
1080 | 1607.397 | 1395.2
1081 | 1607.2 | 1394.649
1082 | 1606.824 | 1394.604
1083 | 1606.752 | 1394.546
1084 | 1606.691 | 1394.491
1085 | 1606.679 | 1394.4
1086 | 1606.507 | 1394.4
1087 | 1606.5008 | 1394.4
1088 | 1605.867 | 1394.4
1089 | 1605.764 | 1394.126
1090 | 1605.5447 | 1394.069
1091 | 1605.522 | 1393.933
1092 | 1605.2895 | 1393.6
1093 | 1605.2708 | 1393.075
1094 | 1605.1611 | 1393.075
1095 | 1604.899 | 1392.8
1096 | 1604.627 | 1392.8
1097 | 1604.417 | 1392.764
1098 | 1604.172 | 1392.764
1099 | 1604.111 | 1392.501
1100 | 1603.942 | 1392.164
1101 | 1603.774 | 1392.164
1102 | 1603.6198 | 1392
1103 | 1603.4885 | 1392
1104 | 1603.456 | 1392
1105 | 1603.4336 | 1392
1106 | 1603.201 | 1392
1107 | 1603.2 | 1391.946
1108 | 1603.2 | 1391.736
1109 | 1603.039 | 1391.728
1110 | 1602.996 | 1391.496
1111 | 1602.9466 | 1391.367
1112 | 1602.9128 | 1390.98
1113 | 1602.881 | 1390.4
1114 | 1602.583 | 1389.6
1115 | 1602.436 | 1389.326
1116 | 1602.4 | 1389.063
1117 | 1602.301 | 1388.8
1118 | 1602.265 | 1388.767
1119 | 1602.1427 | 1388.675
1120 | 1602.0439 | 1388.646
1121 | 1601.832 | 1388.594
1122 | 1601.6 | 1388.389
1123 | 1601.6 | 1388.231
1124 | 1601.6 | 1388
1125 | 1601.467 | 1387.775
1126 | 1601.404 | 1387.447
1127 | 1601.327 | 1387.323
1128 | 1601.2271 | 1387.2
1129 | 1601.1342 | 1386.835
1130 | 1601.039 | 1386.835
1131 | 1600.8 | 1386.835
1132 | 1600.536 | 1386.586
1133 | 1600.335 | 1386.4
1134 | 1600 | 1386.4
1135 | 1600 | 1386.218
1136 | 1599.883 | 1386.032
1137 | 1599.831 | 1385.6
1138 | 1599.7157 | 1385.46
1139 | 1599.6753 | 1384.8
1140 | 1599.518 | 1384.8
1141 | 1599.501 | 1384.8
1142 | 1599.2 | 1384.131
1143 | 1599.2 | 1384.06
1144 | 1598.971 | 1384
1145 | 1598.4 | 1383.44
1146 | 1598.4 | 1383.398
1147 | 1598.3855 | 1382.778
1148 | 1598.239 | 1382.732
1149 | 1597.991 | 1382.572
1150 | 1597.92 | 1382.4
1151 | 1597.6423 | 1382.173
1152 | 1597.6 | 1382.171
1153 | 1597.596 | 1381.6
1154 | 1597.5495 | 1381.6
1155 | 1597.412 | 1381.309
1156 | 1596.3166 | 1380.8
1157 | 1595.5861 | 1380.8
1158 | 1595.3702 | 1380.577
1159 | 1595.194 | 1380
1160 | 1595.175 | 1379.986
1161 | 1595.0541 | 1379.821
1162 | 1594.663 | 1379.804
1163 | 1594.654 | 1379.414
1164 | 1594.407 | 1379.2
1165 | 1593.999 | 1379.189
1166 | 1593.7705 | 1379.1
1167 | 1593.6599 | 1379.065
1168 | 1593.632 | 1378.632
1169 | 1593.5002 | 1378.553
1170 | 1593.282 | 1378.4
1171 | 1593.236 | 1378.315
1172 | 1593.166 | 1378.126
1173 | 1593.084 | 1378.126
1174 | 1593.023 | 1377.666
1175 | 1592.847 | 1377.629
1176 | 1592.548 | 1377.6
1177 | 1592.421 | 1377.545
1178 | 1592.395 | 1377.407
1179 | 1592.282 | 1377.226
1180 | 1592.239 | 1377.045
1181 | 1592.0899 | 1376.853
1182 | 1591.6166 | 1376.8
1183 | 1591.2 | 1376.8
1184 | 1591.079 | 1376.8
1185 | 1590.8468 | 1376.158
1186 | 1590.8052 | 1376
1187 | 1590.4 | 1376
1188 | 1589.617 | 1375.59
1189 | 1589.6 | 1375.523
1190 | 1589.6 | 1375.404
1191 | 1589.6 | 1375.2
1192 | 1589.6 | 1375.191
1193 | 1589.6 | 1374.926
1194 | 1589.517 | 1374.738
1195 | 1589.396 | 1373.6
1196 | 1589.091 | 1373.307
1197 | 1588.8 | 1372.8
1198 | 1588.775 | 1372.8
1199 | 1588.6233 | 1372.389
1200 | 1588.328 | 1372.389
1201 | 1588.2695 | 1372
1202 | 1588.2052 | 1371.445
1203 | 1588.152 | 1371.2
1204 | 1588.0616 | 1370.792
1205 | 1587.901 | 1369.851
1206 | 1587.586 | 1369.6
1207 | 1587.4332 | 1369.538
1208 | 1587.2847 | 1369.326
1209 | 1587.2847 | 1368.8
1210 | 1587.2 | 1368.8
1211 | 1587.2 | 1368.8
1212 | 1587.2 | 1368.389
1213 | 1587.1934 | 1368.257
1214 | 1586.6892 | 1368.022
1215 | 1586.458 | 1368
1216 | 1585.9659 | 1368
1217 | 1585.9435 | 1367.412
1218 | 1585.7722 | 1367.317
1219 | 1585.6 | 1367.211
1220 | 1585.6 | 1367.2
1221 | 1585.4113 | 1367.2
1222 | 1584.9707 | 1366.663
1223 | 1584.9543 | 1366.634
1224 | 1584.8 | 1366.4
1225 | 1584.5198 | 1366.4
1226 | 1584.409 | 1366.4
1227 | 1584.3586 | 1366.39
1228 | 1584.287 | 1365.6
1229 | 1584.1702 | 1365.6
1230 | 1584.014 | 1365.6
1231 | 1583.2 | 1365.482
1232 | 1583.2 | 1365.124
1233 | 1583.009 | 1364.958
1234 | 1582.693 | 1364.8
1235 | 1582.6231 | 1364.8
1236 | 1582.537 | 1364.8
1237 | 1582.4 | 1364.35
1238 | 1582.275 | 1364
1239 | 1582.1499 | 1363.654
1240 | 1581.6 | 1363.322
1241 | 1581.445 | 1363.2
1242 | 1581.08 | 1362.679
1243 | 1580.9303 | 1362.499
1244 | 1580.825 | 1362.4
1245 | 1580.8 | 1362.4
1246 | 1580.8 | 1362.4
1247 | 1580.7302 | 1362.4
1248 | 1580.699 | 1362.27
1249 | 1580.662 | 1361.6
1250 | 1580.4767 | 1361.6
1251 | 1580.403 | 1361.326
1252 | 1580.373 | 1360.869
1253 | 1580.043 | 1360.8
1254 | 1580 | 1360.8
1255 | 1579.999 | 1360.8
1256 | 1579.901 | 1360.647
1257 | 1579.897 | 1359.2
1258 | 1579.4376 | 1358.4
1259 | 1579.2 | 1358.4
1260 | 1579.2 | 1358.4
1261 | 1578.9248 | 1358.4
1262 | 1578.746 | 1358.364
1263 | 1578.4 | 1358.291
1264 | 1578.4 | 1358.088
1265 | 1577.9614 | 1357.739
1266 | 1577.8526 | 1357.194
1267 | 1577.6 | 1357.077
1268 | 1577.6 | 1356.8
1269 | 1577.5497 | 1356.8
1270 | 1576.944 | 1356.8
1271 | 1576.816 | 1356
1272 | 1576.8 | 1356
1273 | 1576.8 | 1355.957
1274 | 1576.5504 | 1355.757
1275 | 1576.4513 | 1355.726
1276 | 1576 | 1355.507
1277 | 1575.959 | 1355.507
1278 | 1575.5306 | 1355.144
1279 | 1575.2 | 1355.122
1280 | 1574.8582 | 1354.98
1281 | 1574.8537 | 1354.841
1282 | 1574.613 | 1354.4
1283 | 1574.4 | 1354.321
1284 | 1574.4 | 1354.126
1285 | 1574.2258 | 1353.885
1286 | 1573.75 | 1353.426
1287 | 1573.2998 | 1353.116
1288 | 1572.945 | 1353.007
1289 | 1572.7909 | 1352.649
1290 | 1572.735 | 1352.239
1291 | 1572.208 | 1352.07
1292 | 1572.128 | 1352
1293 | 1572 | 1351.886
1294 | 1572 | 1351.872
1295 | 1571.8691 | 1351.817
1296 | 1571.8691 | 1351.522
1297 | 1571.813 | 1351.2
1298 | 1571.3059 | 1351.2
1299 | 1571.2 | 1351.055
1300 | 1571.2 | 1350.4
1301 | 1571.0512 | 1350.4
1302 | 1570.841 | 1350.4
1303 | 1570.749 | 1349.932
1304 | 1570.4 | 1349.679
1305 | 1570.274 | 1349.584
1306 | 1570.042 | 1349.502
1307 | 1569.9972 | 1349.132
1308 | 1569.862 | 1348.944
1309 | 1569.698 | 1348.8
1310 | 1569.6 | 1348.8
1311 | 1569.6 | 1348.8
1312 | 1569.6 | 1348.792
1313 | 1569.6 | 1348
1314 | 1569.14 | 1347.852
1315 | 1568.995 | 1347.784
1316 | 1568.8 | 1347.726
1317 | 1568.8 | 1347.669
1318 | 1568.5977 | 1347.526
1319 | 1568.4882 | 1347.2
1320 | 1568.38 | 1347.2
1321 | 1568 | 1347.2
1322 | 1568 | 1346.4
1323 | 1567.968 | 1345.6
1324 | 1567.5485 | 1345.6
1325 | 1567.2 | 1345.6
1326 | 1567.2 | 1345.6
1327 | 1567.16 | 1345.6
1328 | 1567.117 | 1345.147
1329 | 1567.0843 | 1344.8
1330 | 1567.0843 | 1344.8
1331 | 1566.858 | 1344.8
1332 | 1566.4 | 1344.8
1333 | 1566.4 | 1344.8
1334 | 1566.318 | 1344.762
1335 | 1566.1442 | 1344.526
1336 | 1566.084 | 1344
1337 | 1566.0129 | 1344
1338 | 1565.6 | 1343.38
1339 | 1565.3264 | 1342.549
1340 | 1565.3264 | 1342.52
1341 | 1565.3264 | 1342.418
1342 | 1565.032 | 1342.112
1343 | 1564.8337 | 1341.6
1344 | 1564.8 | 1341.6
1345 | 1564.005 | 1341.6
1346 | 1564 | 1341.6
1347 | 1564 | 1341.163
1348 | 1563.935 | 1340.571
1349 | 1563.6281 | 1340.366
1350 | 1563.602 | 1340
1351 | 1563.4947 | 1340
1352 | 1563.398 | 1339.569
1353 | 1562.9559 | 1339.569
1354 | 1562.899 | 1339.236
1355 | 1562.6978 | 1339.188
1356 | 1562.4 | 1339.042
1357 | 1562.161 | 1338.921
1358 | 1561.9623 | 1338.646
1359 | 1561.8691 | 1338.4
1360 | 1561.823 | 1338.4
1361 | 1561.3107 | 1338.232
1362 | 1561.284 | 1338.074
1363 | 1561.218 | 1337.6
1364 | 1560.8 | 1337.147
1365 | 1560.4337 | 1336.8
1366 | 1560.409 | 1336.8
1367 | 1560.354 | 1336.449
1368 | 1560.347 | 1336
1369 | 1559.6016 | 1335.966
1370 | 1559.5597 | 1335.2
1371 | 1559.029 | 1335.092
1372 | 1559.024 | 1334.926
1373 | 1558.9445 | 1334.666
1374 | 1558.583 | 1334.4
1375 | 1558.4 | 1334.4
1376 | 1558.331 | 1333.6
1377 | 1558.054 | 1333.6
1378 | 1557.9659 | 1333.232
1379 | 1557.9215 | 1333.194
1380 | 1557.6541 | 1332.8
1381 | 1557.6 | 1332.8
1382 | 1557.6 | 1332.8
1383 | 1557.5416 | 1331.639
1384 | 1557.38 | 1331.434
1385 | 1557.2327 | 1331.427
1386 | 1557.127 | 1331.2
1387 | 1556.917 | 1331.2
1388 | 1556.8 | 1330.916
1389 | 1556.8 | 1330.556
1390 | 1556.628 | 1330.257
1391 | 1556.4 | 1329.82
1392 | 1556.2421 | 1329.6
1393 | 1556.164 | 1329.6
1394 | 1556.11 | 1329.555
1395 | 1556.0846 | 1329.085
1396 | 1556 | 1329.031
1397 | 1556 | 1328.876
1398 | 1555.5125 | 1328.8
1399 | 1555.4302 | 1328.8
1400 | 1555.276 | 1328.564
1401 | 1555.2 | 1328.413
1402 | 1555.098 | 1328.156
1403 | 1554.491 | 1328
1404 | 1554.4 | 1327.902
1405 | 1554.4 | 1327.723
1406 | 1554.3395 | 1327.614
1407 | 1554.326 | 1326.4
1408 | 1554.2017 | 1326.126
1409 | 1554.1529 | 1326.022
1410 | 1554.145 | 1325.702
1411 | 1554.022 | 1325.6
1412 | 1553.989 | 1325.6
1413 | 1553.979 | 1325.6
1414 | 1553.8764 | 1325.457
1415 | 1553.6 | 1324.8
1416 | 1553.6 | 1324.8
1417 | 1553.3917 | 1324.8
1418 | 1553.305 | 1324.672
1419 | 1553.0947 | 1324.067
1420 | 1552.9578 | 1324
1421 | 1552.301 | 1324
1422 | 1552.2695 | 1324
1423 | 1552.097 | 1324
1424 | 1551.8563 | 1324
1425 | 1551.5661 | 1323.964
1426 | 1551.507 | 1323.903
1427 | 1551.4233 | 1323.126
1428 | 1551.363 | 1322.503
1429 | 1551.2 | 1322.445
1430 | 1551.2 | 1322.4
1431 | 1551.141 | 1322.4
1432 | 1551.0702 | 1322.126
1433 | 1550.943 | 1322.038
1434 | 1550.847 | 1321.613
1435 | 1550.773 | 1321.6
1436 | 1550.7356 | 1321.6
1437 | 1550.416 | 1321.6
1438 | 1550.4 | 1321.035
1439 | 1550.4 | 1320.994
1440 | 1549.679 | 1320.949
1441 | 1549.6 | 1320.795
1442 | 1548.9698 | 1320.365
1443 | 1548.9034 | 1320.258
1444 | 1548.8 | 1320
1445 | 1548.8 | 1319.943
1446 | 1548.768 | 1319.726
1447 | 1548.5916 | 1319.2
1448 | 1548.0484 | 1319.16
1449 | 1548 | 1318.926
1450 | 1547.9905 | 1318.85
1451 | 1547.887 | 1318.787
1452 | 1547.5341 | 1318.4
1453 | 1547.522 | 1318.4
1454 | 1547.461 | 1318.126
1455 | 1547.415 | 1318.055
1456 | 1547.1005 | 1317.825
1457 | 1546.8023 | 1317.825
1458 | 1546.6392 | 1317.687
1459 | 1546.546 | 1317.007
1460 | 1546.5163 | 1316.91
1461 | 1546.4283 | 1316.835
1462 | 1546.4 | 1316.8
1463 | 1546.4 | 1316.738
1464 | 1546.4 | 1316.109
1465 | 1546.268 | 1316
1466 | 1546.2679 | 1315.2
1467 | 1546.263 | 1315.122
1468 | 1546.02 | 1315.11
1469 | 1545.6 | 1315.07
1470 | 1545.6 | 1314.954
1471 | 1545.343 | 1314.638
1472 | 1545.3275 | 1314.635
1473 | 1545.1075 | 1314.4
1474 | 1545.101 | 1314.374
1475 | 1544.9103 | 1314.233
1476 | 1544.8 | 1313.639
1477 | 1544.8 | 1313.6
1478 | 1544.713 | 1313.6
1479 | 1544.646 | 1313.251
1480 | 1544.619 | 1312.8
1481 | 1544.599 | 1312.8
1482 | 1544.327 | 1312.8
1483 | 1544.0628 | 1312.424
1484 | 1544.0628 | 1312.249
1485 | 1544 | 1312.249
1486 | 1543.7762 | 1312
1487 | 1543.6956 | 1311.592
1488 | 1543.6519 | 1311.479
1489 | 1543.534 | 1311.2
1490 | 1543.2 | 1310.775
1491 | 1542.9749 | 1310.4
1492 | 1542.9506 | 1310.4
1493 | 1542.7756 | 1310.4
1494 | 1542.7437 | 1310.4
1495 | 1542.4 | 1310.163
1496 | 1542.4 | 1309.918
1497 | 1542.4 | 1309.918
1498 | 1542.1992 | 1309.702
1499 | 1542.1261 | 1309.226
1500 | 1542.057 | 1308.997
1501 | 1541.713 | 1308.846
1502 | 1541.6 | 1308.49
1503 | 1541.5026 | 1308
1504 | 1540.824 | 1307.982
1505 | 1540.8 | 1307.827
1506 | 1540.8 | 1306.284
1507 | 1540.8 | 1306.083
1508 | 1540.681 | 1306.033
1509 | 1540.524 | 1306.033
1510 | 1540.0611 | 1305.82
1511 | 1540.045 | 1305.6
1512 | 1539.8915 | 1305.6
1513 | 1539.86 | 1305.548
1514 | 1539.824 | 1305.546
1515 | 1539.811 | 1305.303
1516 | 1539.509 | 1304.8
1517 | 1539.2 | 1304.8
1518 | 1539.2 | 1304.8
1519 | 1539.01 | 1304.759
1520 | 1538.833 | 1304.72
1521 | 1538.7348 | 1304.439
1522 | 1538.6406 | 1304
1523 | 1538.6163 | 1304
1524 | 1538.464 | 1304
1525 | 1538.4 | 1303.625
1526 | 1538.349 | 1303.396
1527 | 1538.188 | 1303.2
1528 | 1538.105 | 1303.2
1529 | 1537.608 | 1302.952
1530 | 1537.6 | 1302.881
1531 | 1537.6 | 1302.803
1532 | 1537.5607 | 1302.63
1533 | 1537.5301 | 1302.606
1534 | 1537.528 | 1302.4
1535 | 1537.3752 | 1301.939
1536 | 1537.263 | 1301.734
1537 | 1537.183 | 1301.326
1538 | 1537.052 | 1300
1539 | 1536.9168 | 1300
1540 | 1536.8077 | 1300
1541 | 1536.804 | 1300
1542 | 1536.8 | 1299.867
1543 | 1536.6216 | 1299.532
1544 | 1536.546 | 1299.258
1545 | 1536.423 | 1299.2
1546 | 1536.183 | 1299.2
1547 | 1536 | 1298.848
1548 | 1535.971 | 1298.486
1549 | 1535.8845 | 1298.4
1550 | 1535.856 | 1298.193
1551 | 1535.769 | 1298.131
1552 | 1535.5758 | 1297.634
1553 | 1535.5124 | 1297.073
1554 | 1535.2541 | 1296.8
1555 | 1535.2298 | 1296.726
1556 | 1534.8067 | 1296.421
1557 | 1534.4519 | 1295.933
1558 | 1534.4 | 1295.2
1559 | 1534.4 | 1295.2
1560 | 1534.4 | 1294.4
1561 | 1534.3568 | 1294.4
1562 | 1534.321 | 1294.4
1563 | 1534.229 | 1294.4
1564 | 1534.199 | 1294.379
1565 | 1534.0547 | 1294.146
1566 | 1533.6 | 1293.802
1567 | 1533.5207 | 1293.6
1568 | 1533.1581 | 1293.35
1569 | 1533.0237 | 1293.041
1570 | 1532.8 | 1292.96
1571 | 1532.8 | 1292.8
1572 | 1532.198 | 1292.719
1573 | 1532 | 1292
1574 | 1532 | 1292
1575 | 1532 | 1292
1576 | 1532 | 1291.335
1577 | 1531.3527 | 1291.2
1578 | 1531.346 | 1290.494
1579 | 1531.2 | 1290.4
1580 | 1531.2 | 1290.4
1581 | 1531.2 | 1290.4
1582 | 1531.013 | 1290.4
1583 | 1530.9776 | 1290.4
1584 | 1530.86 | 1290.198
1585 | 1530.718 | 1289.367
1586 | 1530.064 | 1288.8
1587 | 1529.9046 | 1288.125
1588 | 1529.712 | 1288
1589 | 1529.6 | 1288
1590 | 1529.6 | 1288
1591 | 1529.6 | 1287.915
1592 | 1529.6 | 1287.627
1593 | 1529.519 | 1287.2
1594 | 1528.8197 | 1287.2
1595 | 1528.819 | 1287.2
1596 | 1528.475 | 1286.744
1597 | 1528.3529 | 1286.61
1598 | 1528.29 | 1286.4
1599 | 1528.207 | 1286.4
1600 | 1528.0967 | 1285.833
1601 | 1528.006 | 1285.689
1602 | 1528 | 1285.6
1603 | 1527.881 | 1285.6
1604 | 1527.7062 | 1285.6
1605 | 1527.7062 | 1284.704
1606 | 1527.332 | 1284.113
1607 | 1527.327 | 1284
1608 | 1527.2199 | 1284
1609 | 1526.8884 | 1284
1610 | 1526.8884 | 1283.96
1611 | 1526.8378 | 1283.787
1612 | 1526.73 | 1283.726
1613 | 1526.413 | 1283.2
1614 | 1526.4 | 1283.2
1615 | 1526.4 | 1283.014
1616 | 1526.204 | 1282.4
1617 | 1526.041 | 1282.357
1618 | 1525.9328 | 1282.193
1619 | 1525.6 | 1282.011
1620 | 1525.6 | 1281.6
1621 | 1525.559 | 1281.326
1622 | 1525.4623 | 1280.8
1623 | 1525.3618 | 1280.8
1624 | 1525.3581 | 1280.599
1625 | 1525.044 | 1280
1626 | 1524.5 | 1280
1627 | 1524 | 1279.805
1628 | 1524 | 1278.874
1629 | 1524 | 1278.268
1630 | 1523.695 | 1277.6
1631 | 1523.623 | 1277.6
1632 | 1523.622 | 1276.8
1633 | 1523.5696 | 1276.745
1634 | 1522.957 | 1276.292
1635 | 1522.874 | 1276
1636 | 1522.828 | 1276
1637 | 1522.7988 | 1276
1638 | 1522.665 | 1275.732
1639 | 1522.428 | 1275.693
1640 | 1522.4 | 1275.392
1641 | 1522.3454 | 1275.2
1642 | 1522.0625 | 1275.021
1643 | 1521.983 | 1274.956
1644 | 1521.9814 | 1274.827
1645 | 1521.9814 | 1274.656
1646 | 1521.9772 | 1274.4
1647 | 1521.6 | 1274.4
1648 | 1521.6 | 1274.4
1649 | 1521.6 | 1274.4
1650 | 1521.1636 | 1274.312
1651 | 1520.8 | 1274.142
1652 | 1520.7915 | 1274.126
1653 | 1520.4757 | 1273.361
1654 | 1520.337 | 1272.8
1655 | 1520.142 | 1272.8
1656 | 1520.027 | 1272.8
1657 | 1519.8933 | 1272.45
1658 | 1519.876 | 1272.11
1659 | 1519.6659 | 1272
1660 | 1519.5135 | 1272
1661 | 1519.235 | 1271.2
1662 | 1519.2 | 1270.908
1663 | 1519.172 | 1270.858
1664 | 1519.101 | 1270.4
1665 | 1518.9141 | 1270.4
1666 | 1518.9095 | 1270.294
1667 | 1518.8139 | 1270.243
1668 | 1518.8139 | 1269.443
1669 | 1518.7101 | 1268.8
1670 | 1518.4 | 1268.8
1671 | 1518.4 | 1268.8
1672 | 1518.4 | 1268.8
1673 | 1517.919 | 1268.772
1674 | 1517.8449 | 1268.767
1675 | 1517.6 | 1268.748
1676 | 1517.6 | 1268.167
1677 | 1517.6 | 1268.157
1678 | 1517.3603 | 1268
1679 | 1517.328 | 1268
1680 | 1517.155 | 1267.963
1681 | 1517.038 | 1267.674
1682 | 1516.8 | 1267.2
1683 | 1516.8 | 1267.2
1684 | 1516.4783 | 1267.052
1685 | 1516.32 | 1267.052
1686 | 1516 | 1266.409
1687 | 1515.751 | 1266.409
1688 | 1515.3156 | 1266.4
1689 | 1515.2 | 1266.4
1690 | 1515.2 | 1266.4
1691 | 1515.2 | 1266.126
1692 | 1515.135 | 1265.991
1693 | 1514.83 | 1265.6
1694 | 1514.752 | 1265.6
1695 | 1514.737 | 1265.459
1696 | 1514.4 | 1265.326
1697 | 1514.4 | 1264.8
1698 | 1514.373 | 1264.8
1699 | 1514.242 | 1264.8
1700 | 1514.182 | 1264
1701 | 1513.8031 | 1263.865
1702 | 1513.6533 | 1263.865
1703 | 1513.4915 | 1263.865
1704 | 1513.4756 | 1263.261
1705 | 1513.323 | 1263.2
1706 | 1512.8 | 1263.173
1707 | 1512.8 | 1262.525
1708 | 1512.8 | 1262.525
1709 | 1512.8 | 1262.4
1710 | 1512.557 | 1262.4
1711 | 1512.4939 | 1262.152
1712 | 1512.119 | 1262.126
1713 | 1512.0147 | 1261.142
1714 | 1511.9217 | 1260.677
1715 | 1511.5332 | 1260.526
1716 | 1511.5071 | 1260.276
1717 | 1511.408 | 1260.271
1718 | 1511.2516 | 1260.07
1719 | 1510.972 | 1260
1720 | 1510.8356 | 1260
1721 | 1510.7833 | 1260
1722 | 1510.4219 | 1259.807
1723 | 1510.4 | 1259.489
1724 | 1510.4 | 1259.21
1725 | 1510.3678 | 1259.117
1726 | 1510.044 | 1258.926
1727 | 1509.998 | 1258.426
1728 | 1509.994 | 1258.426
1729 | 1509.8552 | 1258.4
1730 | 1509.6793 | 1258.077
1731 | 1509.6 | 1257.822
1732 | 1509.5909 | 1257.673
1733 | 1509.5909 | 1257.6
1734 | 1509.5259 | 1257.49
1735 | 1509.416 | 1257.345
1736 | 1509.3432 | 1257.086
1737 | 1509.312 | 1257.086
1738 | 1509.175 | 1257.027
1739 | 1509.1443 | 1257.004
1740 | 1508.8 | 1256.8
1741 | 1508.661 | 1256.8
1742 | 1508.577 | 1256.268
1743 | 1508.5094 | 1256.268
1744 | 1508.333 | 1256.268
1745 | 1508 | 1256
1746 | 1508 | 1256
1747 | 1508 | 1255.837
1748 | 1508 | 1255.666
1749 | 1507.763 | 1255.652
1750 | 1507.2 | 1255.533
1751 | 1507.155 | 1255.382
1752 | 1507.149 | 1255.099
1753 | 1506.995 | 1254.973
1754 | 1506.9156 | 1254.973
1755 | 1506.879 | 1254.623
1756 | 1506.7813 | 1254.4
1757 | 1506.4 | 1254.4
1758 | 1506.384 | 1254.4
1759 | 1506.159 | 1254.291
1760 | 1505.9819 | 1254.271
1761 | 1505.7062 | 1253.158
1762 | 1505.6 | 1252.915
1763 | 1505.134 | 1252.8
1764 | 1505.096 | 1252.8
1765 | 1504.309 | 1252.8
1766 | 1504 | 1252.591
1767 | 1504 | 1251.519
1768 | 1504 | 1251.519
1769 | 1504 | 1251.519
1770 | 1503.829 | 1251.2
1771 | 1503.6577 | 1251.12
1772 | 1503.542 | 1251.115
1773 | 1503.503 | 1250.926
1774 | 1503.303 | 1250.788
1775 | 1503.2 | 1250.547
1776 | 1503.2 | 1250.462
1777 | 1503.1713 | 1250.4
1778 | 1503.1713 | 1250.4
1779 | 1503.121 | 1249.6
1780 | 1502.9147 | 1248.913
1781 | 1502.4 | 1248.913
1782 | 1502.098 | 1248.8
1783 | 1502.036 | 1248.8
1784 | 1502.032 | 1248.8
1785 | 1501.8804 | 1248.8
1786 | 1501.8215 | 1248.8
1787 | 1501.802 | 1248.526
1788 | 1501.38 | 1248.455
1789 | 1501.2835 | 1248.039
1790 | 1500.8 | 1248.008
1791 | 1500.8 | 1248
1792 | 1500.5405 | 1248
1793 | 1500.2676 | 1248
1794 | 1500.0918 | 1247.726
1795 | 1500.064 | 1247.726
1796 | 1500 | 1247.2
1797 | 1500 | 1247.191
1798 | 1500 | 1246.986
1799 | 1499.82 | 1246.4
1800 | 1499.779 | 1246.373
1801 | 1499.733 | 1245.725
1802 | 1499.6906 | 1245.6
1803 | 1499.2 | 1245.6
1804 | 1499.0822 | 1244.8
1805 | 1498.899 | 1244.8
1806 | 1498.823 | 1244.739
1807 | 1498.7138 | 1244.526
1808 | 1498.4 | 1244.275
1809 | 1498.2644 | 1244.187
1810 | 1498.248 | 1243.943
1811 | 1497.729 | 1243.943
1812 | 1497.656 | 1243.943
1813 | 1497.6 | 1243.2
1814 | 1497.6 | 1243.029
1815 | 1497.6 | 1242.926
1816 | 1497.593 | 1242.4
1817 | 1497.353 | 1242.349
1818 | 1497.263 | 1241.6
1819 | 1497.0151 | 1240.8
1820 | 1496.8 | 1240.77
1821 | 1496.668 | 1240.77
1822 | 1496.6287 | 1240.54
1823 | 1496.27 | 1240.087
1824 | 1496.2674 | 1240
1825 | 1496 | 1240
1826 | 1495.9604 | 1239.336
1827 | 1495.2 | 1239.2
1828 | 1495.022 | 1239.2
1829 | 1494.969 | 1239.2
1830 | 1494.9623 | 1238.616
1831 | 1494.8291 | 1238.439
1832 | 1494.782 | 1238.4
1833 | 1494.729 | 1238.391
1834 | 1494.49 | 1238.281
1835 | 1494.4 | 1238.194
1836 | 1494.4 | 1238.137
1837 | 1494.4 | 1238.126
1838 | 1494.4 | 1237.903
1839 | 1494.4 | 1237.796
1840 | 1494.3067 | 1237.706
1841 | 1494.1654 | 1237.706
1842 | 1494.1654 | 1237.567
1843 | 1494.0026 | 1237.145
1844 | 1494.002 | 1237.145
1845 | 1493.8665 | 1236.8
1846 | 1493.831 | 1236.8
1847 | 1493.7656 | 1236.409
1848 | 1493.6 | 1236.324
1849 | 1493.6 | 1236.109
1850 | 1493.401 | 1235.969
1851 | 1493.3574 | 1235.2
1852 | 1493.2586 | 1235.077
1853 | 1493.2053 | 1234.4
1854 | 1493.196 | 1234.4
1855 | 1493.1455 | 1233.6
1856 | 1493.09 | 1233.6
1857 | 1493.0687 | 1233.467
1858 | 1493.053 | 1233.467
1859 | 1493.014 | 1233.287
1860 | 1492.8 | 1233.287
1861 | 1492.56 | 1233.262
1862 | 1492.5396 | 1233.143
1863 | 1492.397 | 1233.09
1864 | 1492.2516 | 1232.871
1865 | 1492.205 | 1232.8
1866 | 1492.134 | 1232.8
1867 | 1492 | 1232.409
1868 | 1492 | 1232.408
1869 | 1491.985 | 1232.224
1870 | 1491.966 | 1232.18
1871 | 1491.899 | 1232
1872 | 1491.7748 | 1232
1873 | 1491.7217 | 1231.447
1874 | 1491.7217 | 1231.319
1875 | 1491.7213 | 1230.799
1876 | 1491.7106 | 1230.799
1877 | 1491.6931 | 1230.764
1878 | 1491.5815 | 1230.67
1879 | 1491.3363 | 1230.493
1880 | 1491.287 | 1230.4
1881 | 1491.2 | 1230.4
1882 | 1490.9918 | 1230.4
1883 | 1490.9597 | 1230.108
1884 | 1490.5497 | 1229.933
1885 | 1490.4715 | 1229.6
1886 | 1490.436 | 1229.599
1887 | 1490.4 | 1229.417
1888 | 1490.4 | 1229.197
1889 | 1490.238 | 1229.116
1890 | 1490.1674 | 1228.8
1891 | 1490.1332 | 1228.38
1892 | 1489.7845 | 1228.38
1893 | 1489.6 | 1228.318
1894 | 1489.5089 | 1228
1895 | 1489.3905 | 1227.345
1896 | 1489.362 | 1227.2
1897 | 1489.1425 | 1227.105
1898 | 1489.129 | 1226.934
1899 | 1488.8 | 1226.847
1900 | 1488.8 | 1226.823
1901 | 1488.8 | 1226.4
1902 | 1488.8 | 1226.4
1903 | 1488.8 | 1226.4
1904 | 1488.8 | 1226.4
1905 | 1488.651 | 1226.4
1906 | 1488.6136 | 1226.128
1907 | 1488.5872 | 1226.126
1908 | 1488.4238 | 1226.008
1909 | 1488.288 | 1225.6
1910 | 1488.271 | 1225.6
1911 | 1488.1212 | 1225.6
1912 | 1488 | 1225.376
1913 | 1488 | 1225.375
1914 | 1488 | 1225.273
1915 | 1487.9546 | 1225.22
1916 | 1487.923 | 1225.027
1917 | 1487.855 | 1224.801
1918 | 1487.8366 | 1224.8
1919 | 1487.795 | 1224.798
1920 | 1487.5921 | 1223.726
1921 | 1487.386 | 1223.726
1922 | 1487.273 | 1223.2
1923 | 1486.7248 | 1223.2
1924 | 1486.483 | 1223.2
1925 | 1486.419 | 1222.834
1926 | 1486.3518 | 1222.564
1927 | 1486.331 | 1222.511
1928 | 1485.876 | 1222.506
1929 | 1485.795 | 1222.4
1930 | 1485.6 | 1222.4
1931 | 1485.5058 | 1222.4
1932 | 1485.5058 | 1222.4
1933 | 1485.364 | 1222.348
1934 | 1485.342 | 1222.124
1935 | 1484.496 | 1222.121
1936 | 1484.2371 | 1221.838
1937 | 1484.153 | 1221.699
1938 | 1484 | 1221.63
1939 | 1484 | 1221.6
1940 | 1483.656 | 1221.129
1941 | 1483.589 | 1221.015
1942 | 1483.2 | 1220.833
1943 | 1483.2 | 1220.8
1944 | 1483.009 | 1220.8
1945 | 1483.009 | 1220.57
1946 | 1482.886 | 1220.036
1947 | 1482.4 | 1220
1948 | 1482.2121 | 1220
1949 | 1482.151 | 1220
1950 | 1482.0911 | 1220
1951 | 1481.714 | 1219.726
1952 | 1481.469 | 1219.547
1953 | 1481.371 | 1219.2
1954 | 1480.9778 | 1219.2
1955 | 1480.8333 | 1218.757
1956 | 1480.8 | 1218.567
1957 | 1480.8 | 1218.4
1958 | 1480.787 | 1218.239
1959 | 1480.775 | 1218.021
1960 | 1480.7011 | 1217.706
1961 | 1480.6329 | 1217.6
1962 | 1480.4755 | 1217.6
1963 | 1480.0672 | 1217.286
1964 | 1479.7011 | 1217.286
1965 | 1479.6564 | 1217.117
1966 | 1479.4543 | 1216.912
1967 | 1479.406 | 1216.848
1968 | 1479.2732 | 1216.8
1969 | 1479.2 | 1216.685
1970 | 1479.2 | 1216.294
1971 | 1479.054 | 1216.294
1972 | 1478.554 | 1216
1973 | 1478.4 | 1216
1974 | 1478.389 | 1216
1975 | 1478.2277 | 1215.604
1976 | 1478.101 | 1215.295
1977 | 1477.914 | 1215.2
1978 | 1477.846 | 1215.131
1979 | 1477.6 | 1215.079
1980 | 1477.6 | 1214.4
1981 | 1477.577 | 1214.4
1982 | 1476.9595 | 1214.354
1983 | 1476.872 | 1214.131
1984 | 1476.864 | 1213.792
1985 | 1476.806 | 1213.608
1986 | 1476.6339 | 1213.6
1987 | 1476.616 | 1213.6
1988 | 1476.183 | 1212.841
1989 | 1476 | 1212.8
1990 | 1476 | 1212.8
1991 | 1475.707 | 1212.669
1992 | 1475.6089 | 1212.067
1993 | 1475.4056 | 1212
1994 | 1475.2 | 1212
1995 | 1475.2 | 1211.742
1996 | 1475.2 | 1211.739
1997 | 1475.0421 | 1211.675
1998 | 1475.0401 | 1211.2
1999 | 1474.906 | 1211.2
2000 | 1474.877 | 1211.2
2001 | 1474.584 | 1211.2
2002 | 1474.4 | 1210.926
2003 | 1474.147 | 1210.769
2004 | 1473.9411 | 1210.666
2005 | 1473.887 | 1210.4
2006 | 1473.8341 | 1210.4
2007 | 1473.5876 | 1209.867
2008 | 1473.3059 | 1209.693
2009 | 1473.083 | 1209.195
2010 | 1472.9116 | 1208.916
2011 | 1472.893 | 1208.8
2012 | 1472.8 | 1208.778
2013 | 1472.8 | 1208.753
2014 | 1472.679 | 1208.67
2015 | 1472.454 | 1208.553
2016 | 1472.409 | 1208.526
2017 | 1472 | 1208.424
2018 | 1472 | 1208.083
2019 | 1472 | 1207.724
2020 | 1472 | 1207.315
2021 | 1471.9558 | 1207.2
2022 | 1471.92 | 1207.2
2023 | 1471.9052 | 1207.2
2024 | 1471.8526 | 1207.2
2025 | 1471.8474 | 1207.103
2026 | 1471.833 | 1206.988
2027 | 1471.768 | 1206.489
2028 | 1471.2 | 1206.489
2029 | 1471.2 | 1206.486
2030 | 1471.04 | 1206.4
2031 | 1470.638 | 1206.4
2032 | 1470.4 | 1206.4
2033 | 1470.4 | 1206.253
2034 | 1470.4 | 1205.906
2035 | 1470.4 | 1205.692
2036 | 1470.4 | 1205.6
2037 | 1470.3045 | 1205.541
2038 | 1470.149 | 1205.397
2039 | 1470.106 | 1204.8
2040 | 1469.7754 | 1204.8
2041 | 1469.7754 | 1204.8
2042 | 1469.6 | 1204.782
2043 | 1469.6 | 1204.716
2044 | 1469.4619 | 1204.663
2045 | 1469.4619 | 1204
2046 | 1469.4209 | 1204
2047 | 1469.341 | 1204
2048 | 1469.1901 | 1203.862
2049 | 1468.8335 | 1203.717
2050 | 1468.8 | 1203.477
2051 | 1468.701 | 1203.477
2052 | 1468.257 | 1203.028
2053 | 1468.154 | 1202.504
2054 | 1468.113 | 1202.4
2055 | 1468.0047 | 1202.4
2056 | 1468 | 1202.277
2057 | 1467.4236 | 1201.79
2058 | 1467.39 | 1201.79
2059 | 1467.239 | 1201.6
2060 | 1467.2 | 1201.6
2061 | 1467.0712 | 1201.146
2062 | 1466.806 | 1200.8
2063 | 1466.4 | 1200.8
2064 | 1466.4 | 1200.8
2065 | 1466.4 | 1200.8
2066 | 1466.4 | 1200.409
2067 | 1466.369 | 1200.369
2068 | 1466.2743 | 1200.114
2069 | 1466.1104 | 1200
2070 | 1466.0823 | 1199.833
2071 | 1465.9979 | 1199.633
2072 | 1465.832 | 1199.593
2073 | 1465.729 | 1199.474
2074 | 1465.6696 | 1199.317
2075 | 1465.6 | 1199.317
2076 | 1465.6 | 1199.2
2077 | 1465.4775 | 1199.2
2078 | 1465.448 | 1198.816
2079 | 1464.8 | 1198.42
2080 | 1464.7333 | 1198.4
2081 | 1464.687 | 1198.4
2082 | 1464.5285 | 1198.162
2083 | 1464.5285 | 1198.121
2084 | 1464.006 | 1198.039
2085 | 1464 | 1198.039
2086 | 1464 | 1197.262
2087 | 1463.9441 | 1196.907
2088 | 1463.8837 | 1196.8
2089 | 1463.7515 | 1196.8
2090 | 1463.702 | 1196.43
2091 | 1463.659 | 1196.129
2092 | 1463.2 | 1196
2093 | 1463.2 | 1196
2094 | 1463.2 | 1196
2095 | 1463.195 | 1195.667
2096 | 1462.838 | 1195.574
2097 | 1462.819 | 1195.574
2098 | 1462.4025 | 1195.22
2099 | 1462.4 | 1195.2
2100 | 1462.36 | 1195.2
2101 | 1462.071 | 1195.2
2102 | 1461.828 | 1194.958
2103 | 1461.6 | 1194.403
2104 | 1461.6 | 1194.4
2105 | 1461.4939 | 1194.4
2106 | 1461.4783 | 1194.4
2107 | 1461.462 | 1194.4
2108 | 1461.298 | 1194.359
2109 | 1461.244 | 1194.292
2110 | 1461.008 | 1193.739
2111 | 1460.9439 | 1193.6
2112 | 1460.8 | 1193.6
2113 | 1460.8 | 1193.382
2114 | 1460.6961 | 1193.214
2115 | 1460.6438 | 1192.825
2116 | 1460.39 | 1192.811
2117 | 1460.1058 | 1192.472
2118 | 1460 | 1192
2119 | 1460 | 1192
2120 | 1459.9884 | 1192
2121 | 1459.8264 | 1192
2122 | 1459.662 | 1191.835
2123 | 1459.4151 | 1191.823
2124 | 1459.2 | 1191.726
2125 | 1459.2 | 1191.158
2126 | 1459.2 | 1190.934
2127 | 1459.2 | 1190.112
2128 | 1459.2 | 1190.071
2129 | 1459.2 | 1189.754
2130 | 1459.2 | 1189.6
2131 | 1459.1023 | 1189.6
2132 | 1458.87 | 1189.6
2133 | 1458.823 | 1189.6
2134 | 1458.605 | 1189.6
2135 | 1458.486 | 1189.336
2136 | 1458.461 | 1189.249
2137 | 1458.4473 | 1189.089
2138 | 1458.4 | 1188.8
2139 | 1458.4 | 1188.667
2140 | 1458.3055 | 1188
2141 | 1458.236 | 1187.938
2142 | 1458.112 | 1187.865
2143 | 1457.6 | 1187.865
2144 | 1457.6 | 1187.726
2145 | 1457.6 | 1187.2
2146 | 1457.536 | 1187.129
2147 | 1457.5078 | 1186.947
2148 | 1457.42 | 1186.4
2149 | 1457.305 | 1186.394
2150 | 1457.0651 | 1185.904
2151 | 1456.8 | 1185.901
2152 | 1456.702 | 1185.808
2153 | 1456.677 | 1185.424
2154 | 1456.6718 | 1185.353
2155 | 1456.647 | 1185.214
2156 | 1456.594 | 1184.973
2157 | 1456.5445 | 1184.973
2158 | 1456.398 | 1184.973
2159 | 1456.248 | 1184.831
2160 | 1456.1419 | 1184.831
2161 | 1456.088 | 1184.831
2162 | 1456 | 1184.218
2163 | 1455.9617 | 1184.187
2164 | 1455.678 | 1184.187
2165 | 1455.5941 | 1184.063
2166 | 1455.515 | 1184.005
2167 | 1455.5 | 1184
2168 | 1455.483 | 1184
2169 | 1455.323 | 1183.452
2170 | 1454.847 | 1183.2
2171 | 1454.836 | 1183.2
2172 | 1454.312 | 1183.2
2173 | 1454.101 | 1182.926
2174 | 1453.973 | 1182.4
2175 | 1453.859 | 1182.4
2176 | 1453.632 | 1182.4
2177 | 1453.6 | 1182.126
2178 | 1453.6 | 1182.043
2179 | 1453.6 | 1181.981
2180 | 1453.2837 | 1181.981
2181 | 1453.1366 | 1181.76
2182 | 1453.0225 | 1181.6
2183 | 1452.7272 | 1181.182
2184 | 1452.682 | 1180.813
2185 | 1452.636 | 1180.8
2186 | 1452.169 | 1180.8
2187 | 1451.9165 | 1180.8
2188 | 1451.9165 | 1180.8
2189 | 1451.8731 | 1180.51
2190 | 1451.78 | 1180.51
2191 | 1451.75 | 1180.249
2192 | 1451.2 | 1180.048
2193 | 1450.922 | 1180
2194 | 1450.7679 | 1179.774
2195 | 1450.765 | 1179.632
2196 | 1450.762 | 1179.392
2197 | 1450.739 | 1179.2
2198 | 1450.6684 | 1179.2
2199 | 1450.4455 | 1179.2
2200 | 1450.0124 | 1179.2
2201 | 1449.6 | 1179.039
2202 | 1449.6 | 1178.997
2203 | 1449.6 | 1178.493
2204 | 1449.583 | 1178.4
2205 | 1449.3753 | 1178.4
2206 | 1449.081 | 1178.307
2207 | 1448.9237 | 1177.801
2208 | 1448.8 | 1177.616
2209 | 1448.8 | 1177.568
2210 | 1448.694 | 1177.488
2211 | 1448.549 | 1177.326
2212 | 1448.412 | 1177.061
2213 | 1448.2039 | 1176.811
2214 | 1448.199 | 1176.8
2215 | 1448.14 | 1176.8
2216 | 1447.9459 | 1176.8
2217 | 1447.708 | 1176.207
2218 | 1447.5589 | 1176.039
2219 | 1447.547 | 1175.793
2220 | 1447.357 | 1175.733
2221 | 1447.2 | 1175.2
2222 | 1447.2 | 1175.16
2223 | 1447.2 | 1174.613
2224 | 1446.565 | 1174.613
2225 | 1446.5205 | 1174.573
2226 | 1446.4 | 1173.954
2227 | 1446.4 | 1173.816
2228 | 1446.4 | 1173.6
2229 | 1446.4 | 1172.8
2230 | 1446.2015 | 1172.8
2231 | 1446.081 | 1172.602
2232 | 1445.9232 | 1172.559
2233 | 1445.882 | 1172.412
2234 | 1445.753 | 1172.4
2235 | 1445.6 | 1172.039
2236 | 1445.488 | 1172
2237 | 1445.428 | 1172
2238 | 1445.3682 | 1171.95
2239 | 1445.2968 | 1171.24
2240 | 1445.1054 | 1170.709
2241 | 1444.8 | 1170.629
2242 | 1444.8 | 1170.575
2243 | 1444.5613 | 1170.4
2244 | 1444 | 1170.212
2245 | 1444 | 1169.6
2246 | 1444 | 1169.6
2247 | 1444 | 1169.6
2248 | 1444 | 1168.8
2249 | 1444 | 1168.8
2250 | 1444 | 1168.053
2251 | 1443.7099 | 1168
2252 | 1443.6317 | 1168
2253 | 1443.606 | 1168
2254 | 1443.602 | 1167.2
2255 | 1443.5696 | 1167.2
2256 | 1443.5337 | 1167.2
2257 | 1443.4841 | 1167.038
2258 | 1443.3311 | 1166.976
2259 | 1443.0903 | 1166.973
2260 | 1443.0721 | 1166.476
2261 | 1443.0422 | 1166.4
2262 | 1442.884 | 1166.225
2263 | 1442.5236 | 1165.874
2264 | 1442.4 | 1165.874
2265 | 1441.9686 | 1165.6
2266 | 1441.807 | 1165.6
2267 | 1441.6 | 1165.064
2268 | 1441.5708 | 1164.8
2269 | 1441.5264 | 1164.8
2270 | 1441.2678 | 1164.328
2271 | 1441.0183 | 1164.328
2272 | 1440.8 | 1163.2
2273 | 1440.8 | 1163.2
2274 | 1440.8 | 1162.857
2275 | 1440.7739 | 1162.66
2276 | 1440.7666 | 1162.4
2277 | 1440.758 | 1162.3
2278 | 1440.601 | 1162.3
2279 | 1440.062 | 1162.122
2280 | 1440 | 1161.066
2281 | 1440 | 1160.8
2282 | 1439.8744 | 1160.784
2283 | 1439.865 | 1160.526
2284 | 1439.8057 | 1160.349
2285 | 1439.505 | 1160.269
2286 | 1439.2 | 1159.2
2287 | 1439.1789 | 1159.2
2288 | 1439.024 | 1158.86
2289 | 1438.896 | 1158.444
2290 | 1438.5628 | 1158.4
2291 | 1438.3833 | 1158.4
2292 | 1438.064 | 1158.387
2293 | 1438.053 | 1158.277
2294 | 1438.004 | 1158.277
2295 | 1437.9908 | 1157.729
2296 | 1437.913 | 1157.638
2297 | 1437.6 | 1157.6
2298 | 1437.172 | 1157.326
2299 | 1436.8198 | 1157.229
2300 | 1436.8 | 1156.896
2301 | 1436.8 | 1156.591
2302 | 1436.8 | 1156.445
2303 | 1436.7719 | 1156
2304 | 1436.7588 | 1156
2305 | 1436.5587 | 1155.725
2306 | 1436.5587 | 1155.502
2307 | 1436.28 | 1155.338
2308 | 1436.12 | 1155.2
2309 | 1436.091 | 1154.822
2310 | 1436 | 1154.776
2311 | 1436 | 1154.691
2312 | 1436 | 1154.383
2313 | 1436 | 1154.133
2314 | 1435.996 | 1154.133
2315 | 1435.98 | 1153.78
2316 | 1435.791 | 1153.6
2317 | 1435.7711 | 1152.976
2318 | 1435.638 | 1152.8
2319 | 1435.4445 | 1152.8
2320 | 1435.047 | 1152.8
2321 | 1435.033 | 1152.774
2322 | 1434.9975 | 1152
2323 | 1434.587 | 1152
2324 | 1434.4 | 1151.824
2325 | 1434.4 | 1151.824
2326 | 1434.3988 | 1150.4
2327 | 1434.3111 | 1150.4
2328 | 1434.2978 | 1149.667
2329 | 1434.29 | 1149.6
2330 | 1434.147 | 1149.6
2331 | 1434.101 | 1149.6
2332 | 1434.037 | 1148.438
2333 | 1433.9206 | 1148.27
2334 | 1433.6019 | 1148.147
2335 | 1433.6 | 1148.147
2336 | 1433.6 | 1148
2337 | 1433.6 | 1148
2338 | 1433.6 | 1147.917
2339 | 1433.6 | 1147.538
2340 | 1433.3713 | 1147.411
2341 | 1433.37 | 1147.38
2342 | 1433.2991 | 1147.2
2343 | 1432.8 | 1147.2
2344 | 1432.8 | 1147.2
2345 | 1432.8 | 1147.054
2346 | 1432.8 | 1146.4
2347 | 1432.0201 | 1146.127
2348 | 1432.0081 | 1145.6
2349 | 1432 | 1145.6
2350 | 1431.852 | 1145.326
2351 | 1431.814 | 1145.154
2352 | 1431.431 | 1144.8
2353 | 1431.3986 | 1144.8
2354 | 1431.2113 | 1144.463
2355 | 1431.2023 | 1144
2356 | 1431.2023 | 1143.659
2357 | 1431.2 | 1143.326
2358 | 1431.2 | 1143.31
2359 | 1431.18 | 1142.926
2360 | 1431.156 | 1142.4
2361 | 1430.954 | 1142.4
2362 | 1430.445 | 1142.4
2363 | 1430.4144 | 1142.4
2364 | 1430.4064 | 1142.353
2365 | 1430.4 | 1141.7
2366 | 1430.4 | 1141.6
2367 | 1430.203 | 1141.144
2368 | 1430.0072 | 1141.01
2369 | 1429.627 | 1141.01
2370 | 1429.6 | 1140.8
2371 | 1429.6 | 1140.526
2372 | 1429.6 | 1140.056
2373 | 1429.5663 | 1140
2374 | 1429.4651 | 1140
2375 | 1429.4511 | 1139.651
2376 | 1429.443 | 1139.423
2377 | 1429.3409 | 1139.32
2378 | 1429.183 | 1139.2
2379 | 1429.0673 | 1138.688
2380 | 1428.8 | 1138.419
2381 | 1428.7283 | 1138.4
2382 | 1428.5228 | 1138.247
2383 | 1428.3799 | 1138.126
2384 | 1428.0237 | 1138.126
2385 | 1428.0124 | 1137.956
2386 | 1428 | 1137.6
2387 | 1428 | 1137.114
2388 | 1428 | 1136.8
2389 | 1428 | 1136.61
2390 | 1428 | 1136.324
2391 | 1427.931 | 1136.175
2392 | 1427.898 | 1135.966
2393 | 1427.7269 | 1135.9
2394 | 1427.338 | 1135.566
2395 | 1427.2354 | 1135.2
2396 | 1427.2 | 1134.926
2397 | 1427.2 | 1134.769
2398 | 1427.1132 | 1134.33
2399 | 1426.651 | 1134.33
2400 | 1426.3624 | 1133.6
2401 | 1426.323 | 1133.6
2402 | 1426.2953 | 1133.412
2403 | 1426.2825 | 1133.326
2404 | 1426.2447 | 1133.168
2405 | 1425.846 | 1132.998
2406 | 1425.732 | 1132.8
2407 | 1425.6 | 1132.51
2408 | 1425.6 | 1132.464
2409 | 1425.4775 | 1132
2410 | 1425.4723 | 1132
2411 | 1425.388 | 1132
2412 | 1425.043 | 1132
2413 | 1424.9425 | 1131.482
2414 | 1424.881 | 1131.34
2415 | 1424.8 | 1131.2
2416 | 1424.8 | 1131.2
2417 | 1424.8 | 1131.2
2418 | 1424.6399 | 1130.926
2419 | 1424.522 | 1130.4
2420 | 1424.1277 | 1129.6
2421 | 1424.117 | 1129.561
2422 | 1424 | 1129.353
2423 | 1424 | 1128.8
2424 | 1423.9667 | 1128.8
2425 | 1423.8829 | 1128.8
2426 | 1423.8418 | 1128.763
2427 | 1423.6773 | 1128
2428 | 1423.45 | 1128
2429 | 1423.39 | 1127.787
2430 | 1423.3507 | 1127.728
2431 | 1423.2 | 1127.597
2432 | 1423.2 | 1127.552
2433 | 1423.2 | 1127.552
2434 | 1423.2 | 1127.462
2435 | 1422.7357 | 1127.2
2436 | 1422.6934 | 1127.2
2437 | 1422.593 | 1127.2
2438 | 1422.494 | 1127.2
2439 | 1422.415 | 1127.015
2440 | 1422.4 | 1126.97
2441 | 1422.4 | 1126.926
2442 | 1422.4 | 1126.926
2443 | 1421.989 | 1126.802
2444 | 1421.8944 | 1126.505
2445 | 1421.717 | 1126.505
2446 | 1421.665 | 1126.4
2447 | 1421.6486 | 1126.4
2448 | 1421.6 | 1125.815
2449 | 1421.6 | 1124.8
2450 | 1421.6 | 1124.789
2451 | 1421.245 | 1124.23
2452 | 1421.187 | 1124
2453 | 1421.0247 | 1123.875
2454 | 1421.0199 | 1123.875
2455 | 1421.0199 | 1123.875
2456 | 1420.868 | 1122.777
2457 | 1420.8 | 1122.711
2458 | 1420.6499 | 1122.676
2459 | 1420.356 | 1122.631
2460 | 1420.243 | 1122.506
2461 | 1420.2091 | 1122.404
2462 | 1420.1043 | 1122.4
2463 | 1420.083 | 1122.4
2464 | 1420 | 1122.171
2465 | 1420 | 1121.899
2466 | 1419.829 | 1121.6
2467 | 1419.609 | 1121.6
2468 | 1419.53 | 1121.6
2469 | 1419.4661 | 1121.6
2470 | 1419.2 | 1121.389
2471 | 1419.024 | 1121.24
2472 | 1419.01 | 1120.8
2473 | 1418.787 | 1120.197
2474 | 1418.6891 | 1120
2475 | 1418.6527 | 1120
2476 | 1418.5776 | 1119.86
2477 | 1418.435 | 1119.724
2478 | 1418.4 | 1119.461
2479 | 1418.0826 | 1119.461
2480 | 1418.0826 | 1119.2
2481 | 1417.9132 | 1119.162
2482 | 1417.6642 | 1118.926
2483 | 1417.562 | 1118.926
2484 | 1417.3471 | 1118.791
2485 | 1417.335 | 1118.58
2486 | 1417.2992 | 1118.4
2487 | 1417.2834 | 1118.4
2488 | 1417.1352 | 1118.4
2489 | 1417.1352 | 1118.4
2490 | 1416.8 | 1118.093
2491 | 1416.8 | 1118.034
2492 | 1416.8 | 1117.6
2493 | 1416.8 | 1117.527
2494 | 1416.4814 | 1117.285
2495 | 1416.4175 | 1117.237
2496 | 1416.264 | 1116.935
2497 | 1416.215 | 1116.921
2498 | 1416.2125 | 1116.46
2499 | 1416.1869 | 1116.444
2500 | 1416 | 1116.44
2501 | 1416 | 1115.644
2502 | 1416 | 1115.535
2503 | 1415.902 | 1115.396
2504 | 1415.791 | 1115.2
2505 | 1415.659 | 1115.2
2506 | 1415.654 | 1115.146
2507 | 1415.472 | 1114.906
2508 | 1415.4066 | 1114.746
2509 | 1415.3466 | 1114.4
2510 | 1415.2 | 1114.304
2511 | 1415.2 | 1114.129
2512 | 1414.8457 | 1114.073
2513 | 1414.8044 | 1114.073
2514 | 1414.8031 | 1114.05
2515 | 1414.7093 | 1114.05
2516 | 1414.405 | 1113.884
2517 | 1414.4 | 1113.6
2518 | 1414.4 | 1113.577
2519 | 1414.4 | 1113.554
2520 | 1414.2487 | 1113.253
2521 | 1414.2467 | 1113.066
2522 | 1413.981 | 1112.922
2523 | 1413.61 | 1112.8
2524 | 1413.6 | 1112.647
2525 | 1413.2101 | 1112.526
2526 | 1413.067 | 1112.467
2527 | 1412.9376 | 1112.001
2528 | 1412.897 | 1111.887
2529 | 1412.8828 | 1111.831
2530 | 1412.8 | 1111.473
2531 | 1412.8 | 1111.31
2532 | 1412.702 | 1111.2
2533 | 1412 | 1111.2
2534 | 1412 | 1111.2
2535 | 1411.917 | 1111.022
2536 | 1411.614 | 1110.926
2537 | 1411.611 | 1110.62
2538 | 1411.5744 | 1110.195
2539 | 1411.5744 | 1109.9
2540 | 1411.5744 | 1109.6
2541 | 1411.2891 | 1109.6
2542 | 1411.2 | 1109.6
2543 | 1411.2 | 1109.164
2544 | 1411.199 | 1108.972
2545 | 1411.0786 | 1108.8
2546 | 1411.0387 | 1108
2547 | 1410.943 | 1108
2548 | 1410.7274 | 1107.763
2549 | 1410.682 | 1107.662
2550 | 1410.488 | 1107.2
2551 | 1410.4 | 1107.009
2552 | 1410.3765 | 1106.878
2553 | 1410.31 | 1106.524
2554 | 1410.099 | 1106.524
2555 | 1409.846 | 1106.4
2556 | 1409.776 | 1106.126
2557 | 1409.71 | 1105.904
2558 | 1409.6953 | 1105.785
2559 | 1409.602 | 1105.701
2560 | 1409.6 | 1105.284
2561 | 1409.584 | 1105.284
2562 | 1409.4378 | 1105.094
2563 | 1409.196 | 1104.986
2564 | 1409.122 | 1104.806
2565 | 1408.9952 | 1104.016
2566 | 1408.8984 | 1104
2567 | 1408.803 | 1103.817
2568 | 1408.8 | 1103.652
2569 | 1408.8 | 1103.453
2570 | 1408.8 | 1103.2
2571 | 1408.691 | 1103.2
2572 | 1408.5208 | 1103.006
2573 | 1408.483 | 1102.475
2574 | 1408.437 | 1102.4
2575 | 1408.436 | 1102.4
2576 | 1408.139 | 1102.355
2577 | 1408.1145 | 1102.236
2578 | 1408.1115 | 1102.168
2579 | 1408.003 | 1102.126
2580 | 1408 | 1101.641
2581 | 1408 | 1101.6
2582 | 1408 | 1101.6
2583 | 1408 | 1101.6
2584 | 1408 | 1101.407
2585 | 1408 | 1100.259
2586 | 1408 | 1100
2587 | 1407.813 | 1100
2588 | 1407.738 | 1099.602
2589 | 1407.71 | 1098.909
2590 | 1407.4852 | 1098.878
2591 | 1407.3079 | 1098.867
2592 | 1407.2 | 1098.4
2593 | 1407.2 | 1097.396
2594 | 1407.2 | 1097.326
2595 | 1407.035 | 1096.71
2596 | 1407.007 | 1096.26
2597 | 1406.8437 | 1095.2
2598 | 1406.6674 | 1094.4
2599 | 1406.455 | 1094.128
2600 | 1405.725 | 1093.855
2601 | 1405.7108 | 1093.718
2602 | 1405.7098 | 1093.6
2603 | 1405.6574 | 1093.353
2604 | 1405.6336 | 1093.108
2605 | 1405.6 | 1092.8
2606 | 1405.495 | 1092.8
2607 | 1405.356 | 1092.621
2608 | 1404.929 | 1092.284
2609 | 1404.902 | 1092
2610 | 1404.8432 | 1092
2611 | 1404.829 | 1091.912
2612 | 1404.8 | 1091.726
2613 | 1404.8 | 1091.598
2614 | 1404.7042 | 1091.2
2615 | 1404.3944 | 1091.049
2616 | 1404.339 | 1090.926
2617 | 1404.316 | 1090.776
2618 | 1404.2924 | 1090.59
2619 | 1404.2291 | 1090.4
2620 | 1403.753 | 1090.4
2621 | 1403.535 | 1090.126
2622 | 1403.2 | 1089.6
2623 | 1403.2 | 1089.507
2624 | 1403.197 | 1089.267
2625 | 1403.1504 | 1088.8
2626 | 1403.041 | 1088.8
2627 | 1402.9586 | 1088.8
2628 | 1402.9448 | 1088.8
2629 | 1402.913 | 1088.8
2630 | 1402.659 | 1088.672
2631 | 1402.5233 | 1088.57
2632 | 1402.5233 | 1088.323
2633 | 1402.4 | 1088
2634 | 1402.4 | 1088
2635 | 1402.3734 | 1087.834
2636 | 1402.2623 | 1087.445
2637 | 1401.9869 | 1087.2
2638 | 1401.945 | 1086.566
2639 | 1401.7604 | 1086.4
2640 | 1401.7369 | 1085.925
2641 | 1401.676 | 1085.797
2642 | 1401.6253 | 1085.755
2643 | 1401.399 | 1085.6
2644 | 1401.019 | 1085.493
2645 | 1400.986 | 1084.892
2646 | 1400.8 | 1084.8
2647 | 1400.8 | 1084.8
2648 | 1400.707 | 1084.8
2649 | 1400.2571 | 1084.374
2650 | 1400.201 | 1084.09
2651 | 1400.192 | 1083.856
2652 | 1400.1248 | 1083.661
2653 | 1400.0426 | 1083.244
2654 | 1400 | 1083.2
2655 | 1400 | 1082.992
2656 | 1400 | 1082.752
2657 | 1399.92 | 1082.646
2658 | 1399.808 | 1082.4
2659 | 1399.7203 | 1082.4
2660 | 1399.4642 | 1082.144
2661 | 1399.3357 | 1082.126
2662 | 1399.3069 | 1081.973
2663 | 1398.5489 | 1081.377
2664 | 1398.4887 | 1081.235
2665 | 1398.4 | 1080.8
2666 | 1398.4 | 1080.8
2667 | 1398.4 | 1080.675
2668 | 1398.4 | 1080.58
2669 | 1398.008 | 1080.526
2670 | 1397.6 | 1080.526
2671 | 1397.6 | 1080
2672 | 1397.6 | 1079.591
2673 | 1397.5799 | 1078.987
2674 | 1397.4561 | 1078.848
2675 | 1397.369 | 1078.82
2676 | 1396.8 | 1078.4
2677 | 1396.8 | 1078.146
2678 | 1396.8 | 1078.126
2679 | 1396.8 | 1078.126
2680 | 1396.75 | 1077.647
2681 | 1396.2434 | 1077.6
2682 | 1396.16 | 1077.467
2683 | 1396 | 1076.8
2684 | 1396 | 1076.086
2685 | 1396 | 1076.059
2686 | 1395.96 | 1076
2687 | 1395.618 | 1076
2688 | 1395.5694 | 1076
2689 | 1395.4795 | 1075.33
2690 | 1395.381 | 1075.33
2691 | 1395.2815 | 1075.28
2692 | 1395.2 | 1075.2
2693 | 1395.2 | 1075.192
2694 | 1395.2 | 1074.926
2695 | 1395.182 | 1074.904
2696 | 1395.164 | 1074.595
2697 | 1395.108 | 1074.126
2698 | 1394.876 | 1074.024
2699 | 1394.604 | 1073.61
2700 | 1394.5459 | 1073.6
2701 | 1394.5459 | 1073.6
2702 | 1394.4908 | 1073.6
2703 | 1394.4 | 1073.6
2704 | 1394.4 | 1073.537
2705 | 1394.4 | 1073.408
2706 | 1394.4 | 1072.8
2707 | 1394.3683 | 1072.8
2708 | 1394.3631 | 1072.526
2709 | 1394.271 | 1072.319
2710 | 1394.1765 | 1071.835
2711 | 1394.158 | 1071.815
2712 | 1394.069 | 1071.653
2713 | 1393.933 | 1071.251
2714 | 1393.785 | 1071.227
2715 | 1393.734 | 1071.2
2716 | 1393.713 | 1071.2
2717 | 1393.6 | 1070.4
2718 | 1393.0749 | 1070.4
2719 | 1393.0749 | 1070.4
2720 | 1393.065 | 1070.214
2721 | 1392.8 | 1069.6
2722 | 1392.8 | 1069.446
2723 | 1392.7643 | 1069.424
2724 | 1392.7643 | 1069.424
2725 | 1392.659 | 1068.8
2726 | 1392.639 | 1068.711
2727 | 1392.377 | 1068.694
2728 | 1392.1637 | 1068.344
2729 | 1392.1637 | 1068.086
2730 | 1392.0499 | 1067.841
2731 | 1392 | 1067.374
2732 | 1392 | 1067.268
2733 | 1392 | 1067.24
2734 | 1392 | 1067.2
2735 | 1392 | 1066.671
2736 | 1391.9465 | 1066.4
2737 | 1391.9465 | 1066.236
2738 | 1391.9206 | 1065.6
2739 | 1391.7281 | 1064.8
2740 | 1391.679 | 1064.8
2741 | 1391.4963 | 1064.219
2742 | 1391.3668 | 1064
2743 | 1391.3668 | 1064
2744 | 1391.3492 | 1063.726
2745 | 1391.303 | 1062.926
2746 | 1391.249 | 1062.856
2747 | 1390.4 | 1062.574
2748 | 1390.1667 | 1062.327
2749 | 1389.6814 | 1061.855
2750 | 1389.6 | 1061.6
2751 | 1389.6 | 1061.581
2752 | 1389.518 | 1060.89
2753 | 1389.4705 | 1060.2
2754 | 1388.914 | 1059.884
2755 | 1388.834 | 1058.818
2756 | 1388.8 | 1058.399
2757 | 1388.8 | 1058.227
2758 | 1388.6752 | 1058.126
2759 | 1388.6465 | 1057.701
2760 | 1388.3885 | 1057.602
2761 | 1388.3388 | 1057.6
2762 | 1388 | 1057.6
2763 | 1388 | 1057.413
2764 | 1388 | 1056.979
2765 | 1387.7571 | 1056.526
2766 | 1387.754 | 1056
2767 | 1387.724 | 1056
2768 | 1387.644 | 1056
2769 | 1387.3227 | 1055.859
2770 | 1387.202 | 1055.365
2771 | 1387.2 | 1055.2
2772 | 1386.8347 | 1055.2
2773 | 1386.8347 | 1055.082
2774 | 1386.8347 | 1054.736
2775 | 1386.66 | 1054.736
2776 | 1386.5855 | 1054.4
2777 | 1386.4 | 1054.4
2778 | 1386.4 | 1053.6
2779 | 1386.4 | 1052.882
2780 | 1386.4 | 1052.144
2781 | 1386.2658 | 1052
2782 | 1386.1353 | 1051.726
2783 | 1386.057 | 1051.227
2784 | 1385.6 | 1051.224
2785 | 1385.6 | 1051.2
2786 | 1385.46 | 1051.2
2787 | 1385.337 | 1051.2
2788 | 1384.9171 | 1050.911
2789 | 1384.8 | 1050.665
2790 | 1384.8 | 1050.473
2791 | 1384.8 | 1050.323
2792 | 1384.773 | 1050.323
2793 | 1384.7712 | 1050.323
2794 | 1384.7626 | 1050.126
2795 | 1384.49 | 1049.84
2796 | 1384.2118 | 1049.6
2797 | 1384.1314 | 1049.276
2798 | 1384.068 | 1049.211
2799 | 1384.0595 | 1048.984
2800 | 1384 | 1048.116
2801 | 1384 | 1048
2802 | 1384 | 1047.767
2803 | 1383.5979 | 1047.767
2804 | 1383.572 | 1047.726
2805 | 1383.4399 | 1047.342
2806 | 1383.414 | 1047.299
2807 | 1383.408 | 1047.2
2808 | 1383.398 | 1046.931
2809 | 1383.033 | 1046.877
2810 | 1382.822 | 1046.763
2811 | 1382.7776 | 1046.485
2812 | 1382.406 | 1046.446
2813 | 1382.4 | 1046.4
2814 | 1382.4 | 1046.126
2815 | 1382.264 | 1045.775
2816 | 1382.173 | 1045.759
2817 | 1382.135 | 1045.717
2818 | 1381.943 | 1045.6
2819 | 1381.8306 | 1045.6
2820 | 1381.741 | 1045.174
2821 | 1381.6 | 1045.084
2822 | 1381.6 | 1044.8
2823 | 1381.448 | 1044
2824 | 1380.964 | 1044
2825 | 1380.935 | 1044
2826 | 1380.8 | 1043.726
2827 | 1380.8 | 1043.2
2828 | 1380.8 | 1042.813
2829 | 1380.768 | 1042.651
2830 | 1380.6823 | 1042.295
2831 | 1380.4794 | 1042.232
2832 | 1380.393 | 1042.129
2833 | 1380.315 | 1041.6
2834 | 1380.276 | 1041.496
2835 | 1380.2104 | 1041.291
2836 | 1380 | 1041.064
2837 | 1380 | 1040.8
2838 | 1379.9864 | 1040.56
2839 | 1379.821 | 1040.17
2840 | 1379.816 | 1040.17
2841 | 1379.6333 | 1040.025
2842 | 1379.589 | 1040.025
2843 | 1379.4135 | 1040.025
2844 | 1379.2 | 1040
2845 | 1379.1589 | 1039.653
2846 | 1379.1 | 1039.543
2847 | 1379.0653 | 1038.766
2848 | 1378.996 | 1038.098
2849 | 1378.71 | 1038.098
2850 | 1378.6088 | 1037.961
2851 | 1378.581 | 1037.819
2852 | 1378.4 | 1037.534
2853 | 1378.4 | 1037.331
2854 | 1378.1088 | 1036.927
2855 | 1378.0269 | 1036.8
2856 | 1377.861 | 1036.8
2857 | 1377.713 | 1036.717
2858 | 1377.6534 | 1036.436
2859 | 1377.629 | 1036.348
2860 | 1377.6 | 1036.086
2861 | 1377.6 | 1035.612
2862 | 1377.594 | 1035.335
2863 | 1377.5454 | 1034.433
2864 | 1377.423 | 1034.4
2865 | 1377.2255 | 1034.374
2866 | 1376.8 | 1034.255
2867 | 1376.8 | 1034.234
2868 | 1376.8 | 1034.141
2869 | 1376.8 | 1034.126
2870 | 1376.6976 | 1034.118
2871 | 1376.542 | 1033.916
2872 | 1376.532 | 1033.743
2873 | 1376.376 | 1033.407
2874 | 1376.3664 | 1033.349
2875 | 1376.1579 | 1033.328
2876 | 1376 | 1032.919
2877 | 1376 | 1032.791
2878 | 1376 | 1032.582
2879 | 1375.817 | 1032.572
2880 | 1375.5899 | 1032
2881 | 1375.523 | 1031.935
2882 | 1375.3968 | 1031.882
2883 | 1375.315 | 1031.459
2884 | 1375.2 | 1031.2
2885 | 1375.2 | 1031.199
2886 | 1375.182 | 1031.191
2887 | 1375.012 | 1031.191
2888 | 1374.738 | 1030.5
2889 | 1374.694 | 1030.4
2890 | 1374.539 | 1029.964
2891 | 1374.5232 | 1029.326
2892 | 1374.39 | 1029.259
2893 | 1374.2539 | 1029.119
2894 | 1373.6 | 1029.119
2895 | 1373.6 | 1028.83
2896 | 1373.544 | 1028.825
2897 | 1373.2187 | 1028.8
2898 | 1373.1364 | 1028.257
2899 | 1372.937 | 1028
2900 | 1372.877 | 1028
2901 | 1372.872 | 1027.986
2902 | 1372.8 | 1027.836
2903 | 1372.8 | 1027.584
2904 | 1372.623 | 1027.567
2905 | 1372.3889 | 1027.146
2906 | 1372.3889 | 1027.005
2907 | 1372.3541 | 1026.869
2908 | 1372.328 | 1026.42
2909 | 1372.2356 | 1026.4
2910 | 1372 | 1026.4
2911 | 1371.9495 | 1026.377
2912 | 1371.928 | 1026.153
2913 | 1371.782 | 1026.126
2914 | 1371.7788 | 1025.315
2915 | 1371.731 | 1024.746
2916 | 1371.4446 | 1024.005
2917 | 1371.414 | 1024
2918 | 1371.2114 | 1023.947
2919 | 1371.2 | 1023.738
2920 | 1371.137 | 1023.374
2921 | 1371.0223 | 1023.254
2922 | 1370.921 | 1023.228
2923 | 1370.3069 | 1022.4
2924 | 1370.109 | 1022.314
2925 | 1369.8509 | 1022.287
2926 | 1369.757 | 1022.212
2927 | 1369.6 | 1021.637
2928 | 1369.6 | 1021.6
2929 | 1369.6 | 1021.6
2930 | 1369.5383 | 1021.578
2931 | 1368.8 | 1021.521
2932 | 1368.8 | 1020.945
2933 | 1368.8 | 1020.897
2934 | 1368.8 | 1020.897
2935 | 1368.6657 | 1020.831
2936 | 1368.5727 | 1020.8
2937 | 1368.5009 | 1020.378
2938 | 1368.496 | 1020
2939 | 1368.332 | 1020
2940 | 1368.2571 | 1019.834
2941 | 1368.2013 | 1019.698
2942 | 1368.022 | 1019.449
2943 | 1368 | 1019.431
2944 | 1368 | 1019.2
2945 | 1367.8348 | 1019.2
2946 | 1367.5967 | 1018.695
2947 | 1367.56 | 1018.4
2948 | 1367.4141 | 1018.198
2949 | 1367.4116 | 1018.19
2950 | 1367.312 | 1018.068
2951 | 1367.211 | 1017.789
2952 | 1367.2 | 1016
2953 | 1367.2 | 1016
2954 | 1367.166 | 1016
2955 | 1367.1296 | 1015.996
2956 | 1366.848 | 1015.996
2957 | 1366.6633 | 1015.956
2958 | 1366.655 | 1015.159
2959 | 1366.6343 | 1015.018
2960 | 1366.6343 | 1014.926
2961 | 1366.4 | 1014.926
2962 | 1366.4 | 1014.714
2963 | 1366.4 | 1014.418
2964 | 1366.0648 | 1014.4
2965 | 1366.055 | 1013.904
2966 | 1365.6 | 1013.326
2967 | 1365.6 | 1013.233
2968 | 1365.6 | 1012.811
2969 | 1365.5684 | 1012.747
2970 | 1365.4821 | 1012.701
2971 | 1365.2484 | 1012.543
2972 | 1365.124 | 1012
2973 | 1365.056 | 1011.616
2974 | 1365.0331 | 1011.506
2975 | 1364.9581 | 1011.2
2976 | 1364.8 | 1010.939
2977 | 1364.8 | 1010.575
2978 | 1364.8 | 1010.471
2979 | 1364.7797 | 1010.4
2980 | 1364.7042 | 1010.015
2981 | 1364.2726 | 1009.89
2982 | 1364.1007 | 1009.6
2983 | 1364 | 1009.089
2984 | 1364 | 1008.8
2985 | 1363.969 | 1008.399
2986 | 1363.817 | 1008.399
2987 | 1363.693 | 1008
2988 | 1363.6541 | 1007.762
2989 | 1363.4758 | 1007.726
2990 | 1363.3224 | 1007.726
2991 | 1363.3224 | 1007.606
2992 | 1363.2866 | 1007.377
2993 | 1363.2 | 1007.251
2994 | 1362.6896 | 1007.2
2995 | 1362.6789 | 1007.2
2996 | 1362.5046 | 1007.152
2997 | 1362.4 | 1007.017
2998 | 1362.4 | 1006.927
2999 | 1362.4 | 1006.4
3000 | 1362.4 | 1005.636
3001 | 1362.4 | 1005.546
3002 | 1362.378 | 1004.72
3003 | 1362.282 | 1004.254
3004 | 1362.2406 | 1004
3005 | 1361.861 | 1003.985
3006 | 1361.769 | 1003.211
3007 | 1361.6 | 1001.473
3008 | 1361.6 | 1001.326
3009 | 1361.6 | 1001.128
3010 | 1361.6 | 1001.043
3011 | 1361.5313 | 1001.043
3012 | 1361.5307 | 1001.043
3013 | 1361.436 | 1000.696
3014 | 1361.4245 | 1000.53
3015 | 1361.338 | 1000.307
3016 | 1361.338 | 1000.11
3017 | 1361.037 | 1000
3018 | 1361.032 | 999.726
3019 | 1361.0005 | 999.2
3020 | 1360.959 | 998.126
3021 | 1360.953 | 997.6
3022 | 1360.939 | 996.886
3023 | 1360.8689 | 996.812
3024 | 1360.865 | 996.8
3025 | 1360.8 | 996.336
3026 | 1360.8 | 996.223
3027 | 1360.8 | 996.062
3028 | 1360.7414 | 996
3029 | 1360.73 | 995.498
3030 | 1360.6473 | 995.276
3031 | 1360.505 | 995.2
3032 | 1360.451 | 995.2
3033 | 1359.178 | 994.822
3034 | 1359.024 | 994.4
3035 | 1358.4 | 993.688
3036 | 1358.4 | 993.658
3037 | 1358.4 | 993.247
3038 | 1358.4 | 993.203
3039 | 1358.284 | 992.8
3040 | 1358.0879 | 992.526
3041 | 1358.071 | 992.402
3042 | 1357.844 | 992
3043 | 1357.8284 | 991.849
3044 | 1357.739 | 991.373
3045 | 1357.6 | 991.155
3046 | 1357.6 | 991.131
3047 | 1357.1939 | 990.836
3048 | 1357.1007 | 989.602
3049 | 1357.0867 | 989.283
3050 | 1357.077 | 989.274
3051 | 1356.959 | 989.274
3052 | 1356.8 | 988.89
3053 | 1356.8 | 988.8
3054 | 1356.8 | 988.8
3055 | 1356.489 | 988.642
3056 | 1356.354 | 988.369
3057 | 1356.3038 | 988.369
3058 | 1356.1404 | 987.476
3059 | 1356.1138 | 986.711
3060 | 1356 | 986.549
3061 | 1356 | 986.4
3062 | 1356 | 986.228
3063 | 1356 | 986.126
3064 | 1355.7571 | 985.788
3065 | 1355.743 | 985.606
3066 | 1355.7183 | 985.6
3067 | 1355.6593 | 985.6
3068 | 1355.634 | 984.8
3069 | 1355.5716 | 984.8
3070 | 1355.5069 | 984.8
3071 | 1355.5069 | 984.324
3072 | 1355.422 | 983.2
3073 | 1355.3308 | 982.843
3074 | 1355.19 | 982.843
3075 | 1355.1441 | 982.4
3076 | 1355.1218 | 982.126
3077 | 1354.983 | 981.6
3078 | 1354.9802 | 981.46
3079 | 1354.9627 | 981.396
3080 | 1354.9452 | 981.326
3081 | 1354.534 | 980.8
3082 | 1354.4 | 980.573
3083 | 1354.304 | 980.448
3084 | 1354.15 | 980.204
3085 | 1354.034 | 979.933
3086 | 1353.885 | 979.489
3087 | 1353.651 | 979.2
3088 | 1353.643 | 978.942
3089 | 1353.618 | 978.767
3090 | 1353.606 | 978.639
3091 | 1353.6 | 978.526
3092 | 1353.5085 | 978.4
3093 | 1353.4263 | 978.4
3094 | 1353.2033 | 978.165
3095 | 1353.1162 | 978.069
3096 | 1353.11 | 977.6
3097 | 1353.09 | 976.851
3098 | 1352.8 | 976.8
3099 | 1352.8 | 976.8
3100 | 1352.7826 | 976.8
3101 | 1352.7545 | 976.121
3102 | 1352.6494 | 976.062
3103 | 1352.587 | 976.035
3104 | 1352.5624 | 975.936
3105 | 1352.422 | 975.766
3106 | 1352.375 | 975.549
3107 | 1352.3591 | 975.2
3108 | 1352.3193 | 975.117
3109 | 1352.3193 | 975.084
3110 | 1352.296 | 974.926
3111 | 1352.2386 | 974.573
3112 | 1352 | 974.555
3113 | 1352 | 974.256
3114 | 1351.8858 | 974.126
3115 | 1351.8724 | 973.864
3116 | 1351.624 | 973.864
3117 | 1351.591 | 973.6
3118 | 1351.5224 | 973.326
3119 | 1351.25 | 973.174
3120 | 1351.2 | 973.174
3121 | 1351.2 | 973.174
3122 | 1351.1431 | 972.357
3123 | 1351.055 | 972.015
3124 | 1350.9121 | 972
3125 | 1350.4 | 971.807
3126 | 1350.4 | 971.793
3127 | 1350.4 | 971.2
3128 | 1350.4 | 970.886
3129 | 1350.247 | 970.768
3130 | 1350.2371 | 970.42
3131 | 1350.183 | 970.4
3132 | 1349.9434 | 970.254
3133 | 1349.7673 | 970.151
3134 | 1349.6792 | 969.464
3135 | 1349.631 | 969.119
3136 | 1349.6 | 968.978
3137 | 1349.218 | 968.526
3138 | 1349.1318 | 968.339
3139 | 1349.1184 | 968
3140 | 1349.0361 | 967.493
3141 | 1349.006 | 967.209
3142 | 1348.9437 | 967.2
3143 | 1348.873 | 966.957
3144 | 1348.8 | 966.511
3145 | 1348.8 | 966.267
3146 | 1348.8 | 966.144
3147 | 1348.658 | 965.966
3148 | 1348.064 | 965.439
3149 | 1348 | 965.326
3150 | 1347.911 | 965.025
3151 | 1347.852 | 964.8
3152 | 1347.8468 | 964.526
3153 | 1347.7837 | 964.211
3154 | 1347.642 | 963.906
3155 | 1347.5913 | 963.404
3156 | 1347.526 | 963.2
3157 | 1347.201 | 963.2
3158 | 1347.2 | 962.796
3159 | 1347.2 | 962.656
3160 | 1347.2 | 962.262
3161 | 1347.2 | 962.249
3162 | 1347.2 | 962.126
3163 | 1347.2 | 962.06
3164 | 1347.1615 | 961.6
3165 | 1347.1392 | 961.325
3166 | 1347.0834 | 960.8
3167 | 1346.8708 | 960.741
3168 | 1346.761 | 960.365
3169 | 1346.552 | 960
3170 | 1346.4339 | 960
3171 | 1346.4 | 959.854
3172 | 1346.4 | 958.99
3173 | 1346.221 | 958.492
3174 | 1345.6 | 957.94
3175 | 1345.6 | 957.6
3176 | 1345.6 | 957.6
3177 | 1345.6 | 956.912
3178 | 1345.6 | 956.861
3179 | 1345.6 | 956.176
3180 | 1345.557 | 956.176
3181 | 1345.486 | 956
3182 | 1345.155 | 955.981
3183 | 1345.1535 | 955.979
3184 | 1345.1473 | 955.97
3185 | 1345.1473 | 955.907
3186 | 1345.146 | 955.516
3187 | 1344.8 | 955.216
3188 | 1344.8 | 954.9
3189 | 1344.8 | 954.407
3190 | 1344.8 | 954.4
3191 | 1344.8 | 954.4
3192 | 1344.7616 | 953.6
3193 | 1344.335 | 953.094
3194 | 1344 | 953.003
3195 | 1344 | 952.883
3196 | 1343.987 | 952.526
3197 | 1343.3802 | 952.323
3198 | 1343.34 | 951.726
3199 | 1343.2 | 951.027
3200 | 1343.063 | 950.4
3201 | 1343.015 | 950.4
3202 | 1342.5492 | 950.4
3203 | 1342.539 | 949.69
3204 | 1342.5199 | 949.6
3205 | 1342.4171 | 949.6
3206 | 1342.0133 | 949.6
3207 | 1341.9598 | 949.6
3208 | 1341.9598 | 949.577
3209 | 1341.872 | 948.923
3210 | 1341.667 | 948.642
3211 | 1341.6 | 947.027
3212 | 1341.6 | 946.719
3213 | 1341.6 | 946.4
3214 | 1341.6 | 945.906
3215 | 1341.6 | 945.906
3216 | 1341.317 | 945.879
3217 | 1341.1629 | 945.145
3218 | 1341.1629 | 945.143
3219 | 1341.153 | 944.807
3220 | 1340.908 | 944.8
3221 | 1340.7248 | 944.165
3222 | 1340.366 | 943.98
3223 | 1340.366 | 943.474
3224 | 1340.192 | 943.2
3225 | 1340.07 | 943.2
3226 | 1340 | 942.426
3227 | 1340 | 942.4
3228 | 1340 | 942.4
3229 | 1339.573 | 942.4
3230 | 1339.5691 | 942.4
3231 | 1339.5691 | 941.402
3232 | 1339.569 | 940.833
3233 | 1339.387 | 940.811
3234 | 1339.324 | 940.526
3235 | 1339.2413 | 940
3236 | 1339.2361 | 939.33
3237 | 1339.1925 | 939.326
3238 | 1339.188 | 939.318
3239 | 1339.0123 | 939.259
3240 | 1338.908 | 939.2
3241 | 1338.8744 | 937.788
3242 | 1338.785 | 937.6
3243 | 1338.6645 | 937.6
3244 | 1338.6464 | 937.214
3245 | 1338.632 | 936.987
3246 | 1338.4 | 936.976
3247 | 1338.4 | 936
3248 | 1338.234 | 935.434
3249 | 1338.153 | 934.4
3250 | 1338.141 | 934.11
3251 | 1338.014 | 934.041
3252 | 1337.9229 | 933.765
3253 | 1337.8875 | 933.6
3254 | 1337.607 | 933.114
3255 | 1337.6 | 933.103
3256 | 1337.6 | 932.423
3257 | 1337.6 | 932
3258 | 1337.421 | 932
3259 | 1337.3169 | 931.789
3260 | 1337.162 | 931.141
3261 | 1337.062 | 931.042
3262 | 1336.8 | 929.67
3263 | 1336.8 | 929.471
3264 | 1336.7828 | 928.8
3265 | 1336.752 | 928.279
3266 | 1336.4734 | 928.068
3267 | 1336.4693 | 927.904
3268 | 1336.4483 | 927.2
3269 | 1336.3816 | 927.2
3270 | 1336 | 926.898
3271 | 1335.966 | 926.887
3272 | 1335.878 | 926.843
3273 | 1335.808 | 926.601
3274 | 1335.797 | 925.286
3275 | 1335.6922 | 924.966
3276 | 1335.484 | 924.884
3277 | 1335.2 | 924.234
3278 | 1335.2 | 924
3279 | 1335.156 | 923.2
3280 | 1335.092 | 923.2
3281 | 1335.092 | 923.003
3282 | 1334.6984 | 923.003
3283 | 1334.591 | 922.505
3284 | 1334.4 | 922.423
3285 | 1334.4 | 921.6
3286 | 1334.239 | 920.8
3287 | 1334.168 | 920.526
3288 | 1333.7106 | 920
3289 | 1333.6 | 919.991
3290 | 1333.6 | 919.796
3291 | 1333.6 | 919.3
3292 | 1333.194 | 918.664
3293 | 1333.0199 | 918.61
3294 | 1332.948 | 918.411
3295 | 1332.8 | 918.4
3296 | 1332.8 | 918.102
3297 | 1332.8 | 918.101
3298 | 1332.8 | 917.843
3299 | 1332.7466 | 917.605
3300 | 1332.407 | 917.6
3301 | 1332.3971 | 916.878
3302 | 1332.189 | 916.01
3303 | 1332.16 | 916
3304 | 1332.0267 | 915.459
3305 | 1332 | 915.357
3306 | 1331.8493 | 915.2
3307 | 1331.6386 | 914.935
3308 | 1331.5524 | 914.839
3309 | 1331.4271 | 914.334
3310 | 1331.4199 | 914.251
3311 | 1331.273 | 913.718
3312 | 1331.2 | 913.183
3313 | 1331.2 | 912.584
3314 | 1331.149 | 912.045
3315 | 1330.6818 | 912
3316 | 1330.5557 | 911.703
3317 | 1330.2779 | 911.703
3318 | 1330.2706 | 911.584
3319 | 1330.2572 | 911.515
3320 | 1329.9719 | 910.321
3321 | 1329.8202 | 910.126
3322 | 1329.8202 | 909.341
3323 | 1329.6 | 909.207
3324 | 1329.6 | 909.103
3325 | 1329.4033 | 908.8
3326 | 1329.2874 | 908.736
3327 | 1329.2253 | 908.47
3328 | 1329.0847 | 908.453
3329 | 1329.046 | 907.559
3330 | 1328.98 | 907.388
3331 | 1328.8758 | 907.2
3332 | 1328.8 | 906.4
3333 | 1328.8 | 906.4
3334 | 1328.616 | 906.186
3335 | 1328.5643 | 906.161
3336 | 1328.4127 | 906.161
3337 | 1328.349 | 906.126
3338 | 1328.345 | 906.121
3339 | 1328.1557 | 905.586
3340 | 1327.845 | 905.425
3341 | 1327.7543 | 904.8
3342 | 1327.615 | 904.454
3343 | 1327.6136 | 904.032
3344 | 1327.605 | 904
3345 | 1327.2 | 904
3346 | 1327.158 | 903.2
3347 | 1327.1344 | 902.962
3348 | 1327.1212 | 902.483
3349 | 1326.8189 | 901.759
3350 | 1326.775 | 901.6
3351 | 1326.4 | 901.054
3352 | 1326.4 | 900.751
3353 | 1326.022 | 900.166
3354 | 1325.832 | 899.687
3355 | 1325.723 | 899.541
3356 | 1325.7023 | 899.2
3357 | 1325.6 | 899.2
3358 | 1325.6 | 898.4
3359 | 1325.6 | 898.129
3360 | 1325.4565 | 898.07
3361 | 1324.926 | 897.837
3362 | 1324.8 | 897.326
3363 | 1324.8 | 896.587
3364 | 1324.8 | 896.424
3365 | 1324.6715 | 896.349
3366 | 1324.0666 | 896.223
3367 | 1324 | 896
3368 | 1324 | 895.517
3369 | 1324 | 895.252
3370 | 1324 | 895.126
3371 | 1324 | 895.126
3372 | 1324 | 895.033
3373 | 1323.9027 | 894.4
3374 | 1323.515 | 893.599
3375 | 1323.308 | 893.506
3376 | 1323.29 | 893.326
3377 | 1323.1257 | 893.148
3378 | 1322.503 | 893.11
3379 | 1322.4 | 893.024
3380 | 1322.0172 | 892.921
3381 | 1321.969 | 892.8
3382 | 1321.6131 | 892.8
3383 | 1321.611 | 892.463
3384 | 1321.6 | 891.925
3385 | 1321.6 | 891.83
3386 | 1321.6 | 891.153
3387 | 1321.6 | 890.4
3388 | 1321.3359 | 890.068
3389 | 1320.9939 | 889.337
3390 | 1320.8 | 889.27
3391 | 1320.8 | 888.43
3392 | 1320.8 | 888
3393 | 1320.7953 | 887.144
3394 | 1320.769 | 886.366
3395 | 1320.721 | 885.704
3396 | 1320.5876 | 885.625
3397 | 1320.5663 | 885.326
3398 | 1320.2584 | 884.959
3399 | 1320 | 884.928
3400 | 1319.2 | 884.242
3401 | 1319.2 | 884
3402 | 1319.1596 | 883.2
3403 | 1319.128 | 883.198
3404 | 1318.85 | 882.926
3405 | 1318.7874 | 882.694
3406 | 1318.43 | 882.624
3407 | 1318.4 | 881.089
3408 | 1318.4 | 880.8
3409 | 1318.4 | 880.622
3410 | 1318.0519 | 880
3411 | 1317.887 | 879.931
3412 | 1317.8249 | 879.895
3413 | 1317.8249 | 879.241
3414 | 1317.715 | 878.594
3415 | 1317.6872 | 878.4
3416 | 1317.571 | 878.304
3417 | 1317.507 | 877.6
3418 | 1317.272 | 877.6
3419 | 1317.246 | 877.19
3420 | 1317.153 | 876.8
3421 | 1316.9102 | 876.8
3422 | 1316.835 | 876.8
3423 | 1316.8 | 876.8
3424 | 1316.533 | 876.577
3425 | 1316 | 876.526
3426 | 1315.8883 | 875.787
3427 | 1315.8883 | 875.2
3428 | 1315.8453 | 875.072
3429 | 1315.8048 | 874.891
3430 | 1315.4865 | 874.609
3431 | 1315.4265 | 874.4
3432 | 1315.27 | 874.26
3433 | 1315.264 | 874.082
3434 | 1315.2 | 873.584
3435 | 1315.1216 | 873.062
3436 | 1315.1098 | 872.859
3437 | 1315.0705 | 872.559
3438 | 1314.638 | 872.332
3439 | 1314.6289 | 872.032
3440 | 1314.622 | 871.884
3441 | 1314.5969 | 871.643
3442 | 1314.4 | 871.349
3443 | 1314.3991 | 871.2
3444 | 1314.3743 | 870.958
3445 | 1314.233 | 870.547
3446 | 1314.143 | 870.268
3447 | 1314.0022 | 870.262
3448 | 1313.9909 | 869.6
3449 | 1313.727 | 869.385
3450 | 1313.6387 | 868.137
3451 | 1313.6 | 867.224
3452 | 1313.6 | 867.2
3453 | 1313.6 | 867.059
3454 | 1313.6 | 866.127
3455 | 1313.406 | 865.982
3456 | 1313.362 | 865.045
3457 | 1313.2718 | 864.908
3458 | 1313.251 | 864.861
3459 | 1313.0255 | 864.8
3460 | 1312.8 | 863.2
3461 | 1312.8 | 862.555
3462 | 1312.8 | 862.413
3463 | 1312.8 | 861.228
3464 | 1312.5904 | 860.8
3465 | 1312.509 | 860.8
3466 | 1312.456 | 860.592
3467 | 1312.2971 | 860.429
3468 | 1312.2486 | 859.726
3469 | 1312.2486 | 859.418
3470 | 1312 | 859.31
3471 | 1311.495 | 858.639
3472 | 1311.4301 | 858.501
3473 | 1311.2 | 858.445
3474 | 1311.2 | 857.797
3475 | 1310.4 | 857.086
3476 | 1310.4 | 856.607
3477 | 1310.4 | 856.244
3478 | 1310.4 | 856
3479 | 1310.1635 | 855.409
3480 | 1310.148 | 855.2
3481 | 1310.033 | 855.2
3482 | 1309.9178 | 854.4
3483 | 1309.9178 | 854.363
3484 | 1309.8432 | 853.681
3485 | 1309.7799 | 853.6
3486 | 1309.4418 | 852.8
3487 | 1309.39 | 852.082
3488 | 1309.361 | 852
3489 | 1309.2256 | 851.2
3490 | 1308.9971 | 851.022
3491 | 1308.846 | 850.869
3492 | 1308.643 | 850.4
3493 | 1308.586 | 850.202
3494 | 1308.4901 | 849.97
3495 | 1308.312 | 849.6
3496 | 1308.225 | 849.571
3497 | 1308 | 849.326
3498 | 1307.932 | 848.911
3499 | 1307.6936 | 848.851
3500 | 1307.693 | 848.79
3501 | 1307.476 | 848.16
3502 | 1307.3767 | 848
3503 | 1307.2764 | 847.63
3504 | 1307.2 | 847.272
3505 | 1306.7683 | 847.062
3506 | 1306.7255 | 846.488
3507 | 1306.374 | 846.456
3508 | 1306.2835 | 845.835
3509 | 1306.162 | 845.6
3510 | 1306.0833 | 844.324
3511 | 1306.039 | 843.2
3512 | 1306.0331 | 843.152
3513 | 1306.0331 | 841.871
3514 | 1305.6 | 841.6
3515 | 1305.6 | 841.6
3516 | 1305.6 | 840.8
3517 | 1305.6 | 840.743
3518 | 1305.548 | 840.562
3519 | 1305.53 | 840.526
3520 | 1305.495 | 840
3521 | 1305.477 | 839.726
3522 | 1305.359 | 839.639
3523 | 1305.329 | 839.202
3524 | 1305.3029 | 839.2
3525 | 1304.8 | 839.191
3526 | 1304.8 | 838.61
3527 | 1304.8 | 838.4
3528 | 1304.669 | 838.4
3529 | 1304.5051 | 836.64
3530 | 1304.4387 | 836
3531 | 1304 | 835.985
3532 | 1304 | 835.931
3533 | 1304 | 835.728
3534 | 1304 | 835.083
3535 | 1304 | 835.035
3536 | 1303.888 | 834.476
3537 | 1303.802 | 834.295
3538 | 1303.577 | 833.326
3539 | 1303.2 | 832.38
3540 | 1303.2 | 832.128
3541 | 1303.011 | 831.138
3542 | 1302.91 | 830.4
3543 | 1302.813 | 830.097
3544 | 1302.803 | 829.6
3545 | 1302.6298 | 829.6
3546 | 1302.6059 | 828.8
3547 | 1302.5098 | 828.8
3548 | 1302.4 | 828.526
3549 | 1302.3903 | 828.486
3550 | 1302.102 | 828.216
3551 | 1302.0681 | 828.003
3552 | 1301.9392 | 827.2
3553 | 1301.865 | 826.827
3554 | 1301.6783 | 826.749
3555 | 1301.609 | 826.584
3556 | 1301.431 | 826.4
3557 | 1301.2096 | 825.326
3558 | 1301.174 | 825.135
3559 | 1301.099 | 824.194
3560 | 1300.99 | 823.782
3561 | 1300.8 | 823.295
3562 | 1300.4519 | 822.782
3563 | 1300.328 | 822.712
3564 | 1300.3109 | 822.704
3565 | 1300.307 | 822.126
3566 | 1300.2516 | 821.681
3567 | 1300 | 821.21
3568 | 1300 | 820.926
3569 | 1300 | 820.8
3570 | 1300 | 820.532
3571 | 1300 | 820.204
3572 | 1300 | 820
3573 | 1299.8671 | 819.726
3574 | 1299.5317 | 819.346
3575 | 1299.5317 | 819.2
3576 | 1299.4648 | 818.634
3577 | 1299.258 | 818.4
3578 | 1299.2 | 818.377
3579 | 1299.2 | 817.646
3580 | 1299.188 | 817.391
3581 | 1299.0474 | 816.704
3582 | 1299.0406 | 816.517
3583 | 1298.9278 | 816.427
3584 | 1298.7306 | 816.364
3585 | 1298.4857 | 816
3586 | 1298.407 | 815.698
3587 | 1298.4 | 815.376
3588 | 1298.3816 | 815.376
3589 | 1298.1928 | 815.2
3590 | 1298.188 | 813.628
3591 | 1298.1309 | 813.626
3592 | 1297.88 | 813.626
3593 | 1297.7951 | 813.601
3594 | 1297.339 | 813.6
3595 | 1296.981 | 813.25
3596 | 1296.8027 | 812.991
3597 | 1296.8011 | 812.401
3598 | 1296.8 | 812.001
3599 | 1296.7098 | 812
3600 | 1296.6671 | 810.881
3601 | 1296.4209 | 810.296
3602 | 1296.3319 | 810.04
3603 | 1296.2238 | 809.482
3604 | 1296.1408 | 808.8
3605 | 1296.0874 | 808.125
3606 | 1295.9329 | 808.043
3607 | 1295.9295 | 808
3608 | 1295.9036 | 807.884
3609 | 1295.781 | 807.601
3610 | 1295.7403 | 807.479
3611 | 1295.2535 | 807.118
3612 | 1295.2 | 806.865
3613 | 1295.2 | 806.702
3614 | 1295.1505 | 806.13
3615 | 1295.145 | 805.724
3616 | 1294.5152 | 804.8
3617 | 1294.4 | 804.8
3618 | 1294.4 | 804.662
3619 | 1294.4 | 804.647
3620 | 1294.4 | 804.387
3621 | 1294.379 | 804
3622 | 1294.3433 | 803.629
3623 | 1294.28 | 803.266
3624 | 1294.1465 | 803.2
3625 | 1293.998 | 803.2
3626 | 1293.6 | 802.757
3627 | 1293.522 | 802.556
3628 | 1293.3496 | 802.291
3629 | 1293.304 | 800.503
3630 | 1293.095 | 799.709
3631 | 1293.0716 | 798.4
3632 | 1292.9603 | 797.74
3633 | 1292.903 | 797.608
3634 | 1292.8316 | 797.6
3635 | 1292.8 | 797.6
3636 | 1292.8 | 797.6
3637 | 1292.8 | 796.8
3638 | 1292.068 | 796.671
3639 | 1292 | 796.566
3640 | 1292 | 796
3641 | 1292 | 795.802
3642 | 1292 | 795.294
3643 | 1292 | 794.926
3644 | 1291.5998 | 793.549
3645 | 1291.2 | 792.93
3646 | 1291.1281 | 792.819
3647 | 1290.5356 | 792.601
3648 | 1290.4943 | 792
3649 | 1290.4 | 791.442
3650 | 1290.4 | 790.4
3651 | 1290.4 | 788.702
3652 | 1290.4 | 787.987
3653 | 1290.4 | 787.603
3654 | 1290.1975 | 787.452
3655 | 1290.1975 | 787.316
3656 | 1290.0993 | 787.109
3657 | 1289.5668 | 786.847
3658 | 1289.506 | 786.461
3659 | 1289.4335 | 786.306
3660 | 1289.3666 | 786.299
3661 | 1289.3435 | 785.828
3662 | 1289.3338 | 785.6
3663 | 1289.2178 | 785.535
3664 | 1288.8 | 785.235
3665 | 1288.8 | 785.146
3666 | 1288.7009 | 784.8
3667 | 1288.464 | 784.8
3668 | 1288.2412 | 784.8
3669 | 1288.141 | 784
3670 | 1288.1255 | 783.726
3671 | 1288.096 | 783.69
3672 | 1288.0652 | 783.2
3673 | 1288 | 782.593
3674 | 1288 | 782.545
3675 | 1288 | 781.136
3676 | 1288 | 780.957
3677 | 1287.992 | 780.608
3678 | 1287.915 | 780.473
3679 | 1287.7714 | 780
3680 | 1287.5099 | 779.881
3681 | 1287.4348 | 779.651
3682 | 1287.314 | 779.45
3683 | 1287.2 | 779.434
3684 | 1287.2 | 779.2
3685 | 1287.2 | 779.13
3686 | 1287.2 | 778.4
3687 | 1287.2 | 777.633
3688 | 1286.7441 | 777.6
3689 | 1286.664 | 776.121
3690 | 1286.6096 | 775.027
3691 | 1286.45 | 774.634
3692 | 1286.4464 | 774.4
3693 | 1286.429 | 773.972
3694 | 1286.4 | 772.717
3695 | 1286.4 | 772.296
3696 | 1286.4 | 772.026
3697 | 1286.247 | 771.322
3698 | 1285.8327 | 771.214
3699 | 1285.8327 | 770.803
3700 | 1285.689 | 770.803
3701 | 1285.6 | 770.505
3702 | 1285.6 | 770.212
3703 | 1285.6 | 770.133
3704 | 1285.579 | 769.6
3705 | 1285.3627 | 769.338
3706 | 1285.355 | 769.338
3707 | 1285.1606 | 769.326
3708 | 1284.5469 | 769.017
3709 | 1284.4951 | 768.029
3710 | 1284.4902 | 768
3711 | 1284.095 | 767.794
3712 | 1284.0444 | 766.986
3713 | 1284 | 766.926
3714 | 1284 | 766.126
3715 | 1284 | 766.126
3716 | 1283.8 | 765.6
3717 | 1283.7869 | 765.483
3718 | 1283.7711 | 764.993
3719 | 1283.758 | 764
3720 | 1283.562 | 763.244
3721 | 1283.4824 | 762.515
3722 | 1283.48 | 762.08
3723 | 1283.2 | 761.897
3724 | 1283.2 | 761.508
3725 | 1283.014 | 761.392
3726 | 1282.839 | 760.8
3727 | 1282.753 | 760.319
3728 | 1282.735 | 760
3729 | 1282.7249 | 759.792
3730 | 1282.4 | 759.2
3731 | 1282.3573 | 758.237
3732 | 1282.1932 | 758.227
3733 | 1282.017 | 758.128
3734 | 1282.0114 | 758.128
3735 | 1281.661 | 757.827
3736 | 1281.6469 | 757.348
3737 | 1281.6 | 756.99
3738 | 1281.582 | 756.99
3739 | 1281.294 | 755.887
3740 | 1281.246 | 755.2
3741 | 1281.053 | 755.2
3742 | 1280.998 | 755.2
3743 | 1280.894 | 754.922
3744 | 1280.8 | 754.857
3745 | 1280.8 | 754.4
3746 | 1280.8 | 754.4
3747 | 1280.783 | 753.6
3748 | 1280.5994 | 752.979
3749 | 1280.4233 | 752.8
3750 | 1280.109 | 752.485
3751 | 1280.093 | 752.155
3752 | 1280 | 751.2
3753 | 1280 | 750.836
3754 | 1280 | 750.805
3755 | 1279.819 | 750.288
3756 | 1279.8048 | 750.23
3757 | 1279.245 | 749.96
3758 | 1279.1002 | 749.163
3759 | 1278.8742 | 748.537
3760 | 1278.5809 | 748.526
3761 | 1278.412 | 748.514
3762 | 1278.2681 | 748.366
3763 | 1278.239 | 748.313
3764 | 1278.237 | 745.888
3765 | 1278.067 | 745.6
3766 | 1278.022 | 745.043
3767 | 1278.001 | 744.86
3768 | 1277.6 | 744.473
3769 | 1277.6 | 743.176
3770 | 1277.5983 | 743.092
3771 | 1277.595 | 742.126
3772 | 1277.5 | 741.772
3773 | 1277.059 | 741.6
3774 | 1276.9675 | 741.6
3775 | 1276.8627 | 741.6
3776 | 1276.8 | 741.241
3777 | 1276.6757 | 741.193
3778 | 1276.497 | 740.8
3779 | 1276.219 | 740.538
3780 | 1276.1272 | 739.372
3781 | 1276 | 739.318
3782 | 1276 | 739.032
3783 | 1276 | 738.4
3784 | 1275.9643 | 738.091
3785 | 1275.894 | 736.96
3786 | 1275.7325 | 736.781
3787 | 1275.6932 | 736
3788 | 1275.614 | 735.986
3789 | 1275.5441 | 735.2
3790 | 1275.3917 | 734.4
3791 | 1275.2 | 734.4
3792 | 1275.0212 | 733.864
3793 | 1274.9556 | 733.593
3794 | 1274.8271 | 733.55
3795 | 1274.6729 | 733.479
3796 | 1274.6562 | 732
3797 | 1274.438 | 732
3798 | 1274.4 | 730.053
3799 | 1274.4 | 729.003
3800 | 1274.4 | 728.8
3801 | 1274.4 | 728.8
3802 | 1274.4 | 728.671
3803 | 1274.4 | 728.35
3804 | 1274.3118 | 727.547
3805 | 1274.3118 | 727.2
3806 | 1274.12 | 726.4
3807 | 1274.013 | 726.052
3808 | 1273.679 | 725.6
3809 | 1273.643 | 724.597
3810 | 1273.3611 | 724.27
3811 | 1273.3423 | 723.883
3812 | 1273.22 | 723.845
3813 | 1272.8 | 723.207
3814 | 1272.8 | 723.2
3815 | 1272.8 | 721.6
3816 | 1272.8 | 721.272
3817 | 1272.5121 | 720.8
3818 | 1272.4496 | 720.607
3819 | 1272 | 720.263
3820 | 1272 | 717.6
3821 | 1271.929 | 717.154
3822 | 1271.7255 | 716.419
3823 | 1271.683 | 716.239
3824 | 1271.2 | 715.661
3825 | 1271.2 | 715.549
3826 | 1270.9311 | 714.957
3827 | 1270.9077 | 714.789
3828 | 1270.866 | 714.167
3829 | 1270.8584 | 713.976
3830 | 1270.7349 | 713.6
3831 | 1270.68 | 712
3832 | 1270.5584 | 711.983
3833 | 1270.539 | 711.072
3834 | 1270.4 | 710.926
3835 | 1270.4 | 710.882
3836 | 1270.4 | 709.937
3837 | 1270.4 | 708.8
3838 | 1270.332 | 708.8
3839 | 1270.2939 | 708.285
3840 | 1270.2431 | 708.198
3841 | 1270.1677 | 708.107
3842 | 1270.075 | 708
3843 | 1269.6825 | 707.721
3844 | 1269.4808 | 707.41
3845 | 1269.4781 | 707.041
3846 | 1269.4429 | 706.928
3847 | 1269.1333 | 706.499
3848 | 1268.8 | 706.099
3849 | 1268.8 | 705.6
3850 | 1268.8 | 705.1
3851 | 1268.8 | 704.969
3852 | 1268.772 | 704
3853 | 1268.6028 | 703.74
3854 | 1268.3941 | 702.934
3855 | 1268.221 | 702.926
3856 | 1268.157 | 702.003
3857 | 1268.07 | 701.641
3858 | 1268 | 701.041
3859 | 1268 | 700.81
3860 | 1268 | 700.8
3861 | 1267.9631 | 700.8
3862 | 1267.9631 | 700.665
3863 | 1267.883 | 700.526
3864 | 1267.674 | 700
3865 | 1267.651 | 699.708
3866 | 1267.6269 | 699.398
3867 | 1267.43 | 698.536
3868 | 1267.3981 | 697.565
3869 | 1267.2 | 696.761
3870 | 1267.2 | 695.977
3871 | 1267.0966 | 695.905
3872 | 1267.0523 | 695.598
3873 | 1267.0523 | 695.435
3874 | 1266.8185 | 694.642
3875 | 1266.559 | 694.4
3876 | 1266.465 | 694.051
3877 | 1266.4219 | 693.833
3878 | 1266.4092 | 692.702
3879 | 1266.4092 | 692.571
3880 | 1266.4 | 692.526
3881 | 1266.4 | 691.482
3882 | 1266.4 | 691.355
3883 | 1266.4 | 691.049
3884 | 1266.3005 | 689.6
3885 | 1265.9984 | 688.601
3886 | 1265.787 | 688.067
3887 | 1265.6 | 687.726
3888 | 1265.6 | 687.661
3889 | 1265.597 | 687.596
3890 | 1265.5835 | 686.784
3891 | 1265.572 | 686.707
3892 | 1265.5332 | 686.4
3893 | 1265.4585 | 685.983
3894 | 1265.2017 | 685.598
3895 | 1265.0944 | 684.911
3896 | 1264.8 | 684.863
3897 | 1264.8 | 683.623
3898 | 1264.8 | 682.665
3899 | 1264.732 | 682.583
3900 | 1264.5447 | 682.401
3901 | 1264.538 | 682.312
3902 | 1264.4646 | 682.301
3903 | 1264 | 682.184
3904 | 1263.9143 | 682.031
3905 | 1263.8647 | 681.192
3906 | 1263.8647 | 679.643
3907 | 1263.8647 | 678.988
3908 | 1263.6571 | 678.563
3909 | 1263.475 | 678.512
3910 | 1263.2609 | 677.6
3911 | 1263.257 | 677.041
3912 | 1263.2 | 676.473
3913 | 1262.5245 | 675.963
3914 | 1262.5245 | 675.207
3915 | 1262.4 | 674.819
3916 | 1262.4 | 674.4
3917 | 1262.4 | 674.241
3918 | 1262.2861 | 673.094
3919 | 1262.195 | 671.438
3920 | 1262.1523 | 670.4
3921 | 1262.025 | 669.6
3922 | 1261.7184 | 669.369
3923 | 1261.705 | 668.588
3924 | 1261.6 | 668.306
3925 | 1261.322 | 667.884
3926 | 1261.111 | 667.298
3927 | 1260.9775 | 667.2
3928 | 1260.8348 | 666.613
3929 | 1260.6772 | 666.443
3930 | 1260.412 | 666.124
3931 | 1260.2759 | 665.905
3932 | 1260 | 665.59
3933 | 1260 | 665.221
3934 | 1260 | 664.438
3935 | 1259.8074 | 663.439
3936 | 1259.699 | 663.369
3937 | 1259.2103 | 662.271
3938 | 1259.2 | 661.327
3939 | 1259.1168 | 661.326
3940 | 1258.89 | 660.655
3941 | 1258.648 | 659.853
3942 | 1258.4261 | 658.731
3943 | 1258.4261 | 658.4
3944 | 1258.4 | 656.8
3945 | 1258.4 | 656.8
3946 | 1258.144 | 656.613
3947 | 1257.977 | 654.706
3948 | 1257.8224 | 654.4
3949 | 1257.696 | 653.275
3950 | 1257.6 | 652.8
3951 | 1257.6 | 652.675
3952 | 1257.5245 | 651.958
3953 | 1257.4896 | 651.2
3954 | 1257.452 | 649.663
3955 | 1257.345 | 648
3956 | 1257.086 | 647.726
3957 | 1257.086 | 647.2
3958 | 1257.0037 | 646.581
3959 | 1256.8 | 646.4
3960 | 1256.8 | 646.159
3961 | 1256.603 | 645.706
3962 | 1256.2682 | 645.015
3963 | 1256.2682 | 644.8
3964 | 1256.2682 | 644.695
3965 | 1256.2333 | 644.559
3966 | 1256.0216 | 643.618
3967 | 1256 | 641.717
3968 | 1256 | 640.8
3969 | 1255.783 | 639.989
3970 | 1255.664 | 639.836
3971 | 1255.5327 | 637.353
3972 | 1255.5094 | 636
3973 | 1255.3689 | 635.2
3974 | 1255.265 | 634.814
3975 | 1255.2 | 633.232
3976 | 1255.151 | 632.68
3977 | 1255.099 | 632.419
3978 | 1254.993 | 630.568
3979 | 1254.9727 | 630.4
3980 | 1254.9727 | 630.318
3981 | 1254.555 | 630.283
3982 | 1254.4 | 629.766
3983 | 1254.4 | 629.001
3984 | 1254.4 | 627.296
3985 | 1254.291 | 626.4
3986 | 1254.203 | 625.6
3987 | 1253.8934 | 625.3
3988 | 1253.3755 | 624.791
3989 | 1253.158 | 622.4
3990 | 1253.0838 | 622.306
3991 | 1252.9154 | 621.658
3992 | 1252.9006 | 619.643
3993 | 1252.8 | 619.411
3994 | 1252.8 | 619.066
3995 | 1252.8 | 617.719
3996 | 1252.8 | 617.676
3997 | 1252.5906 | 617.6
3998 | 1252.525 | 617.426
3999 | 1252.2468 | 617.349
4000 | 1251.764 | 617.129
4001 | 1251.649 | 616.689
4002 | 1251.5192 | 616
4003 | 1251.5192 | 615.826
4004 | 1251.5192 | 615.826
4005 | 1251.361 | 615.726
4006 | 1251.306 | 614.511
4007 | 1251.2 | 613.497
4008 | 1251.1195 | 612.681
4009 | 1251.1145 | 612
4010 | 1251.0074 | 611.521
4011 | 1250.9173 | 611.471
4012 | 1250.7879 | 611.2
4013 | 1250.4936 | 609.183
4014 | 1250.4619 | 608.705
4015 | 1250.4 | 607.936
4016 | 1250.4 | 607.802
4017 | 1250.4 | 607.642
4018 | 1250.3824 | 606.4
4019 | 1250.2042 | 606.012
4020 | 1250.1114 | 605.977
4021 | 1249.9334 | 605.303
4022 | 1249.8858 | 605.093
4023 | 1249.6 | 604.902
4024 | 1249.3245 | 604.044
4025 | 1249.2235 | 603.67
4026 | 1249.168 | 602.4
4027 | 1248.913 | 602.276
4028 | 1248.913 | 600.762
4029 | 1248.8063 | 600.452
4030 | 1248.8 | 600.19
4031 | 1248.8 | 599.398
4032 | 1248.8 | 599.2
4033 | 1248.8 | 598.817
4034 | 1248.8 | 598.708
4035 | 1248.8 | 596.114
4036 | 1248.417 | 595.297
4037 | 1248.3052 | 595.286
4038 | 1248.0084 | 594.763
4039 | 1248 | 594.4
4040 | 1248 | 593.745
4041 | 1247.998 | 593.35
4042 | 1247.462 | 592.8
4043 | 1247.32 | 592.72
4044 | 1247.2 | 591.726
4045 | 1247.1906 | 591.2
4046 | 1247.034 | 589.513
4047 | 1247.0319 | 586.769
4048 | 1246.9858 | 584.8
4049 | 1246.7915 | 584.526
4050 | 1246.7064 | 584
4051 | 1246.7064 | 583.917
4052 | 1246.6844 | 583.669
4053 | 1246.649 | 583.544
4054 | 1246.4 | 583.37
4055 | 1246.4 | 583.2
4056 | 1246.4 | 581.755
4057 | 1246.387 | 581.675
4058 | 1246.3728 | 580.8
4059 | 1246.3699 | 580.479
4060 | 1245.954 | 579.2
4061 | 1245.736 | 578.333
4062 | 1245.6 | 577.906
4063 | 1245.6 | 576.8
4064 | 1245.0055 | 576.515
4065 | 1244.8 | 575.2
4066 | 1244.8 | 574.556
4067 | 1244.8 | 573.6
4068 | 1244.4999 | 573.408
4069 | 1244.499 | 572.882
4070 | 1244.374 | 572.328
4071 | 1244.187 | 571.112
4072 | 1244 | 570.857
4073 | 1243.9425 | 570.377
4074 | 1243.9425 | 569.582
4075 | 1243.9425 | 568.237
4076 | 1243.8855 | 567.511
4077 | 1243.5472 | 566.222
4078 | 1243.412 | 564.206
4079 | 1243.3736 | 563.226
4080 | 1243.2 | 562.472
4081 | 1243.2 | 560.088
4082 | 1243.0288 | 560
4083 | 1242.7375 | 558.4
4084 | 1242.4 | 557.618
4085 | 1242.3884 | 556.147
4086 | 1242.3487 | 556.1
4087 | 1241.914 | 556
4088 | 1241.663 | 554.253
4089 | 1241.662 | 554.071
4090 | 1241.6 | 553.845
4091 | 1241.5596 | 553.781
4092 | 1241.5501 | 552.958
4093 | 1241.5078 | 552.192
4094 | 1241.291 | 551.231
4095 | 1241.187 | 550.946
4096 | 1241.158 | 550.282
4097 | 1240.9649 | 549.322
4098 | 1240.8 | 548.296
4099 | 1240.7703 | 548
4100 | 1240.7703 | 547.36
4101 | 1240.471 | 546.585
4102 | 1240.205 | 546.31
4103 | 1240.0867 | 545.732
4104 | 1240.0192 | 545.475
4105 | 1240 | 545.206
4106 | 1240 | 542.4
4107 | 1240 | 541.553
4108 | 1239.89 | 541.436
4109 | 1239.8562 | 540.387
4110 | 1239.8362 | 538.156
4111 | 1239.767 | 537.759
4112 | 1239.5337 | 537.115
4113 | 1239.472 | 536.8
4114 | 1239.3475 | 536.73
4115 | 1239.2694 | 536.421
4116 | 1239.2 | 535.659
4117 | 1239.2 | 535.067
4118 | 1239.2 | 534.838
4119 | 1239.2 | 534.4
4120 | 1239.039 | 534.126
4121 | 1239.0123 | 532.169
4122 | 1238.9154 | 529.015
4123 | 1238.8415 | 527.26
4124 | 1238.812 | 526.4
4125 | 1238.6166 | 525.326
4126 | 1238.6157 | 524.352
4127 | 1238.61 | 523.995
4128 | 1238.5577 | 523.455
4129 | 1238.4395 | 522.926
4130 | 1238.4 | 521.225
4131 | 1238.4 | 520.71
4132 | 1238.1945 | 520
4133 | 1238.191 | 519.861
4134 | 1238.1 | 519.726
4135 | 1238.0554 | 518.62
4136 | 1237.7156 | 518.251
4137 | 1237.7056 | 517.681
4138 | 1237.7056 | 517.422
4139 | 1237.7056 | 516.868
4140 | 1237.6625 | 516.446
4141 | 1237.5674 | 515.678
4142 | 1237.532 | 515.675
4143 | 1237.1447 | 513.6
4144 | 1237.1447 | 513.541
4145 | 1237.0149 | 512.995
4146 | 1237.0149 | 512.779
4147 | 1236.892 | 512.744
4148 | 1236.8333 | 512.604
4149 | 1236.827 | 511.49
4150 | 1236.8 | 507.381
4151 | 1236.8 | 506.791
4152 | 1236.8 | 505.6
4153 | 1236.5588 | 505.6
4154 | 1236.4091 | 504.376
4155 | 1236.3242 | 504.267
4156 | 1236.1086 | 504
4157 | 1236.1086 | 504
4158 | 1235.9792 | 503.976
4159 | 1235.738 | 503.2
4160 | 1235.6617 | 503.03
4161 | 1235.312 | 502.466
4162 | 1235.2 | 502.434
4163 | 1234.863 | 502.04
4164 | 1234.4 | 502.04
4165 | 1234.4 | 501.6
4166 | 1234.242 | 500.825
4167 | 1234.1608 | 499.726
4168 | 1234.0498 | 499.297
4169 | 1234.046 | 498.668
4170 | 1233.7922 | 498.4
4171 | 1233.7778 | 498.4
4172 | 1233.7118 | 498.4
4173 | 1233.607 | 496.48
4174 | 1233.6 | 496.461
4175 | 1233.6 | 496.461
4176 | 1233.4671 | 496.461
4177 | 1233.4671 | 496.142
4178 | 1233.429 | 495.834
4179 | 1233.2875 | 495.827
4180 | 1233.2875 | 495.605
4181 | 1233.0561 | 494.4
4182 | 1232.8708 | 491.468
4183 | 1232.8 | 490.709
4184 | 1232.8 | 490.174
4185 | 1232.8 | 489.95
4186 | 1232.7184 | 489.214
4187 | 1232.4093 | 489.171
4188 | 1232.224 | 487.555
4189 | 1232.1801 | 487.2
4190 | 1232.152 | 487.2
4191 | 1232.0808 | 486.748
4192 | 1232 | 486.272
4193 | 1232 | 485.89
4194 | 1231.998 | 485.6
4195 | 1231.9892 | 485.6
4196 | 1231.626 | 485.537
4197 | 1231.447 | 485.305
4198 | 1231.431 | 484.941
4199 | 1231.2495 | 484.8
4200 | 1231.0896 | 484.749
4201 | 1231.0111 | 484.144
4202 | 1230.7987 | 484.086
4203 | 1230.7987 | 483.711
4204 | 1230.7481 | 482.522
4205 | 1230.6701 | 482.52
4206 | 1230.58 | 482.4
4207 | 1230.4932 | 481.323
4208 | 1230.4 | 480.8
4209 | 1230.4 | 480.586
4210 | 1230.108 | 478.93
4211 | 1230.108 | 478.323
4212 | 1230.0597 | 477.6
4213 | 1229.933 | 476.307
4214 | 1229.6 | 475.742
4215 | 1229.5985 | 475.046
4216 | 1229.4174 | 474.136
4217 | 1229.373 | 472.921
4218 | 1229.2948 | 472.289
4219 | 1229.1162 | 472
4220 | 1228.928 | 471.127
4221 | 1228.803 | 470.368
4222 | 1228.8 | 469.074
4223 | 1228.6313 | 468.776
4224 | 1228.3805 | 467.2
4225 | 1228.3805 | 466.885
4226 | 1228.3184 | 466.006
4227 | 1228.2872 | 465.678
4228 | 1228.1419 | 465.6
4229 | 1228.0848 | 465.383
4230 | 1228.071 | 464.413
4231 | 1228.0489 | 459.919
4232 | 1228 | 459.221
4233 | 1228 | 458.509
4234 | 1227.897 | 458.4
4235 | 1227.421 | 457.786
4236 | 1227.347 | 457.605
4237 | 1227.3453 | 456.526
4238 | 1227.291 | 456.064
4239 | 1227.2 | 454.536
4240 | 1226.996 | 454.4
4241 | 1226.957 | 454.314
4242 | 1226.9442 | 451.258
4243 | 1226.8474 | 450.967
4244 | 1226.7781 | 450.933
4245 | 1226.4 | 450.855
4246 | 1226.4 | 450.4
4247 | 1226.4 | 448.648
4248 | 1226.4 | 447.479
4249 | 1226.4 | 446.131
4250 | 1226.4 | 442.451
4251 | 1226.0084 | 442.176
4252 | 1225.8163 | 441.186
4253 | 1225.774 | 440.81
4254 | 1225.6264 | 440.683
4255 | 1225.6 | 437.738
4256 | 1225.6 | 437.175
4257 | 1225.6 | 436.575
4258 | 1225.6 | 435.784
4259 | 1225.411 | 433.874
4260 | 1225.3763 | 433.609
4261 | 1225.2732 | 432.451
4262 | 1225.2315 | 432.245
4263 | 1224.946 | 431.253
4264 | 1224.9167 | 431.2
4265 | 1224.801 | 428.893
4266 | 1224.8 | 428.118
4267 | 1224.544 | 426.089
4268 | 1224.436 | 422.47
4269 | 1224.246 | 421.943
4270 | 1223.9724 | 421.6
4271 | 1223.3853 | 419.96
4272 | 1223.2 | 419.895
4273 | 1223.2 | 418.217
4274 | 1223.2 | 416.8
4275 | 1222.75 | 414.71
4276 | 1222.7384 | 413.327
4277 | 1222.683 | 411.486
4278 | 1222.5996 | 411.095
4279 | 1222.5105 | 410.425
4280 | 1222.4 | 410.4
4281 | 1222.4 | 410.16
4282 | 1222.4 | 408.804
4283 | 1222.4 | 407.546
4284 | 1222.4 | 406.921
4285 | 1222.398 | 406.912
4286 | 1222.285 | 406.461
4287 | 1222.1238 | 404.483
4288 | 1221.935 | 403.253
4289 | 1221.8379 | 403.19
4290 | 1221.6987 | 402.664
4291 | 1221.6297 | 402.077
4292 | 1221.6 | 400.216
4293 | 1221.3717 | 400.084
4294 | 1221.1291 | 399.101
4295 | 1220.8328 | 397.6
4296 | 1220.8 | 397.571
4297 | 1220.8 | 396.926
4298 | 1220.5699 | 396.381
4299 | 1220.12 | 395.755
4300 | 1220.0359 | 394.4
4301 | 1220 | 393.645
4302 | 1220 | 393.295
4303 | 1220 | 392.924
4304 | 1220 | 392.558
4305 | 1219.8369 | 392.244
4306 | 1219.569 | 391.726
4307 | 1219.223 | 390.923
4308 | 1219.2 | 390.4
4309 | 1219.2 | 390.105
4310 | 1219.0571 | 388.469
4311 | 1218.7567 | 387.2
4312 | 1218.646 | 386.949
4313 | 1218.5665 | 386.834
4314 | 1218.473 | 386.4
4315 | 1218.4 | 385.854
4316 | 1218.2391 | 385.694
4317 | 1218.137 | 384
4318 | 1218.0211 | 382.4
4319 | 1217.803 | 382.4
4320 | 1217.7058 | 381.6
4321 | 1217.6 | 380.8
4322 | 1217.6 | 380.526
4323 | 1217.6 | 380
4324 | 1217.598 | 378.4
4325 | 1217.422 | 378.4
4326 | 1217.408 | 377.732
4327 | 1217.2856 | 376.928
4328 | 1217.2856 | 376.8
4329 | 1217.1598 | 376.58
4330 | 1217.119 | 375.903
4331 | 1216.9309 | 375.384
4332 | 1216.8483 | 375.337
4333 | 1216.8397 | 374.999
4334 | 1216.8 | 372
4335 | 1216.6852 | 371.376
4336 | 1216.588 | 370.581
4337 | 1216.436 | 369.717
4338 | 1216.2944 | 369.659
4339 | 1216.2944 | 369.6
4340 | 1216 | 368.8
4341 | 1216 | 368.25
4342 | 1216 | 368.162
4343 | 1216 | 367.365
4344 | 1215.9093 | 367.2
4345 | 1215.698 | 366.724
4346 | 1215.644 | 365.57
4347 | 1215.6037 | 362.525
4348 | 1215.6037 | 362.437
4349 | 1215.461 | 361.6
4350 | 1215.2952 | 360.8
4351 | 1215.2 | 359.589
4352 | 1215.149 | 359.351
4353 | 1215.1313 | 357.967
4354 | 1215.0892 | 357.6
4355 | 1215.0791 | 355.436
4356 | 1214.924 | 354.4
4357 | 1214.887 | 352.135
4358 | 1214.49 | 352
4359 | 1214.4 | 350.655
4360 | 1214.4 | 349.893
4361 | 1214.4 | 348.804
4362 | 1214.3544 | 348.8
4363 | 1214.3435 | 348.416
4364 | 1214.229 | 345.183
4365 | 1214.189 | 345.024
4366 | 1214.131 | 344.184
4367 | 1213.9294 | 343.115
4368 | 1213.91 | 342.926
4369 | 1213.663 | 342.873
4370 | 1213.608 | 342.4
4371 | 1213.6 | 341.853
4372 | 1213.6 | 341.068
4373 | 1212.985 | 338.774
4374 | 1212.909 | 338.585
4375 | 1212.8409 | 338.059
4376 | 1212.8063 | 335.588
4377 | 1212.806 | 334.751
4378 | 1212.8 | 333.691
4379 | 1212.8 | 332.934
4380 | 1212.52 | 332.433
4381 | 1212.443 | 332.057
4382 | 1212.067 | 332.039
4383 | 1212 | 331.757
4384 | 1212 | 325.6
4385 | 1212 | 325.338
4386 | 1212 | 324.975
4387 | 1211.7488 | 324.8
4388 | 1211.742 | 324.765
4389 | 1211.6653 | 324.334
4390 | 1211.4596 | 323.702
4391 | 1211.392 | 323.043
4392 | 1211.3632 | 320.242
4393 | 1211.2 | 318.593
4394 | 1211.2 | 318.4
4395 | 1211.2 | 317.121
4396 | 1211.2 | 316.237
4397 | 1211.064 | 316
4398 | 1210.9693 | 315.371
4399 | 1210.7689 | 313.6
4400 | 1210.6659 | 312.461
4401 | 1210.4 | 311.553
4402 | 1210.4 | 311.503
4403 | 1209.862 | 309.221
4404 | 1209.6927 | 308.8
4405 | 1209.6763 | 307.599
4406 | 1209.6 | 306.744
4407 | 1209.5909 | 305.868
4408 | 1209.1949 | 305.6
4409 | 1209.14 | 304.539
4410 | 1209.033 | 304.411
4411 | 1208.997 | 303.415
4412 | 1208.9158 | 303.415
4413 | 1208.8 | 303.354
4414 | 1208.7526 | 301.596
4415 | 1208.6635 | 300.417
4416 | 1208.6278 | 299.982
4417 | 1208.3058 | 299.2
4418 | 1208.0826 | 298.813
4419 | 1208 | 298.715
4420 | 1207.7239 | 298.695
4421 | 1207.4389 | 298.453
4422 | 1207.3155 | 298.356
4423 | 1207.2 | 297.439
4424 | 1207.2 | 297.228
4425 | 1207.2 | 296.8
4426 | 1207.2 | 296.8
4427 | 1207.142 | 296.63
4428 | 1207.035 | 296
4429 | 1206.9883 | 294.516
4430 | 1206.845 | 293.6
4431 | 1206.68 | 292.8
4432 | 1206.6721 | 292.78
4433 | 1206.6248 | 292.5
4434 | 1206.4888 | 291.2
4435 | 1206.4888 | 290.679
4436 | 1206.4 | 289.931
4437 | 1206.4 | 289.913
4438 | 1206.4 | 288.526
4439 | 1206.253 | 287.352
4440 | 1206.2528 | 287.2
4441 | 1206.214 | 285.6
4442 | 1205.8909 | 285.136
4443 | 1205.6919 | 284.8
4444 | 1205.541 | 284.359
4445 | 1205.407 | 284.28
4446 | 1205.397 | 284.004
4447 | 1204.9136 | 283.692
4448 | 1204.8 | 282.717
4449 | 1204.8 | 282.182
4450 | 1204.8 | 282.151
4451 | 1204.7818 | 281.691
4452 | 1204.6634 | 280.8
4453 | 1204.4444 | 280.636
4454 | 1204 | 279.708
4455 | 1204 | 278.921
4456 | 1204 | 276.006
4457 | 1204 | 276
4458 | 1203.916 | 274.351
4459 | 1203.862 | 273.571
4460 | 1203.8265 | 272.738
4461 | 1203.6531 | 272.249
4462 | 1203.4772 | 272
4463 | 1203.4772 | 270.265
4464 | 1203.2 | 269.697
4465 | 1203.2 | 267.246
4466 | 1203.199 | 266.9
4467 | 1203.114 | 266.4
4468 | 1203.09 | 266.238
4469 | 1203.0278 | 264.692
4470 | 1202.7821 | 264
4471 | 1202.5043 | 263.022
4472 | 1202.4 | 261.6
4473 | 1202.4 | 260.582
4474 | 1202.3589 | 259.481
4475 | 1202.344 | 259.2
4476 | 1201.79 | 258.906
4477 | 1201.79 | 258.863
4478 | 1201.671 | 258.72
4479 | 1201.6 | 258.056
4480 | 1201.6 | 256.602
4481 | 1201.4218 | 256.165
4482 | 1201.1464 | 255.985
4483 | 1201.14 | 255.869
4484 | 1201.115 | 255.553
4485 | 1201.095 | 255.376
4486 | 1200.8854 | 255.342
4487 | 1200.8 | 255.2
4488 | 1200.8 | 252.706
4489 | 1200.8 | 252.464
4490 | 1200.8 | 251.409
4491 | 1200.7723 | 251.189
4492 | 1200.7083 | 250.579
4493 | 1200.592 | 250.094
4494 | 1200.589 | 248.78
4495 | 1200.4086 | 248.493
4496 | 1200.3686 | 248.416
4497 | 1200.2556 | 248.309
4498 | 1200.195 | 247.843
4499 | 1200.115 | 247.567
4500 | 1200.1137 | 247.3
4501 | 1200 | 246.574
4502 | 1199.6331 | 243.713
4503 | 1199.5926 | 243.2
4504 | 1199.3168 | 242.947
4505 | 1199.3168 | 242.4
4506 | 1199.225 | 242.057
4507 | 1199.2 | 239.177
4508 | 1199.2 | 238.849
4509 | 1199.2 | 238.715
4510 | 1199.0566 | 238.4
4511 | 1198.9713 | 237.6
4512 | 1198.8976 | 236.189
4513 | 1198.8156 | 236
4514 | 1198.4 | 235.412
4515 | 1198.4 | 235.224
4516 | 1198.38 | 234.833
4517 | 1198.3366 | 234.4
4518 | 1198.1621 | 234.4
4519 | 1198.1208 | 233.488
4520 | 1198.058 | 233
4521 | 1198.0387 | 232.99
4522 | 1198.0387 | 232.418
4523 | 1197.79 | 232.264
4524 | 1197.303 | 231.2
4525 | 1197.2617 | 230.751
4526 | 1196.9072 | 230.648
4527 | 1196.8 | 230.639
4528 | 1196.8 | 230.4
4529 | 1196.4829 | 230.285
4530 | 1196.4679 | 230.267
4531 | 1196.422 | 229.197
4532 | 1196.191 | 228.818
4533 | 1196.1437 | 228.8
4534 | 1196.1292 | 227.643
4535 | 1196 | 227.322
4536 | 1196 | 227.303
4537 | 1196 | 227.2
4538 | 1195.968 | 226.4
4539 | 1195.6673 | 225.42
4540 | 1195.5738 | 224.535
4541 | 1195.5738 | 223.782
4542 | 1195.4363 | 223.758
4543 | 1195.22 | 223.324
4544 | 1195.2 | 223.2
4545 | 1195.2 | 223.2
4546 | 1195.2 | 222.364
4547 | 1194.744 | 222.332
4548 | 1194.5136 | 222.204
4549 | 1194.461 | 221.632
4550 | 1194.4 | 221.6
4551 | 1194.4 | 221.106
4552 | 1194.4 | 220.766
4553 | 1193.8661 | 220
4554 | 1193.7386 | 219.874
4555 | 1193.708 | 219.862
4556 | 1193.6 | 218.4
4557 | 1193.6 | 216.83
4558 | 1193.2138 | 216.762
4559 | 1193.172 | 216.305
4560 | 1193.029 | 215.317
4561 | 1192.8111 | 215.212
4562 | 1192.7735 | 215.039
4563 | 1192.6799 | 214.87
4564 | 1192.4164 | 214.198
4565 | 1192.407 | 213.658
4566 | 1192.262 | 213.633
4567 | 1192 | 213.156
4568 | 1192 | 211.241
4569 | 1192 | 210.769
4570 | 1192 | 210.739
4571 | 1191.895 | 210.4
4572 | 1191.8232 | 210.07
4573 | 1191.5872 | 209.702
4574 | 1191.5782 | 209.147
4575 | 1191.2752 | 207.619
4576 | 1191.2 | 207.2
4577 | 1191.2 | 207.2
4578 | 1191.158 | 206.607
4579 | 1191.082 | 206.425
4580 | 1190.5629 | 206.159
4581 | 1190.56 | 205.13
4582 | 1190.482 | 204
4583 | 1190.4 | 204
4584 | 1190.4 | 203.206
4585 | 1190.0714 | 203.2
4586 | 1189.8149 | 202.635
4587 | 1189.7541 | 201.296
4588 | 1189.61 | 200.129
4589 | 1189.6 | 200
4590 | 1189.6 | 199.723
4591 | 1189.6 | 199.55
4592 | 1189.6 | 199.2
4593 | 1189.6 | 198.119
4594 | 1189.3358 | 197.998
4595 | 1189.1388 | 197.927
4596 | 1188.8 | 197.775
4597 | 1188.8 | 197.342
4598 | 1188.667 | 197.097
4599 | 1188.5309 | 196.977
4600 | 1188.3885 | 195.58
4601 | 1188.218 | 195.2
4602 | 1188 | 193.571
4603 | 1187.9385 | 192.8
4604 | 1187.8648 | 192
4605 | 1187.8648 | 191.372
4606 | 1187.464 | 191.2
4607 | 1187.2856 | 188.557
4608 | 1187.2 | 187.545
4609 | 1187.1293 | 187.338
4610 | 1187.0499 | 187.2
4611 | 1186.9605 | 187.2
4612 | 1186.715 | 186.547
4613 | 1186.5863 | 186.495
4614 | 1186.4 | 186.465
4615 | 1186.3938 | 186.389
4616 | 1186.13 | 186.091
4617 | 1186.075 | 185.688
4618 | 1185.9043 | 185.267
4619 | 1185.808 | 181.65
4620 | 1185.7689 | 181.016
4621 | 1185.424 | 180
4622 | 1185.2801 | 178.903
4623 | 1185.2757 | 178.887
4624 | 1185.2136 | 177.568
4625 | 1185.147 | 176.389
4626 | 1185.0608 | 173.6
4627 | 1184.9728 | 173.427
4628 | 1184.9728 | 172.671
4629 | 1184.9728 | 172
4630 | 1184.8307 | 171.98
4631 | 1184.8307 | 171.2
4632 | 1184.8307 | 171.051
4633 | 1184.8 | 170.51
4634 | 1184.8 | 169.757
4635 | 1184.4607 | 168.445
4636 | 1184.2177 | 167.512
4637 | 1184.1872 | 166.752
4638 | 1184.1872 | 166.461
4639 | 1184 | 165.475
4640 | 1184 | 164.381
4641 | 1183.914 | 160.8
4642 | 1183.594 | 159.726
4643 | 1183.4517 | 158.126
4644 | 1183.22 | 157.401
4645 | 1183.2 | 156.961
4646 | 1183.2 | 156.165
4647 | 1183.2 | 156.021
4648 | 1182.9589 | 155.404
4649 | 1182.912 | 153.397
4650 | 1182.818 | 152.741
4651 | 1182.7428 | 152.116
4652 | 1182.657 | 151.556
4653 | 1182.509 | 151.121
4654 | 1182.4 | 150.064
4655 | 1182.4 | 149.747
4656 | 1182.4 | 148.8
4657 | 1182.4 | 148.8
4658 | 1182.365 | 146.644
4659 | 1182.361 | 146.027
4660 | 1181.9806 | 145.002
4661 | 1181.9806 | 144.913
4662 | 1181.7602 | 144.511
4663 | 1181.647 | 144.339
4664 | 1181.6 | 142.4
4665 | 1181.242 | 141.485
4666 | 1181.19 | 140.96
4667 | 1181.115 | 139.849
4668 | 1181.0885 | 139.56
4669 | 1180.946 | 138.939
4670 | 1180.8 | 138.48
4671 | 1180.8 | 138.4
4672 | 1180.8 | 138.295
4673 | 1180.8 | 137.856
4674 | 1180.5096 | 137.738
4675 | 1180.5096 | 137.504
4676 | 1180.3883 | 136.928
4677 | 1180.2871 | 136.814
4678 | 1180 | 136.8
4679 | 1179.9083 | 135.76
4680 | 1179.7741 | 135.303
4681 | 1179.725 | 135.2
4682 | 1179.3922 | 134.44
4683 | 1179.3631 | 133.403
4684 | 1179.3466 | 133.165
4685 | 1179.255 | 132.8
4686 | 1179.2 | 131.303
4687 | 1179.2 | 130.926
4688 | 1179.2 | 130.353
4689 | 1179.0386 | 129.798
4690 | 1178.9974 | 128.636
4691 | 1178.5865 | 127.807
4692 | 1178.5 | 127.685
4693 | 1178.4929 | 127.2
4694 | 1178.4 | 126.4
4695 | 1178.4 | 126.126
4696 | 1178.36 | 125.775
4697 | 1178.3067 | 125.48
4698 | 1178.106 | 124.8
4699 | 1178.0217 | 124.396
4700 | 1177.8008 | 124.387
4701 | 1177.8001 | 124.332
4702 | 1177.6161 | 124
4703 | 1177.5675 | 123.82
4704 | 1177.554 | 123.533
4705 | 1177.4916 | 123.399
4706 | 1177.0613 | 123.2
4707 | 1176.84 | 122.756
4708 | 1176.832 | 121.6
4709 | 1176.8108 | 121.202
4710 | 1176.8 | 120.885
4711 | 1176.8 | 120.425
4712 | 1176.8 | 120
4713 | 1176.8 | 119.403
4714 | 1176.7039 | 118.647
4715 | 1176.207 | 118.4
4716 | 1176.0394 | 118.4
4717 | 1176 | 117.6
4718 | 1175.793 | 116.95
4719 | 1175.544 | 116.8
4720 | 1175.372 | 116.541
4721 | 1175.229 | 116.526
4722 | 1175.2 | 116.452
4723 | 1175.2 | 116.132
4724 | 1175.0536 | 116
4725 | 1175.0134 | 115.2
4726 | 1174.9733 | 114.987
4727 | 1174.7929 | 114.987
4728 | 1174.6209 | 114.4
4729 | 1174.6132 | 114.4
4730 | 1174.6132 | 113.678
4731 | 1174.5986 | 113.6
4732 | 1174.1449 | 113.313
4733 | 1173.9536 | 113.151
4734 | 1173.817 | 112.861
4735 | 1173.8164 | 112.861
4736 | 1173.7765 | 112.656
4737 | 1173.6 | 112.092
4738 | 1173.32 | 111.958
4739 | 1173.122 | 111.879
4740 | 1172.832 | 111.835
4741 | 1172.8 | 111.726
4742 | 1172.8 | 111.64
4743 | 1172.3997 | 111.2
4744 | 1172.2624 | 110.4
4745 | 1172.039 | 110.4
4746 | 1172 | 110.4
4747 | 1172 | 110.4
4748 | 1171.973 | 110.4
4749 | 1171.9502 | 109.6
4750 | 1171.847 | 109.6
4751 | 1171.6916 | 109.376
4752 | 1171.349 | 108.8
4753 | 1171.326 | 108.8
4754 | 1171.2 | 108.377
4755 | 1171.09 | 108.121
4756 | 1171.084 | 108
4757 | 1170.7092 | 108
4758 | 1170.6288 | 107.217
4759 | 1170.5985 | 107.217
4760 | 1170.4 | 107.217
4761 | 1170.3146 | 107.2
4762 | 1170.2123 | 107.2
4763 | 1170.2102 | 107.2
4764 | 1169.848 | 107.136
4765 | 1169.6 | 107.127
4766 | 1169.6 | 106.4
4767 | 1169.6 | 106.4
4768 | 1169.6 | 106.365
4769 | 1169.1854 | 105.986
4770 | 1169.049 | 105.633
4771 | 1168.8 | 105.6
4772 | 1168.8 | 105.6
4773 | 1168.8 | 105.5
4774 | 1168.6743 | 105.189
4775 | 1168.515 | 105.189
4776 | 1168.446 | 105.179
4777 | 1168.1969 | 104.887
4778 | 1168.124 | 104.887
4779 | 1168.045 | 104.8
4780 | 1168 | 104.8
4781 | 1168 | 104.8
4782 | 1168 | 104.11
4783 | 1167.9465 | 104
4784 | 1167.854 | 104
4785 | 1167.775 | 103.864
4786 | 1167.7466 | 103.377
4787 | 1167.432 | 103.333
4788 | 1167.329 | 103.2
4789 | 1167.2 | 103.2
4790 | 1167.2 | 103.2
4791 | 1167.2 | 102.4
4792 | 1167.2 | 102.229
4793 | 1166.9312 | 101.828
4794 | 1166.901 | 101.779
4795 | 1166.426 | 101.779
4796 | 1166.42 | 101.6
4797 | 1166.4 | 101.6
4798 | 1166.299 | 101.6
4799 | 1166.2254 | 101.6
4800 | 1166.196 | 101.6
4801 | 1165.9822 | 101.6
4802 | 1165.8744 | 101.205
4803 | 1165.8744 | 101.002
4804 | 1165.6 | 100.855
4805 | 1165.6 | 100.8
4806 | 1165.6 | 100.766
4807 | 1165.6 | 100.766
4808 | 1165.4076 | 100.593
4809 | 1165.374 | 100.593
4810 | 1165.2976 | 100.593
4811 | 1165.2105 | 100.274
4812 | 1165.1837 | 100.225
4813 | 1165.131 | 100
4814 | 1165.0637 | 100
4815 | 1165.0506 | 100
4816 | 1164.8 | 100
4817 | 1164.8 | 99.775
4818 | 1164.6709 | 99.448
4819 | 1164.5561 | 99.362
4820 | 1164.4744 | 99.2
4821 | 1164.458 | 99.2
4822 | 1164.3879 | 99.2
4823 | 1164.3282 | 99.2
4824 | 1164.3282 | 98.957
4825 | 1164.3282 | 98.957
4826 | 1163.9011 | 98.671
4827 | 1163.639 | 98.671
4828 | 1163.5669 | 98.56
4829 | 1163.2 | 98.4
4830 | 1163.2 | 98.4
4831 | 1163.1117 | 98.4
4832 | 1162.8571 | 98.4
4833 | 1162.8571 | 98.4
4834 | 1162.7946 | 98.4
4835 | 1162.7327 | 98.243
4836 | 1162.6599 | 97.6
4837 | 1162.556 | 97.371
4838 | 1162.5522 | 97.322
4839 | 1162.4 | 97.117
4840 | 1162.4 | 96.8
4841 | 1162.384 | 96.8
4842 | 1162.3773 | 96.8
4843 | 1162.2995 | 96.8
4844 | 1162.2995 | 96.8
4845 | 1162.25 | 96.767
4846 | 1162.174 | 96.504
4847 | 1162.1216 | 96.34
4848 | 1162.094 | 96.008
4849 | 1161.964 | 96
4850 | 1161.734 | 96
4851 | 1161.6 | 95.627
4852 | 1161.3384 | 95.618
4853 | 1161.248 | 95.2
4854 | 1161.104 | 95.2
4855 | 1161.093 | 95.2
4856 | 1161.083 | 95.2
4857 | 1161.0661 | 94.882
4858 | 1161.038 | 94.868
4859 | 1160.8 | 94.83
4860 | 1160.599 | 94.83
4861 | 1160.5057 | 94.692
4862 | 1160.349 | 94.4
4863 | 1160.2693 | 94.4
4864 | 1159.956 | 94.4
4865 | 1159.838 | 94.4
4866 | 1159.81 | 94.4
4867 | 1159.54 | 94.359
4868 | 1159.2 | 94.033
4869 | 1159.2 | 94.033
4870 | 1158.633 | 94.033
4871 | 1158.511 | 94.01
4872 | 1158.444 | 93.894
4873 | 1158.4 | 93.766
4874 | 1158.4 | 93.6
4875 | 1158.39 | 93.6
4876 | 1158.2769 | 93.6
4877 | 1158.2769 | 93.6
4878 | 1157.6379 | 93.6
4879 | 1157.6 | 93.6
4880 | 1157.2293 | 93.6
4881 | 1157.201 | 93.236
4882 | 1157.0817 | 93.236
4883 | 1156.956 | 93.236
4884 | 1156.8955 | 92.8
4885 | 1156.8955 | 92.8
4886 | 1156.838 | 92.8
4887 | 1156.8 | 92.8
4888 | 1156.517 | 92.8
4889 | 1156.3257 | 92.676
4890 | 1156 | 92.508
4891 | 1156 | 92.439
4892 | 1155.725 | 92.415
4893 | 1155.7145 | 92
4894 | 1155.5019 | 92
4895 | 1155.338 | 91.94
4896 | 1155.2987 | 91.642
4897 | 1155.2 | 91.642
4898 | 1155.2 | 91.597
4899 | 1154.806 | 91.289
4900 | 1154.7758 | 91.204
4901 | 1154.691 | 91.2
4902 | 1154.1328 | 91.2
4903 | 1154.1328 | 91.2
4904 | 1154.0047 | 91.2
4905 | 1153.9649 | 91.2
4906 | 1153.6 | 91.2
4907 | 1153.519 | 91.191
4908 | 1153.41 | 91.061
4909 | 1153.367 | 90.898
4910 | 1153.1952 | 90.845
4911 | 1152.9763 | 90.469
4912 | 1152.8 | 90.4
4913 | 1152.8 | 90.4
4914 | 1152.8 | 90.27
4915 | 1152.652 | 90.048
4916 | 1152 | 89.6
4917 | 1152 | 89.6
4918 | 1151.9371 | 89.6
4919 | 1151.8243 | 89.6
4920 | 1151.8243 | 89.6
4921 | 1151.437 | 89.6
4922 | 1151.05 | 89.6
4923 | 1150.936 | 88.998
4924 | 1150.8718 | 88.998
4925 | 1150.6454 | 88.8
4926 | 1150.5013 | 88.8
4927 | 1150.4507 | 88.455
4928 | 1150.4 | 88.262
4929 | 1150.4 | 88
4930 | 1150.4 | 88
4931 | 1150.3401 | 88
4932 | 1150.1519 | 88
4933 | 1149.785 | 88
4934 | 1149.6178 | 87.658
4935 | 1149.6 | 87.658
4936 | 1149.6 | 87.658
4937 | 1149.6 | 87.658
4938 | 1149.254 | 87.564
4939 | 1149.101 | 87.284
4940 | 1148.4205 | 87.2
4941 | 1148.1467 | 87.2
4942 | 1148.1467 | 87.2
4943 | 1148.1467 | 87.085
4944 | 1148 | 86.791
4945 | 1148 | 86.4
4946 | 1148 | 86.4
4947 | 1147.9167 | 86.126
4948 | 1147.7987 | 86.056
4949 | 1147.683 | 85.6
4950 | 1147.5377 | 85.6
4951 | 1147.534 | 85.6
4952 | 1147.519 | 85.6
4953 | 1147.4112 | 85.6
4954 | 1147.4094 | 85.37
4955 | 1147.38 | 85.32
4956 | 1147.369 | 85.267
4957 | 1147.2 | 84.954
4958 | 1147.2 | 84.8
4959 | 1147.2 | 84.585
4960 | 1147.17 | 84.47
4961 | 1147.0671 | 84
4962 | 1147.015 | 83.849
4963 | 1146.697 | 83.573
4964 | 1146.669 | 83.061
4965 | 1146.5832 | 82.622
4966 | 1146.42 | 82.378
4967 | 1146.4 | 82.378
4968 | 1146.4 | 82.378
4969 | 1146.178 | 82.378
4970 | 1146.147 | 82.191
4971 | 1145.9282 | 81.643
4972 | 1145.8446 | 81.6
4973 | 1145.7167 | 81.6
4974 | 1145.6 | 81.099
4975 | 1145.6 | 81.004
4976 | 1145.6 | 80.475
4977 | 1145.5301 | 80.369
4978 | 1145.1539 | 80.366
4979 | 1144.8 | 80.119
4980 | 1144.8 | 79.7
4981 | 1144.8 | 79.471
4982 | 1144.4632 | 79.106
4983 | 1144.3567 | 78.738
4984 | 1144.1924 | 78.738
4985 | 1144.168 | 78.701
4986 | 1144 | 78.678
4987 | 1143.986 | 77.802
4988 | 1143.3262 | 77.538
4989 | 1143.278 | 77.357
4990 | 1143.2188 | 76.876
4991 | 1143.193 | 76.8
4992 | 1143.128 | 76.63
4993 | 1142.5534 | 76.526
4994 | 1142.4 | 76.362
4995 | 1142.4 | 75.817
4996 | 1142.4 | 75.671
4997 | 1142.4 | 74.503
4998 | 1142.288 | 73.821
4999 | 1142.233 | 72.352
5000 | 1141.8157 | 71.276
5001 | 1141.7005 | 69.342
5002 | 1141.6 | 68.658
5003 | 1141.587 | 68.407
5004 | 1141.3284 | 67.983
5005 | 1141.3222 | 67.194
5006 | 1141.1439 | 66.871
5007 | 1141.0098 | 64.749
5008 | 1141.0098 | 62.885
5009 | 1140.835 | 61.45
5010 | 1140.8 | 61.278
5011 | 1140.583 | 61.095
5012 | 1140.384 | 60.006
5013 | 1140.3677 | 59.573
5014 | 1140.2509 | 57.802
5015 | 1140.056 | 57.76
5016 | 1140 | 57.082
5017 | 1140 | 56.178
5018 | 1140 | 55.186
5019 | 1139.749 | 54.768
5020 | 1139.5362 | 54.06
5021 | 1139.46 | 53.921
5022 | 1139.333 | 52.912
5023 | 1139.3205 | 51.79
5024 | 1139.2 | 51.683
5025 | 1139.2 | 51.103
5026 | 1138.585 | 50.763
5027 | 1138.4192 | 47.886
5028 | 1138.4 | 47.679
5029 | 1138.4 | 47.551
5030 | 1138.269 | 46.448
5031 | 1138.2471 | 46.125
5032 | 1138.22 | 43.981
5033 | 1137.9564 | 43.767
5034 | 1137.6 | 41.456
5035 | 1137.6 | 41.352
5036 | 1137.5314 | 39.336
5037 | 1137.376 | 38.44
5038 | 1137.1705 | 37.411
5039 | 1137.1139 | 36.532
5040 | 1137.052 | 35.89
5041 | 1136.8 | 33.997
5042 | 1136.61 | 33.462
5043 | 1136.3975 | 31.096
5044 | 1136.175 | 30.005
5045 | 1136.1375 | 29.421
5046 | 1135.9657 | 28.577
5047 | 1135.9 | 28.292
5048 | 1135.797 | 27.779
5049 | 1135.5657 | 27.19
5050 | 1135.24 | 27.095
5051 | 1135.205 | 26.957
5052 | 1135.2 | 26.789
5053 | 1135.0278 | 25.918
5054 | 1134.7688 | 25.206
5055 | 1134.4 | 24.696
5056 | 1134.4 | 23.89
5057 | 1134.3734 | 23.373
5058 | 1134.3301 | 23.192
5059 | 1134.3297 | 22.785
5060 | 1134.203 | 19.077
5061 | 1134.1783 | 19.062
5062 | 1133.6 | 18.902
5063 | 1133.5528 | 17.551
5064 | 1133.4363 | 16.356
5065 | 1133.4123 | 15.807
5066 | 1133.191 | 11.635
5067 | 1133.1751 | 11.483
5068 | 1132.8406 | 8.992
5069 | 1132.8 | 8.76
5070 | 1132.7008 | 7.749
5071 | 1132.6778 | 7.696
5072 | 1132.464 | 7.094
5073 | 1132.1777 | 6.84
5074 | 1132.013 | 6.535
5075 | 1132 | 3.741
5076 | 1132 | 2.296
5077 | 1131.4817 | 1.965
5078 | 1131.45 | 1.78
5079 | 1131.3953 | 1.177
5080 | 1131.3791 | 0.234
5081 | 1131.3402 | 0.203
5082 | 1131.2 | 0
5083 | 1131.2 | 0
5084 | 1131.2 | 0
5085 | 1131.2 | 0
5086 | 1131.076 | 0
5087 | 1131.027 | 0
5088 | 1130.671 | 0
5089 | 1130.656 | 0
5090 | 1130.4682 | 0
5091 | 1130.4 | 0
5092 | 1130.342 | 0
5093 | 1130.2855 | 0
5094 | 1129.8233 | 0
5095 | 1129.6 | 0
5096 | 1129.0885 | 0
5097 | 1128.9285 | 0
5098 | 1128.8 | 0
5099 | 1128.8 | 0
5100 | 1128.8 | 0
5101 | 1128.8 | 0
5102 | 1128.7455 | 0
5103 | 1128.6053 | 0
5104 | 1128.5775 | 0
5105 | 1128 | 0
5106 | 1128 | 0
5107 | 1128 | 0
5108 | 1127.7874 | 0
5109 | 1127.5968 | 0
5110 | 1127.5522 | 0
5111 | 1127.5522 | 0
5112 | 1127.549 | 0
5113 | 1127.493 | 0
5114 | 1127.2 | 0
5115 | 1127.2 | 0
5116 | 1127.2 | 0
5117 | 1127.2 | 0
5118 | 1127.2 | 0
5119 | 1127.015 | 0
5120 | 1126.9881 | 0
5121 | 1126.9766 | 0
5122 | 1126.9696 | 0
5123 | 1126.8 | 0
5124 | 1126.6764 | 0
5125 | 1126.5055 | 0
5126 | 1126.5055 | 0
5127 | 1126.43 | 0
5128 | 1126.4 | 0
5129 | 1126.4 | 0
5130 | 1126.266 | 0
5131 | 1125.992 | 0
5132 | 1125.8148 | 0
5133 | 1125.6 | 0
5134 | 1125.5 | 0
5135 | 1125.488 | 0
5136 | 1125.3411 | 0
5137 | 1125.237 | 0
5138 | 1125.2328 | 0
5139 | 1124.8 | 0
5140 | 1124.637 | 0
5141 | 1124.2295 | 0
5142 | 1124.1761 | 0
5143 | 1124 | 0
5144 | 1123.8746 | 0
5145 | 1123.8746 | 0
5146 | 1123.8746 | 0
5147 | 1123.825 | 0
5148 | 1123.7505 | 0
5149 | 1123.4907 | 0
5150 | 1123.1632 | 0
5151 | 1122.8155 | 0
5152 | 1122.777 | 0
5153 | 1122.775 | 0
5154 | 1122.711 | 0
5155 | 1122.6757 | 0
5156 | 1122.6445 | 0
5157 | 1122.6312 | 0
5158 | 1122.521 | 0
5159 | 1122.4035 | 0
5160 | 1122.4 | 0
5161 | 1122.4 | 0
5162 | 1122.4 | 0
5163 | 1122.3613 | 0
5164 | 1121.8987 | 0
5165 | 1121.6603 | 0
5166 | 1121.6 | 0
5167 | 1121.6 | 0
5168 | 1121.6 | 0
5169 | 1121.6 | 0
5170 | 1121.6 | 0
5171 | 1121.586 | 0
5172 | 1121.5161 | 0
5173 | 1121.2717 | 0
5174 | 1121.1221 | 0
5175 | 1120.8 | 0
5176 | 1120.197 | 0
5177 | 1120.1603 | 0
5178 | 1120.1186 | 0
5179 | 1120 | 0
5180 | 1120 | 0
5181 | 1120 | 0
5182 | 1119.86 | 0
5183 | 1119.4615 | 0
5184 | 1119.4615 | 0
5185 | 1119.408 | 0
5186 | 1119.2978 | 0
5187 | 1119.2 | 0
5188 | 1119.0192 | 0
5189 | 1118.7913 | 0
5190 | 1118.7892 | 0
5191 | 1118.7189 | 0
5192 | 1118.58 | 0
5193 | 1118.4 | 0
5194 | 1118.4 | 0
5195 | 1118.4 | 0
5196 | 1118.4 | 0
5197 | 1118.1698 | 0
5198 | 1118.0342 | 0
5199 | 1117.6 | 0
5200 | 1117.5266 | 0
5201 | 1117.404 | 0
5202 | 1117.2373 | 0
5203 | 1117.2373 | 0
5204 | 1117.132 | 0
5205 | 1117.045 | 0
5206 | 1117.0011 | 0
5207 | 1116.8 | 0
5208 | 1116.4602 | 0
5209 | 1116.444 | 0
5210 | 1116.4404 | 0
5211 | 1115.6435 | 0
5212 | 1115.5132 | 0
5213 | 1115.506 | 0
5214 | 1115.4545 | 0
5215 | 1115.2 | 0
5216 | 1115.2 | 0
5217 | 1115.1485 | 0
5218 | 1114.978 | 0
5219 | 1114.9063 | 0
5220 | 1114.771 | 0
5221 | 1114.766 | 0
5222 | 1114.3042 | 0
5223 | 1114.1294 | 0
5224 | 1114.082 | 0
5225 | 1114.0731 | 0
5226 | 1114.0731 | 0
5227 | 1114.0497 | 0
5228 | 1114.0497 | 0
5229 | 1113.8843 | 0
5230 | 1113.713 | 0
5231 | 1113.621 | 0
5232 | 1113.6 | 0
5233 | 1113.5773 | 0
5234 | 1113.5542 | 0
5235 | 1113.3524 | 0
5236 | 1113.2529 | 0
5237 | 1113.0665 | 0
5238 | 1113.0576 | 0
5239 | 1112.8 | 0
5240 | 1112.6918 | 0
5241 | 1112.5755 | 0
5242 | 1112.4017 | 0
5243 | 1112.084 | 0
5244 | 1112.0011 | 0
5245 | 1112 | 0
5246 | 1111.595 | 0
5247 | 1111.3104 | 0
5248 | 1111.2 | 0
5249 | 1111.2 | 0
5250 | 1111.2 | 0
5251 | 1111.0216 | 0
5252 | 1110.796 | 0
5253 | 1110.708 | 0
5254 | 1110.6197 | 0
5255 | 1110.6197 | 0
5256 | 1110.192 | 0
5257 | 1109.9109 | 0
5258 | 1109.8997 | 0
5259 | 1109.7952 | 0
5260 | 1109.748 | 0
5261 | 1109.6 | 0
5262 | 1109.6 | 0
5263 | 1109.6 | 0
5264 | 1109.428 | 0
5265 | 1109.3055 | 0
5266 | 1109.1642 | 0
5267 | 1108.8 | 0
5268 | 1108.431 | 0
5269 | 1108 | 0
5270 | 1108 | 0
5271 | 1107.6746 | 0
5272 | 1107.5098 | 0
5273 | 1107.3417 | 0
5274 | 1107.2 | 0
5275 | 1106.8931 | 0
5276 | 1106.8777 | 0
5277 | 1106.751 | 0
5278 | 1106.567 | 0
5279 | 1106.5238 | 0
5280 | 1106.5238 | 0
5281 | 1106.455 | 0
5282 | 1106.4 | 0
5283 | 1106.227 | 0
5284 | 1105.904 | 0
5285 | 1105.7849 | 0
5286 | 1105.6 | 0
5287 | 1105.581 | 0
5288 | 1105.284 | 0
5289 | 1105.284 | 0
5290 | 1105.275 | 0
5291 | 1105.1884 | 0
5292 | 1105.1745 | 0
5293 | 1105.0942 | 0
5294 | 1104.938 | 0
5295 | 1104.8061 | 0
5296 | 1104.482 | 0
5297 | 1104.2739 | 0
5298 | 1104.242 | 0
5299 | 1104.063 | 0
5300 | 1104.0155 | 0
5301 | 1104 | 0
5302 | 1104 | 0
5303 | 1103.6522 | 0
5304 | 1103.5739 | 0
5305 | 1103.419 | 0
5306 | 1103.3684 | 0
5307 | 1103.2 | 0
5308 | 1103.2 | 0
5309 | 1102.819 | 0
5310 | 1102.5551 | 0
5311 | 1102.5445 | 0
5312 | 1102.4753 | 0
5313 | 1102.4 | 0
5314 | 1102.4 | 0
5315 | 1102.325 | 0
5316 | 1102.0699 | 0
5317 | 1101.8888 | 0
5318 | 1101.8299 | 0
5319 | 1101.732 | 0
5320 | 1101.6408 | 0
5321 | 1101.6 | 0
5322 | 1101.6 | 0
5323 | 1101.4945 | 0
5324 | 1100.807 | 0
5325 | 1100.8 | 0
5326 | 1100.388 | 0
5327 | 1100.2595 | 0
5328 | 1100.2595 | 0
5329 | 1100.227 | 0
5330 | 1100.114 | 0
5331 | 1100.0177 | 0
5332 | 1100 | 0
5333 | 1099.9253 | 0
5334 | 1099.6024 | 0
5335 | 1099.177 | 0
5336 | 1098.997 | 0
5337 | 1098.9089 | 0
5338 | 1098.8781 | 0
5339 | 1098.8669 | 0
5340 | 1098.458 | 0
5341 | 1098.4 | 0
5342 | 1098.227 | 0
5343 | 1098.1261 | 0
5344 | 1098.0768 | 0
5345 | 1098.0623 | 0
5346 | 1097.92 | 0
5347 | 1097.3959 | 0
5348 | 1097.2 | 0
5349 | 1096.806 | 0
5350 | 1096.7099 | 0
5351 | 1096.2598 | 0
5352 | 1095.8283 | 0
5353 | 1095.822 | 0
5354 | 1095.2 | 0
5355 | 1095.1893 | 0
5356 | 1095.157 | 0
5357 | 1094.9209 | 0
5358 | 1094.6009 | 0
5359 | 1094.5292 | 0
5360 | 1094.4 | 0
5361 | 1094.398 | 0
5362 | 1094.2419 | 0
5363 | 1094.152 | 0
5364 | 1094.1275 | 0
5365 | 1093.9 | 0
5366 | 1093.7182 | 0
5367 | 1093.6 | 0
5368 | 1093.3526 | 0
5369 | 1093.259 | 0
5370 | 1093.0432 | 0
5371 | 1093.028 | 0
5372 | 1092.9827 | 0
5373 | 1092.8 | 0
5374 | 1092.8 | 0
5375 | 1092.7 | 0
5376 | 1092.6207 | 0
5377 | 1092.491 | 0
5378 | 1092.2168 | 0
5379 | 1092 | 0
5380 | 1092 | 0
5381 | 1091.61 | 0
5382 | 1091.5981 | 0
5383 | 1091.508 | 0
5384 | 1091.276 | 0
5385 | 1091.2 | 0
5386 | 1090.8972 | 0
5387 | 1090.7762 | 0
5388 | 1090.5899 | 0
5389 | 1090.429 | 0
5390 | 1090.4 | 0
5391 | 1089.986 | 0
5392 | 1089.836 | 0
5393 | 1089.7222 | 0
5394 | 1089.6 | 0
5395 | 1089.6 | 0
5396 | 1089.279 | 0
5397 | 1089.2673 | 0
5398 | 1088.8 | 0
5399 | 1088.8 | 0
5400 | 1088.8 | 0
5401 | 1088.8 | 0
5402 | 1088.8 | 0
5403 | 1088.675 | 0
5404 | 1088.5696 | 0
5405 | 1088.323 | 0
5406 | 1088.1963 | 0
5407 | 1088 | 0
5408 | 1088 | 0
5409 | 1087.883 | 0
5410 | 1087.8341 | 0
5411 | 1087.8341 | 0
5412 | 1087.8272 | 0
5413 | 1087.4829 | 0
5414 | 1087.344 | 0
5415 | 1087.2 | 0
5416 | 1087.115 | 0
5417 | 1087.0664 | 0
5418 | 1086.631 | 0
5419 | 1086.618 | 0
5420 | 1086.4 | 0
5421 | 1086.4 | 0
5422 | 1086.354 | 0
5423 | 1086.2248 | 0
5424 | 1085.9861 | 0
5425 | 1085.7551 | 0
5426 | 1085.7551 | 0
5427 | 1085.638 | 0
5428 | 1085.6 | 0
5429 | 1085.6 | 0
5430 | 1084.892 | 0
5431 | 1084.8 | 0
5432 | 1084.8 | 0
5433 | 1084.3737 | 0
5434 | 1084.0897 | 0
5435 | 1083.978 | 0
5436 | 1083.813 | 0
5437 | 1083.6514 | 0
5438 | 1083.6407 | 0
5439 | 1083.2 | 0
5440 | 1083.2 | 0
5441 | 1083.1262 | 0
5442 | 1082.9924 | 0
5443 | 1082.942 | 0
5444 | 1082.8362 | 0
5445 | 1082.752 | 0
5446 | 1082.4 | 0
5447 | 1082.4 | 0
5448 | 1082.229 | 0
5449 | 1082.1742 | 0
5450 | 1081.973 | 0
5451 | 1081.9499 | 0
5452 | 1081.611 | 0
5453 | 1081.511 | 0
5454 | 1081.3773 | 0
5455 | 1081.276 | 0
5456 | 1081.252 | 0
5457 | 1081.2144 | 0
5458 | 1081.1711 | 0
5459 | 1081.05 | 0
5460 | 1080.957 | 0
5461 | 1080.8 | 0
5462 | 1080.8 | 0
5463 | 1080.5804 | 0
5464 | 1080.559 | 0
5465 | 1080.396 | 0
5466 | 1080.054 | 0
5467 | 1080 | 0
5468 | 1079.7616 | 0
5469 | 1079.591 | 0
5470 | 1079.2074 | 0
5471 | 1079.2 | 0
5472 | 1078.9867 | 0
5473 | 1078.8483 | 0
5474 | 1078.4 | 0
5475 | 1078.2723 | 0
5476 | 1078.1882 | 0
5477 | 1078.088 | 0
5478 | 1078.045 | 0
5479 | 1077.8998 | 0
5480 | 1077.866 | 0
5481 | 1077.8269 | 0
5482 | 1077.6 | 0
5483 | 1077.6 | 0
5484 | 1077.5727 | 0
5485 | 1077.5368 | 0
5486 | 1077.4669 | 0
5487 | 1077.4462 | 0
5488 | 1077.3961 | 0
5489 | 1077.291 | 0
5490 | 1076.9383 | 0
5491 | 1076.9171 | 0
5492 | 1076.8 | 0
5493 | 1076.8 | 0
5494 | 1076.722 | 0
5495 | 1076.3005 | 0
5496 | 1076.0855 | 0
5497 | 1076.0855 | 0
5498 | 1076.0855 | 0
5499 | 1076.0594 | 0
5500 | 1076 | 0
5501 | 1076 | 0
5502 | 1076 | 0
5503 | 1075.8529 | 0
5504 | 1075.5123 | 0
5505 | 1075.3302 | 0
5506 | 1075.3302 | 0
5507 | 1075.2 | 0
5508 | 1075.2 | 0
5509 | 1074.5947 | 0
5510 | 1074.5947 | 0
5511 | 1074.4 | 0
5512 | 1074.33 | 0
5513 | 1074.0238 | 0
5514 | 1073.9732 | 0
5515 | 1073.6523 | 0
5516 | 1073.6 | 0
5517 | 1073.6 | 0
5518 | 1073.6 | 0
5519 | 1073.6 | 0
5520 | 1073.537 | 0
5521 | 1073.4084 | 0
5522 | 1073.3228 | 0
5523 | 1072.8488 | 0
5524 | 1072.8 | 0
5525 | 1072.8 | 0
5526 | 1072.8 | 0
5527 | 1072.5339 | 0
5528 | 1072.2006 | 0
5529 | 1072.122 | 0
5530 | 1072 | 0
5531 | 1072 | 0
5532 | 1071.8147 | 0
5533 | 1071.6526 | 0
5534 | 1071.6104 | 0
5535 | 1071.458 | 0
5536 | 1071.4449 | 0
5537 | 1071.439 | 0
5538 | 1071.3572 | 0
5539 | 1071.282 | 0
5540 | 1071.2507 | 0
5541 | 1071.2 | 0
5542 | 1071.05 | 0
5543 | 1070.4841 | 0
5544 | 1070.4651 | 0
5545 | 1070.4 | 0
5546 | 1070.4 | 0
5547 | 1070.4 | 0
5548 | 1070.1512 | 0
5549 | 1069.6 | 0
5550 | 1069.4461 | 0
5551 | 1069.424 | 0
5552 | 1069.424 | 0
5553 | 1069.3668 | 0
5554 | 1068.8 | 0
5555 | 1068.7106 | 0
5556 | 1068.5028 | 0
5557 | 1068.0858 | 0
5558 | 1067.9509 | 0
5559 | 1067.8206 | 0
5560 | 1067.6514 | 0
5561 | 1067.464 | 0
5562 | 1067.315 | 0
5563 | 1067.268 | 0
5564 | 1067.2395 | 0
5565 | 1067.2 | 0
5566 | 1066.826 | 0
5567 | 1066.4502 | 0
5568 | 1066.4 | 0
5569 | 1066.2364 | 0
5570 | 1066.076 | 0
5571 | 1065.6 | 0
5572 | 1065.5889 | 0
5573 | 1065.211 | 0
5574 | 1064.8 | 0
5575 | 1064.8 | 0
5576 | 1064.339 | 0
5577 | 1064.2324 | 0
5578 | 1064 | 0
5579 | 1064 | 0
5580 | 1063.922 | 0
5581 | 1062.6763 | 0
5582 | 1062.5736 | 0
5583 | 1062.166 | 0
5584 | 1061.6 | 0
5585 | 1061.5812 | 0
5586 | 1061.564 | 0
5587 | 1061.519 | 0
5588 | 1061.386 | 0
5589 | 1061.094 | 0
5590 | 1060.8905 | 0
5591 | 1060.777 | 0
5592 | 1060.1998 | 0
5593 | 1060.1419 | 0
5594 | 1059.8843 | 0
5595 | 1059.7836 | 0
5596 | 1059.5877 | 0
5597 | 1059.333 | 0
5598 | 1058.8184 | 0
5599 | 1058.51 | 0
5600 | 1058.1277 | 0
5601 | 1057.9646 | 0
5602 | 1057.6778 | 0
5603 | 1057.6 | 0
5604 | 1057.6 | 0
5605 | 1057.6 | 0
5606 | 1057.4129 | 0
5607 | 1057.156 | 0
5608 | 1056.4835 | 0
5609 | 1056 | 0
5610 | 1056 | 0
5611 | 1056 | 0
5612 | 1056 | 0
5613 | 1055.859 | 0
5614 | 1055.456 | 0
5615 | 1055.365 | 0
5616 | 1055.2 | 0
5617 | 1055.169 | 0
5618 | 1055.099 | 0
5619 | 1055.082 | 0
5620 | 1054.9635 | 0
5621 | 1054.7357 | 0
5622 | 1054.7357 | 0
5623 | 1054.7081 | 0
5624 | 1054.4 | 0
5625 | 1054.4 | 0
5626 | 1054.4 | 0
5627 | 1054.2475 | 0
5628 | 1054.0186 | 0
5629 | 1053.7961 | 0
5630 | 1053.719 | 0
5631 | 1053.6 | 0
5632 | 1053.267 | 0
5633 | 1053.168 | 0
5634 | 1052.302 | 0
5635 | 1052 | 0
5636 | 1051.8925 | 0
5637 | 1051.3962 | 0
5638 | 1051.2209 | 0
5639 | 1051.2 | 0
5640 | 1051.2 | 0
5641 | 1051.2 | 0
5642 | 1051.1298 | 0
5643 | 1051.0647 | 0
5644 | 1051.0551 | 0
5645 | 1050.9114 | 0
5646 | 1050.829 | 0
5647 | 1050.4 | 0
5648 | 1050.3472 | 0
5649 | 1050.3226 | 0
5650 | 1050.3226 | 0
5651 | 1050.3226 | 0
5652 | 1050.113 | 0
5653 | 1049.8395 | 0
5654 | 1049.667 | 0
5655 | 1049.6 | 0
5656 | 1049.5751 | 0
5657 | 1049.4094 | 0
5658 | 1049.2758 | 0
5659 | 1049.2511 | 0
5660 | 1049.1048 | 0
5661 | 1048.5359 | 0
5662 | 1048.2088 | 0
5663 | 1048.116 | 0
5664 | 1048 | 0
5665 | 1048 | 0
5666 | 1047.8219 | 0
5667 | 1047.7675 | 0
5668 | 1047.7675 | 0
5669 | 1047.2 | 0
5670 | 1047.146 | 0
5671 | 1047.104 | 0
5672 | 1046.5357 | 0
5673 | 1046.5245 | 0
5674 | 1046.4 | 0
5675 | 1046.4 | 0
5676 | 1046.3142 | 0
5677 | 1046.053 | 0
5678 | 1045.7588 | 0
5679 | 1045.7035 | 0
5680 | 1045.6 | 0
5681 | 1045.6 | 0
5682 | 1045.1739 | 0
5683 | 1044.9992 | 0
5684 | 1044.814 | 0
5685 | 1044.8 | 0
5686 | 1044.8 | 0
5687 | 1044.668 | 0
5688 | 1044.091 | 0
5689 | 1044.046 | 0
5690 | 1044 | 0
5691 | 1044 | 0
5692 | 1044 | 0
5693 | 1043.7397 | 0
5694 | 1043.557 | 0
5695 | 1043.2 | 0
5696 | 1043.0311 | 0
5697 | 1042.9674 | 0
5698 | 1042.9327 | 0
5699 | 1042.651 | 0
5700 | 1042.494 | 0
5701 | 1042.2318 | 0
5702 | 1041.9355 | 0
5703 | 1041.8741 | 0
5704 | 1041.8558 | 0
5705 | 1041.693 | 0
5706 | 1041.6 | 0
5707 | 1041.4963 | 0
5708 | 1041.064 | 0
5709 | 1040.947 | 0
5710 | 1040.8 | 0
5711 | 1040.75 | 0
5712 | 1040.5708 | 0
5713 | 1040.3999 | 0
5714 | 1040.324 | 0
5715 | 1040.17 | 0
5716 | 1040.17 | 0
5717 | 1040.0298 | 0
5718 | 1040.0253 | 0
5719 | 1040.0253 | 0
5720 | 1040.0253 | 0
5721 | 1040 | 0
5722 | 1040 | 0
5723 | 1039.8662 | 0
5724 | 1039.674 | 0
5725 | 1039.5433 | 0
5726 | 1039.4979 | 0
5727 | 1039.4793 | 0
5728 | 1039.2 | 0
5729 | 1038.7663 | 0
5730 | 1038.644 | 0
5731 | 1038.439 | 0
5732 | 1038.0979 | 0
5733 | 1038.0979 | 0
5734 | 1038.061 | 0
5735 | 1037.8187 | 0
5736 | 1037.81 | 0
5737 | 1037.6411 | 0
5738 | 1037.6 | 0
5739 | 1037.4685 | 0
5740 | 1037.0083 | 0
5741 | 1036.9885 | 0
5742 | 1036.9712 | 0
5743 | 1036.8 | 0
5744 | 1036.8 | 0
5745 | 1036.7165 | 0
5746 | 1036.4355 | 0
5747 | 1036.3477 | 0
5748 | 1036.347 | 0
5749 | 1035.63 | 0
5750 | 1035.6122 | 0
5751 | 1035.489 | 0
5752 | 1035.3352 | 0
5753 | 1035.2371 | 0
5754 | 1035.196 | 0
5755 | 1034.934 | 0
5756 | 1034.8766 | 0
5757 | 1034.4 | 0
5758 | 1034.163 | 0
5759 | 1034.1411 | 0
5760 | 1034.1178 | 0
5761 | 1034.0283 | 0
5762 | 1033.825 | 0
5763 | 1033.754 | 0
5764 | 1033.564 | 0
5765 | 1033.486 | 0
5766 | 1033.4007 | 0
5767 | 1033.3278 | 0
5768 | 1032.9192 | 0
5769 | 1032.8 | 0
5770 | 1032.8 | 0
5771 | 1032.7373 | 0
5772 | 1032.5724 | 0
5773 | 1032.5448 | 0
5774 | 1032 | 0
5775 | 1031.9346 | 0
5776 | 1031.8818 | 0
5777 | 1031.53 | 0
5778 | 1031.203 | 0
5779 | 1031.2 | 0
5780 | 1031.199 | 0
5781 | 1031.1911 | 0
5782 | 1031.1911 | 0
5783 | 1030.8817 | 0
5784 | 1030.5004 | 0
5785 | 1030.4 | 0
5786 | 1030.094 | 0
5787 | 1029.977 | 0
5788 | 1029.964 | 0
5789 | 1029.6 | 0
5790 | 1029.466 | 0
5791 | 1029.119 | 0
5792 | 1029.119 | 0
5793 | 1028.874 | 0
5794 | 1028.83 | 0
5795 | 1028.8 | 0
5796 | 1028.635 | 0
5797 | 1028.4225 | 0
5798 | 1028.257 | 0
5799 | 1028 | 0
5800 | 1028 | 0
5801 | 1027.9858 | 0
5802 | 1027.7377 | 0
5803 | 1027.48 | 0
5804 | 1027.129 | 0
5805 | 1027.0912 | 0
5806 | 1026.622 | 0
5807 | 1026.462 | 0
5808 | 1026.4 | 0
5809 | 1026.4 | 0
5810 | 1026.3765 | 0
5811 | 1025.9707 | 0
5812 | 1025.3149 | 0
5813 | 1025.232 | 0
5814 | 1025.0301 | 0
5815 | 1024.9954 | 0
5816 | 1024.991 | 0
5817 | 1024.287 | 0
5818 | 1024.0045 | 0
5819 | 1024 | 0
5820 | 1023.3432 | 0
5821 | 1023.2276 | 0
5822 | 1023.2024 | 0
5823 | 1022.9029 | 0
5824 | 1022.571 | 0
5825 | 1022.55 | 0
5826 | 1022.4 | 0
5827 | 1022.2874 | 0
5828 | 1022.2122 | 0
5829 | 1021.6373 | 0
5830 | 1021.6 | 0
5831 | 1021.5215 | 0
5832 | 1021.1849 | 0
5833 | 1021.024 | 0
5834 | 1020.8968 | 0
5835 | 1020.8968 | 0
5836 | 1020.8308 | 0
5837 | 1020.8308 | 0
5838 | 1020.8 | 0
5839 | 1020.5365 | 0
5840 | 1020.516 | 0
5841 | 1020 | 0
5842 | 1020 | 0
5843 | 1019.8339 | 0
5844 | 1019.831 | 0
5845 | 1019.4494 | 0
5846 | 1019.4307 | 0
5847 | 1019.2 | 0
5848 | 1019.2 | 0
5849 | 1019.092 | 0
5850 | 1018.6952 | 0
5851 | 1018.4 | 0
5852 | 1018.275 | 0
5853 | 1018.1982 | 0
5854 | 1018.0681 | 0
5855 | 1017.97 | 0
5856 | 1017.789 | 0
5857 | 1017.622 | 0
5858 | 1017.2747 | 0
5859 | 1017.1236 | 0
5860 | 1017.049 | 0
5861 | 1016.8 | 0
5862 | 1016.1898 | 0
5863 | 1016.173 | 0
5864 | 1016 | 0
5865 | 1016 | 0
5866 | 1016 | 0
5867 | 1016 | 0
5868 | 1015.996 | 0
5869 | 1015.996 | 0
5870 | 1015.736 | 0
5871 | 1015.72 | 0
5872 | 1015.4608 | 0
5873 | 1015.0755 | 0
5874 | 1015.0176 | 0
5875 | 1014.4 | 0
5876 | 1014.4 | 0
5877 | 1014.359 | 0
5878 | 1014.0104 | 0
5879 | 1013.9043 | 0
5880 | 1013.2333 | 0
5881 | 1012.9324 | 0
5882 | 1012.811 | 0
5883 | 1012.5426 | 0
5884 | 1012.197 | 0
5885 | 1012 | 0
5886 | 1011.616 | 0
5887 | 1011.485 | 0
5888 | 1010.9393 | 0
5889 | 1010.911 | 0
5890 | 1010.871 | 0
5891 | 1010.5833 | 0
5892 | 1010.4706 | 0
5893 | 1010.4 | 0
5894 | 1009.939 | 0
5895 | 1009.8492 | 0
5896 | 1009.7099 | 0
5897 | 1009.6 | 0
5898 | 1009.0892 | 0
5899 | 1008.8 | 0
5900 | 1008.77 | 0
5901 | 1008.407 | 0
5902 | 1008.3985 | 0
5903 | 1008.3985 | 0
5904 | 1008.2725 | 0
5905 | 1008 | 0
5906 | 1007.9081 | 0
5907 | 1007.2 | 0
5908 | 1007.057 | 0
5909 | 1007.0171 | 0
5910 | 1006.9788 | 0
5911 | 1006.9269 | 0
5912 | 1006.925 | 0
5913 | 1006.4 | 0
5914 | 1006.4 | 0
5915 | 1005.6358 | 0
5916 | 1005.3405 | 0
5917 | 1005.2559 | 0
5918 | 1004.7203 | 0
5919 | 1004.4362 | 0
5920 | 1004.3509 | 0
5921 | 1004.2544 | 0
5922 | 1004 | 0
5923 | 1003.9848 | 0
5924 | 1003.5637 | 0
5925 | 1003.5499 | 0
5926 | 1003.5325 | 0
5927 | 1003.501 | 0
5928 | 1003.211 | 0
5929 | 1003.197 | 0
5930 | 1003.1398 | 0
5931 | 1002.649 | 0
5932 | 1002.5404 | 0
5933 | 1002.4448 | 0
5934 | 1002.3878 | 0
5935 | 1002.061 | 0
5936 | 1001.7782 | 0
5937 | 1001.4733 | 0
5938 | 1001.0427 | 0
5939 | 1001.0427 | 0
5940 | 1001.0427 | 0
5941 | 1000.8 | 0
5942 | 1000.6964 | 0
5943 | 1000.3072 | 0
5944 | 1000.1103 | 0
5945 | 1000 | 0
5946 | 999.966 | 0
5947 | 999.303 | 0
5948 | 999.2 | 0
5949 | 999.188 | 0
5950 | 999.0366 | 0
5951 | 998.7939 | 0
5952 | 998.7617 | 0
5953 | 998.7289 | 0
5954 | 998.4 | 0
5955 | 998.236 | 0
5956 | 998.1356 | 0
5957 | 997.74 | 0
5958 | 997.6 | 0
5959 | 997.558 | 0
5960 | 997.388 | 0
5961 | 997.387 | 0
5962 | 996.949 | 0
5963 | 996.848 | 0
5964 | 996.8117 | 0
5965 | 996.8 | 0
5966 | 996.612 | 0
5967 | 996 | 0
5968 | 995.2755 | 0
5969 | 995.2 | 0
5970 | 995.2 | 0
5971 | 994.822 | 0
5972 | 994.4167 | 0
5973 | 994.4 | 0
5974 | 994.134 | 0
5975 | 994.1031 | 0
5976 | 993.966 | 0
5977 | 993.9174 | 0
5978 | 993.8319 | 0
5979 | 993.6875 | 0
5980 | 993.6 | 0
5981 | 993.5084 | 0
5982 | 993.2035 | 0
5983 | 992.8 | 0
5984 | 992.7355 | 0
5985 | 992.2165 | 0
5986 | 992.147 | 0
5987 | 992 | 0
5988 | 991.3731 | 0
5989 | 991.2 | 0
5990 | 991.14 | 0
5991 | 991.1314 | 0
5992 | 991.078 | 0
5993 | 991.068 | 0
5994 | 990.4614 | 0
5995 | 990.0065 | 0
5996 | 989.602 | 0
5997 | 989.561 | 0
5998 | 989.2744 | 0
5999 | 989.2744 | 0
6000 | 988.9209 | 0
6001 | 988.8 | 0
6002 | 988.8 | 0
6003 | 988.5389 | 0
6004 | 988.449 | 0
6005 | 988.3687 | 0
6006 | 988.3687 | 0
6007 | 987.833 | 0
6008 | 987.823 | 0
6009 | 987.594 | 0
6010 | 986.9251 | 0
6011 | 986.7115 | 0
6012 | 985.6059 | 0
6013 | 985.6 | 0
6014 | 985.6 | 0
6015 | 985.1178 | 0
6016 | 984.961 | 0
6017 | 984.8613 | 0
6018 | 984.8 | 0
6019 | 983.6487 | 0
6020 | 983.2 | 0
6021 | 983.0315 | 0
6022 | 982.8432 | 0
6023 | 982.8432 | 0
6024 | 982.402 | 0
6025 | 982.4 | 0
6026 | 981.6 | 0
6027 | 981.3959 | 0
6028 | 981.304 | 0
6029 | 980.994 | 0
6030 | 980.8 | 0
6031 | 980.4482 | 0
6032 | 980.197 | 0
6033 | 979.933 | 0
6034 | 979.2 | 0
6035 | 979.152 | 0
6036 | 979.12 | 0
6037 | 979.053 | 0
6038 | 978.9424 | 0
6039 | 978.516 | 0
6040 | 978.4 | 0
6041 | 978.4 | 0
6042 | 978.1652 | 0
6043 | 977.329 | 0
6044 | 977.25 | 0
6045 | 976.907 | 0
6046 | 976.828 | 0
6047 | 976.8 | 0
6048 | 976.8 | 0
6049 | 976.5554 | 0
6050 | 976.1213 | 0
6051 | 976.035 | 0
6052 | 976.002 | 0
6053 | 975.9364 | 0
6054 | 975.8383 | 0
6055 | 975.5698 | 0
6056 | 975.2784 | 0
6057 | 975.268 | 0
6058 | 974.5728 | 0
6059 | 974.555 | 0
6060 | 974.019 | 0
6061 | 973.8643 | 0
6062 | 973.8643 | 0
6063 | 973.6 | 0
6064 | 973.1736 | 0
6065 | 973.1736 | 0
6066 | 973.1736 | 0
6067 | 972.841 | 0
6068 | 972.737 | 0
6069 | 972.383 | 0
6070 | 972.3574 | 0
6071 | 972.165 | 0
6072 | 972 | 0
6073 | 971.536 | 0
6074 | 971.201 | 0
6075 | 971.2 | 0
6076 | 971.1397 | 0
6077 | 970.887 | 0
6078 | 970.8864 | 0
6079 | 970.741 | 0
6080 | 970.4 | 0
6081 | 970.3841 | 0
6082 | 970.1509 | 0
6083 | 969.7735 | 0
6084 | 969.506 | 0
6085 | 969.134 | 0
6086 | 969.0295 | 0
6087 | 968.9779 | 0
6088 | 968.8011 | 0
6089 | 968.8 | 0
6090 | 968.3737 | 0
6091 | 968.3388 | 0
6092 | 968 | 0
6093 | 967.693 | 0
6094 | 967.4928 | 0
6095 | 967.4233 | 0
6096 | 967.2088 | 0
6097 | 967.2 | 0
6098 | 967.2 | 0
6099 | 966.9575 | 0
6100 | 966.9575 | 0
6101 | 966.93 | 0
6102 | 966.5111 | 0
6103 | 966.2668 | 0
6104 | 966.192 | 0
6105 | 966.144 | 0
6106 | 965.839 | 0
6107 | 965.4739 | 0
6108 | 965.107 | 0
6109 | 964.8 | 0
6110 | 964.8 | 0
6111 | 964.4063 | 0
6112 | 964.1947 | 0
6113 | 964 | 0
6114 | 963.4036 | 0
6115 | 963.2 | 0
6116 | 963.2 | 0
6117 | 962.7957 | 0
6118 | 962.5079 | 0
6119 | 962.443 | 0
6120 | 962.4338 | 0
6121 | 962.0602 | 0
6122 | 961.6 | 0
6123 | 961.6 | 0
6124 | 961.5296 | 0
6125 | 961.4501 | 0
6126 | 961.3246 | 0
6127 | 961.0472 | 0
6128 | 961.001 | 0
6129 | 960.8 | 0
6130 | 960.752 | 0
6131 | 960.7413 | 0
6132 | 960.2503 | 0
6133 | 960 | 0
6134 | 960 | 0
6135 | 959.8536 | 0
6136 | 959.437 | 0
6137 | 958.726 | 0
6138 | 958.609 | 0
6139 | 958.182 | 0
6140 | 957.674 | 0
6141 | 957.647 | 0
6142 | 957.6 | 0
6143 | 957.6 | 0
6144 | 957.501 | 0
6145 | 956.9115 | 0
6146 | 956.861 | 0
6147 | 956.4739 | 0
6148 | 956.176 | 0
6149 | 956.176 | 0
6150 | 955.9065 | 0
6151 | 955.563 | 0
6152 | 955.4405 | 0
6153 | 955.36 | 0
6154 | 955.2158 | 0
6155 | 954.794 | 0
6156 | 954.5252 | 0
6157 | 954.5088 | 0
6158 | 954.4075 | 0
6159 | 954.4 | 0
6160 | 953.993 | 0
6161 | 953.6 | 0
6162 | 953.6 | 0
6163 | 953.4016 | 0
6164 | 952.8174 | 0
6165 | 952.8 | 0
6166 | 952.1242 | 0
6167 | 951.6977 | 0
6168 | 951.408 | 0
6169 | 951.2 | 0
6170 | 951.0801 | 0
6171 | 951.0274 | 0
6172 | 950.4987 | 0
6173 | 950.4 | 0
6174 | 950.4 | 0
6175 | 950.4 | 0
6176 | 949.841 | 0
6177 | 949.7888 | 0
6178 | 949.6904 | 0
6179 | 949.6 | 0
6180 | 949.6 | 0
6181 | 949.6 | 0
6182 | 949.6 | 0
6183 | 949.5925 | 0
6184 | 949.208 | 0
6185 | 948.6415 | 0
6186 | 948.631 | 0
6187 | 948.3591 | 0
6188 | 947.273 | 0
6189 | 946.9489 | 0
6190 | 946.4 | 0
6191 | 946.1464 | 0
6192 | 945.9468 | 0
6193 | 945.9063 | 0
6194 | 945.9063 | 0
6195 | 945.8787 | 0
6196 | 945.2549 | 0
6197 | 945.1432 | 0
6198 | 944.8 | 0
6199 | 944.397 | 0
6200 | 944.3424 | 0
6201 | 944.1649 | 0
6202 | 943.9799 | 0
6203 | 943.5293 | 0
6204 | 943.4742 | 0
6205 | 943.2 | 0
6206 | 943.2 | 0
6207 | 943.2 | 0
6208 | 942.426 | 0
6209 | 942.4 | 0
6210 | 942.4 | 0
6211 | 942.4 | 0
6212 | 942.4 | 0
6213 | 942.1656 | 0
6214 | 941.4022 | 0
6215 | 940.8 | 0
6216 | 939.5312 | 0
6217 | 939.3301 | 0
6218 | 939.3183 | 0
6219 | 939.259 | 0
6220 | 938.7295 | 0
6221 | 938.571 | 0
6222 | 937.788 | 0
6223 | 937.6 | 0
6224 | 936.9874 | 0
6225 | 936.9532 | 0
6226 | 936.672 | 0
6227 | 936.447 | 0
6228 | 936.0094 | 0
6229 | 936 | 0
6230 | 935.942 | 0
6231 | 935.4336 | 0
6232 | 935.0749 | 0
6233 | 934.4 | 0
6234 | 934.389 | 0
6235 | 934.3477 | 0
6236 | 934.1267 | 0
6237 | 934.1104 | 0
6238 | 933.8677 | 0
6239 | 933.853 | 0
6240 | 933.7278 | 0
6241 | 933.699 | 0
6242 | 933.6 | 0
6243 | 933.17 | 0
6244 | 933.114 | 0
6245 | 933.1028 | 0
6246 | 932.616 | 0
6247 | 932.4233 | 0
6248 | 932.415 | 0
6249 | 932 | 0
6250 | 932 | 0
6251 | 931.0419 | 0
6252 | 930.985 | 0
6253 | 930.64 | 0
6254 | 930.6139 | 0
6255 | 930.0798 | 0
6256 | 930.0669 | 0
6257 | 929.6605 | 0
6258 | 929.5402 | 0
6259 | 928.89 | 0
6260 | 928.5379 | 0
6261 | 928.2792 | 0
6262 | 927.5885 | 0
6263 | 927.2 | 0
6264 | 927.2 | 0
6265 | 926.8978 | 0
6266 | 926.8872 | 0
6267 | 926.8434 | 0
6268 | 926.6013 | 0
6269 | 925.5164 | 0
6270 | 925.2842 | 0
6271 | 924.9656 | 0
6272 | 924.647 | 0
6273 | 924 | 0
6274 | 923.2 | 0
6275 | 923.2 | 0
6276 | 923.0026 | 0
6277 | 923.0026 | 0
6278 | 922.415 | 0
6279 | 921.625 | 0
6280 | 921.6 | 0
6281 | 921.6 | 0
6282 | 920.542 | 0
6283 | 920.17 | 0
6284 | 920.1355 | 0
6285 | 920 | 0
6286 | 919.991 | 0
6287 | 919.3003 | 0
6288 | 918.666 | 0
6289 | 918.6645 | 0
6290 | 918.6096 | 0
6291 | 918.411 | 0
6292 | 918.4 | 0
6293 | 918.03 | 0
6294 | 917.901 | 0
6295 | 916.9976 | 0
6296 | 916.0101 | 0
6297 | 916 | 0
6298 | 915.603 | 0
6299 | 915.477 | 0
6300 | 915.255 | 0
6301 | 915.2 | 0
6302 | 914.8386 | 0
6303 | 914.3338 | 0
6304 | 914.2514 | 0
6305 | 914.0068 | 0
6306 | 913.5158 | 0
6307 | 912.0448 | 0
6308 | 912 | 0
6309 | 911.7028 | 0
6310 | 911.7028 | 0
6311 | 911.6949 | 0
6312 | 911.5146 | 0
6313 | 911.1879 | 0
6314 | 910.899 | 0
6315 | 910.3214 | 0
6316 | 909.1027 | 0
6317 | 908.4526 | 0
6318 | 908.0488 | 0
6319 | 907.915 | 0
6320 | 907.5587 | 0
6321 | 906.4 | 0
6322 | 906.4 | 0
6323 | 906.2351 | 0
6324 | 906.1606 | 0
6325 | 906.1606 | 0
6326 | 906.1208 | 0
6327 | 905.877 | 0
6328 | 905.6 | 0
6329 | 905.5732 | 0
6330 | 905.477 | 0
6331 | 905.4251 | 0
6332 | 905.259 | 0
6333 | 905.101 | 0
6334 | 904.8 | 0
6335 | 904.3835 | 0
6336 | 904.057 | 0
6337 | 904 | 0
6338 | 904 | 0
6339 | 903.9083 | 0
6340 | 903.8122 | 0
6341 | 903.735 | 0
6342 | 903.2 | 0
6343 | 902.483 | 0
6344 | 902.102 | 0
6345 | 901.6 | 0
6346 | 900.704 | 0
6347 | 900.697 | 0
6348 | 900.2029 | 0
6349 | 900.079 | 0
6350 | 899.6868 | 0
6351 | 899.541 | 0
6352 | 899.2 | 0
6353 | 898.8077 | 0
6354 | 898.5931 | 0
6355 | 898.574 | 0
6356 | 898.4 | 0
6357 | 898.155 | 0
6358 | 898.0699 | 0
6359 | 897.95 | 0
6360 | 897.6 | 0
6361 | 896.5867 | 0
6362 | 896 | 0
6363 | 895.8243 | 0
6364 | 895.1263 | 0
6365 | 895.1263 | 0
6366 | 895.0328 | 0
6367 | 894.9055 | 0
6368 | 894.813 | 0
6369 | 894.4 | 0
6370 | 893.7415 | 0
6371 | 892.9213 | 0
6372 | 892.8 | 0
6373 | 892.8 | 0
6374 | 891.925 | 0
6375 | 891.6729 | 0
6376 | 891.6729 | 0
6377 | 891.524 | 0
6378 | 891.267 | 0
6379 | 890.7147 | 0
6380 | 890.4 | 0
6381 | 890.4 | 0
6382 | 889.7008 | 0
6383 | 889.368 | 0
6384 | 889.2698 | 0
6385 | 889.2437 | 0
6386 | 889.005 | 0
6387 | 888.9102 | 0
6388 | 888.252 | 0
6389 | 888.082 | 0
6390 | 888.077 | 0
6391 | 888.0562 | 0
6392 | 888 | 0
6393 | 887.264 | 0
6394 | 887.0799 | 0
6395 | 886.366 | 0
6396 | 886.201 | 0
6397 | 886.193 | 0
6398 | 885.9086 | 0
6399 | 885.4685 | 0
6400 | 884.928 | 0
6401 | 883.3154 | 0
6402 | 883.2 | 0
6403 | 882.8525 | 0
6404 | 882.8417 | 0
6405 | 882.8235 | 0
6406 | 882.694 | 0
6407 | 882.651 | 0
6408 | 882.624 | 0
6409 | 882.579 | 0
6410 | 882.1064 | 0
6411 | 881.612 | 0
6412 | 881.4527 | 0
6413 | 881.3451 | 0
6414 | 880.938 | 0
6415 | 880.8 | 0
6416 | 880.622 | 0
6417 | 880 | 0
6418 | 879.9313 | 0
6419 | 879.7304 | 0
6420 | 879.2406 | 0
6421 | 879.0094 | 0
6422 | 878.5446 | 0
6423 | 878.4 | 0
6424 | 877.8811 | 0
6425 | 877.6 | 0
6426 | 877.3751 | 0
6427 | 876.805 | 0
6428 | 876.8 | 0
6429 | 876.8 | 0
6430 | 876.8 | 0
6431 | 876.5771 | 0
6432 | 876.383 | 0
6433 | 876.0043 | 0
6434 | 875.7872 | 0
6435 | 875.2 | 0
6436 | 874.7245 | 0
6437 | 874.2602 | 0
6438 | 874.205 | 0
6439 | 873.0622 | 0
6440 | 873.013 | 0
6441 | 872.9741 | 0
6442 | 872.0645 | 0
6443 | 871.996 | 0
6444 | 871.6431 | 0
6445 | 871.2 | 0
6446 | 870.547 | 0
6447 | 870.304 | 0
6448 | 870.2682 | 0
6449 | 870.2617 | 0
6450 | 869.633 | 0
6451 | 869.487 | 0
6452 | 866.892 | 0
6453 | 866.164 | 0
6454 | 866.1271 | 0
6455 | 864.861 | 0
6456 | 864.8 | 0
6457 | 864.1732 | 0
6458 | 863.605 | 0
6459 | 863.52 | 0
6460 | 863.2 | 0
6461 | 862.4134 | 0
6462 | 861.9735 | 0
6463 | 861.226 | 0
6464 | 860.9694 | 0
6465 | 860.8 | 0
6466 | 860.8 | 0
6467 | 860.713 | 0
6468 | 860.5921 | 0
6469 | 860.551 | 0
6470 | 859.624 | 0
6471 | 859.4179 | 0
6472 | 858.742 | 0
6473 | 858.4429 | 0
6474 | 858.4 | 0
6475 | 858.2665 | 0
6476 | 858.247 | 0
6477 | 857.2624 | 0
6478 | 857.0857 | 0
6479 | 856.951 | 0
6480 | 856.555 | 0
6481 | 856.2803 | 0
6482 | 856 | 0
6483 | 855.7574 | 0
6484 | 855.543 | 0
6485 | 855.4501 | 0
6486 | 855.4089 | 0
6487 | 855.2 | 0
6488 | 855.171 | 0
6489 | 854.4 | 0
6490 | 853.6 | 0
6491 | 853.2232 | 0
6492 | 852.8 | 0
6493 | 852.6441 | 0
6494 | 851.9365 | 0
6495 | 851.5291 | 0
6496 | 851.215 | 0
6497 | 851.2 | 0
6498 | 850.4 | 0
6499 | 850.341 | 0
6500 | 849.9704 | 0
6501 | 848.8505 | 0
6502 | 848.7901 | 0
6503 | 848.4842 | 0
6504 | 848.1616 | 0
6505 | 848.1598 | 0
6506 | 848 | 0
6507 | 847.2718 | 0
6508 | 846.3463 | 0
6509 | 846.0043 | 0
6510 | 845.6 | 0
6511 | 845.369 | 0
6512 | 845.333 | 0
6513 | 845.2702 | 0
6514 | 844.8066 | 0
6515 | 844.7064 | 0
6516 | 843.9182 | 0
6517 | 843.7136 | 0
6518 | 843.2 | 0
6519 | 842.753 | 0
6520 | 842.1704 | 0
6521 | 842.0808 | 0
6522 | 840.5623 | 0
6523 | 840 | 0
6524 | 840 | 0
6525 | 839.555 | 0
6526 | 839.44 | 0
6527 | 838.4 | 0
6528 | 838.4 | 0
6529 | 837.4805 | 0
6530 | 837.0277 | 0
6531 | 836.8 | 0
6532 | 836.64 | 0
6533 | 836 | 0
6534 | 835.9855 | 0
6535 | 835.7275 | 0
6536 | 835.519 | 0
6537 | 833.8618 | 0
6538 | 833.363 | 0
6539 | 832.2691 | 0
6540 | 831.2 | 0
6541 | 831.19 | 0
6542 | 831.1376 | 0
6543 | 830.0973 | 0
6544 | 829.986 | 0
6545 | 829.6 | 0
6546 | 829.113 | 0
6547 | 828.8 | 0
6548 | 828.8 | 0
6549 | 828.8 | 0
6550 | 828.4586 | 0
6551 | 828.43 | 0
6552 | 828.2161 | 0
6553 | 827.5326 | 0
6554 | 827.2 | 0
6555 | 826.7486 | 0
6556 | 826.6632 | 0
6557 | 826.5843 | 0
6558 | 826.4 | 0
6559 | 825.915 | 0
6560 | 825.6 | 0
6561 | 824.194 | 0
6562 | 823.7824 | 0
6563 | 823.5547 | 0
6564 | 823.2952 | 0
6565 | 823.2952 | 0
6566 | 822.6911 | 0
6567 | 822.307 | 0
6568 | 822.233 | 0
6569 | 821.2232 | 0
6570 | 820.8 | 0
6571 | 820.686 | 0
6572 | 820.5325 | 0
6573 | 820.5103 | 0
6574 | 820 | 0
6575 | 819.4309 | 0
6576 | 819.3456 | 0
6577 | 818.6338 | 0
6578 | 818.4 | 0
6579 | 817.356 | 0
6580 | 817.3512 | 0
6581 | 816.4272 | 0
6582 | 816 | 0
6583 | 815.6977 | 0
6584 | 815.3764 | 0
6585 | 815.3764 | 0
6586 | 814.7659 | 0
6587 | 813.6256 | 0
6588 | 813.6256 | 0
6589 | 813.6014 | 0
6590 | 813.6 | 0
6591 | 812.644 | 0
6592 | 812.402 | 0
6593 | 812.063 | 0
6594 | 812 | 0
6595 | 811.981 | 0
6596 | 811.5093 | 0
6597 | 810.397 | 0
6598 | 809.4815 | 0
6599 | 809.242 | 0
6600 | 808.8 | 0
6601 | 807.601 | 0
6602 | 806.8654 | 0
6603 | 806.512 | 0
6604 | 806.1299 | 0
6605 | 806.027 | 0
6606 | 805.6 | 0
6607 | 804.961 | 0
6608 | 804.6468 | 0
6609 | 803.82 | 0
6610 | 803.013 | 0
6611 | 802.622 | 0
6612 | 802.2911 | 0
6613 | 802.242 | 0
6614 | 802.2369 | 0
6615 | 801.8299 | 0
6616 | 800.5026 | 0
6617 | 799.5406 | 0
6618 | 799.2 | 0
6619 | 799.112 | 0
6620 | 799.087 | 0
6621 | 798.5303 | 0
6622 | 798.4 | 0
6623 | 797.7399 | 0
6624 | 797.6 | 0
6625 | 797.6 | 0
6626 | 797.587 | 0
6627 | 796.5663 | 0
6628 | 795.2945 | 0
6629 | 793.1348 | 0
6630 | 792 | 0
6631 | 791.3395 | 0
6632 | 791.2837 | 0
6633 | 790.3815 | 0
6634 | 789.213 | 0
6635 | 788.801 | 0
6636 | 787.8808 | 0
6637 | 785.5354 | 0
6638 | 785.1463 | 0
6639 | 784.8 | 0
6640 | 784.8 | 0
6641 | 784.747 | 0
6642 | 784.7098 | 0
6643 | 782.7914 | 0
6644 | 782.6071 | 0
6645 | 782.5933 | 0
6646 | 782.5449 | 0
6647 | 781.83 | 0
6648 | 781.8035 | 0
6649 | 780.4728 | 0
6650 | 780.334 | 0
6651 | 780 | 0
6652 | 779.6512 | 0
6653 | 779.2 | 0
6654 | 779.2 | 0
6655 | 778.4 | 0
6656 | 777.6212 | 0
6657 | 777.272 | 0
6658 | 776.4017 | 0
6659 | 776.1206 | 0
6660 | 774.9473 | 0
6661 | 774.4 | 0
6662 | 773.4902 | 0
6663 | 772.296 | 0
6664 | 771.604 | 0
6665 | 771.2136 | 0
6666 | 770.837 | 0
6667 | 770.8032 | 0
6668 | 770.8032 | 0
6669 | 769.6 | 0
6670 | 768.029 | 0
6671 | 768 | 0
6672 | 767.602 | 0
6673 | 764 | 0
6674 | 762.515 | 0
6675 | 761.9789 | 0
6676 | 761.6585 | 0
6677 | 760 | 0
6678 | 759.7922 | 0
6679 | 759.475 | 0
6680 | 759.2 | 0
6681 | 758.1283 | 0
6682 | 758.1283 | 0
6683 | 756.9896 | 0
6684 | 756.9896 | 0
6685 | 756.627 | 0
6686 | 756.271 | 0
6687 | 755.2 | 0
6688 | 754.857 | 0
6689 | 754.4 | 0
6690 | 753.773 | 0
6691 | 752.979 | 0
6692 | 752.8 | 0
6693 | 752.1548 | 0
6694 | 750.2304 | 0
6695 | 750.082 | 0
6696 | 747.1449 | 0
6697 | 746.5353 | 0
6698 | 745.043 | 0
6699 | 743.1759 | 0
6700 | 741.7717 | 0
6701 | 741.6 | 0
6702 | 741.6 | 0
6703 | 740.535 | 0
6704 | 740.237 | 0
6705 | 739.3182 | 0
6706 | 739.0318 | 0
6707 | 738.4 | 0
6708 | 738.0913 | 0
6709 | 736.9597 | 0
6710 | 734.6806 | 0
6711 | 734.4698 | 0
6712 | 734.4 | 0
6713 | 733.5934 | 0
6714 | 730.0529 | 0
6715 | 729.6 | 0
6716 | 729.5043 | 0
6717 | 728.8 | 0
6718 | 728.4592 | 0
6719 | 727.5949 | 0
6720 | 727.2 | 0
6721 | 726.714 | 0
6722 | 725.6 | 0
6723 | 724.5973 | 0
6724 | 723.729 | 0
6725 | 723.2 | 0
6726 | 721.6 | 0
6727 | 720.8 | 0
6728 | 720.5879 | 0
6729 | 720.376 | 0
6730 | 717.6 | 0
6731 | 716.923 | 0
6732 | 716.419 | 0
6733 | 716.3965 | 0
6734 | 716.2392 | 0
6735 | 715.847 | 0
6736 | 715.8188 | 0
6737 | 715.661 | 0
6738 | 715.5485 | 0
6739 | 714.1672 | 0
6740 | 714.13 | 0
6741 | 713.6 | 0
6742 | 713.0577 | 0
6743 | 712.7858 | 0
6744 | 711.9834 | 0
6745 | 709.9428 | 0
6746 | 709.607 | 0
6747 | 708.8 | 0
6748 | 708.5433 | 0
6749 | 707.951 | 0
6750 | 706.4 | 0
6751 | 706.0992 | 0
6752 | 705.6 | 0
6753 | 704.9694 | 0
6754 | 704.9694 | 0
6755 | 704.878 | 0
6756 | 704 | 0
6757 | 700.8 | 0
6758 | 700.377 | 0
6759 | 699.2 | 0
6760 | 697.6 | 0
6761 | 697.26 | 0
6762 | 692.7019 | 0
6763 | 691.8841 | 0
6764 | 691.327 | 0
6765 | 690.747 | 0
6766 | 689.9172 | 0
6767 | 689.6 | 0
6768 | 689.6 | 0
6769 | 688.6006 | 0
6770 | 686.5273 | 0
6771 | 686.4 | 0
6772 | 686.4 | 0
6773 | 683.53 | 0
6774 | 682.6487 | 0
6775 | 680.187 | 0
6776 | 680.172 | 0
6777 | 679.439 | 0
6778 | 679.251 | 0
6779 | 678.563 | 0
6780 | 677.6 | 0
6781 | 676.8 | 0
6782 | 675.2074 | 0
6783 | 674.8497 | 0
6784 | 674.256 | 0
6785 | 673.7052 | 0
6786 | 672.9677 | 0
6787 | 672.0078 | 0
6788 | 671.56 | 0
6789 | 671.4383 | 0
6790 | 671.3979 | 0
6791 | 668.8 | 0
6792 | 668.5877 | 0
6793 | 667.766 | 0
6794 | 666.613 | 0
6795 | 664.4379 | 0
6796 | 663.439 | 0
6797 | 662.3137 | 0
6798 | 662.126 | 0
6799 | 660.137 | 0
6800 | 658.296 | 0
6801 | 657.357 | 0
6802 | 657.248 | 0
6803 | 656.8 | 0
6804 | 652.0056 | 0
6805 | 650.269 | 0
6806 | 649.4642 | 0
6807 | 646.748 | 0
6808 | 644.2323 | 0
6809 | 642.919 | 0
6810 | 641.0608 | 0
6811 | 639.7638 | 0
6812 | 639.3445 | 0
6813 | 638.4 | 0
6814 | 637.627 | 0
6815 | 636.197 | 0
6816 | 635.2 | 0
6817 | 632.529 | 0
6818 | 631.5235 | 0
6819 | 627.109 | 0
6820 | 626.4 | 0
6821 | 625.816 | 0
6822 | 624.6762 | 0
6823 | 624.5034 | 0
6824 | 622.722 | 0
6825 | 622.3062 | 0
6826 | 621.669 | 0
6827 | 619.025 | 0
6828 | 618.959 | 0
6829 | 618.406 | 0
6830 | 617.579 | 0
6831 | 615.896 | 0
6832 | 615.8259 | 0
6833 | 615.277 | 0
6834 | 612.699 | 0
6835 | 609.2833 | 0
6836 | 609.1832 | 0
6837 | 607.8018 | 0
6838 | 606.677 | 0
6839 | 606.4 | 0
6840 | 606.0119 | 0
6841 | 603.316 | 0
6842 | 602.4 | 0
6843 | 602.2764 | 0
6844 | 601.179 | 0
6845 | 596.8 | 0
6846 | 596.201 | 0
6847 | 596 | 0
6848 | 594.4 | 0
6849 | 594.4 | 0
6850 | 593.7445 | 0
6851 | 593.572 | 0
6852 | 593.521 | 0
6853 | 592.8 | 0
6854 | 592.386 | 0
6855 | 592.271 | 0
6856 | 592.193 | 0
6857 | 587.2298 | 0
6858 | 586.4 | 0
6859 | 585.8407 | 0
6860 | 584.9195 | 0
6861 | 583.859 | 0
6862 | 583.145 | 0
6863 | 580.8 | 0
6864 | 576.8 | 0
6865 | 574.5564 | 0
6866 | 571.13 | 0
6867 | 567.8021 | 0
6868 | 565.025 | 0
6869 | 563.4848 | 0
6870 | 561.581 | 0
6871 | 559.198 | 0
6872 | 558.473 | 0
6873 | 557.6649 | 0
6874 | 556.7111 | 0
6875 | 552.934 | 0
6876 | 551.2 | 0
6877 | 551.1658 | 0
6878 | 550.7832 | 0
6879 | 546.3104 | 0
6880 | 545.507 | 0
6881 | 544.574 | 0
6882 | 537.6301 | 0
6883 | 536.721 | 0
6884 | 534.4 | 0
6885 | 533.643 | 0
6886 | 532.414 | 0
6887 | 531.2024 | 0
6888 | 526.4 | 0
6889 | 524.3525 | 0
6890 | 520.8758 | 0
6891 | 520.632 | 0
6892 | 516.8685 | 0
6893 | 512.7793 | 0
6894 | 511.4393 | 0
6895 | 511.2727 | 0
6896 | 506.2713 | 0
6897 | 505.6 | 0
6898 | 505.6 | 0
6899 | 505.286 | 0
6900 | 504 | 0
6901 | 504 | 0
6902 | 503.248 | 0
6903 | 503.2 | 0
6904 | 502.0396 | 0
6905 | 502.0396 | 0
6906 | 501.6 | 0
6907 | 500.197 | 0
6908 | 498.735 | 0
6909 | 498.4 | 0
6910 | 498.4 | 0
6911 | 498.4 | 0
6912 | 497.6 | 0
6913 | 496.7951 | 0
6914 | 496.4614 | 0
6915 | 496.4614 | 0
6916 | 496.4614 | 0
6917 | 495.6645 | 0
6918 | 495.6049 | 0
6919 | 490.41 | 0
6920 | 489.888 | 0
6921 | 487.2 | 0
6922 | 485.7777 | 0
6923 | 485.6 | 0
6924 | 485.3049 | 0
6925 | 484.8 | 0
6926 | 483.7112 | 0
6927 | 482.5196 | 0
6928 | 481.147 | 0
6929 | 480.8 | 0
6930 | 479.2755 | 0
6931 | 478.9298 | 0
6932 | 478.6691 | 0
6933 | 477.6 | 0
6934 | 475.7423 | 0
6935 | 472 | 0
6936 | 472 | 0
6937 | 470.5752 | 0
6938 | 470.1641 | 0
6939 | 469.188 | 0
6940 | 467.2 | 0
6941 | 465.3827 | 0
6942 | 460.316 | 0
6943 | 458.959 | 0
6944 | 457.786 | 0
6945 | 455.687 | 0
6946 | 453.9145 | 0
6947 | 452.8416 | 0
6948 | 451.698 | 0
6949 | 451.248 | 0
6950 | 450.4 | 0
6951 | 448.6481 | 0
6952 | 445.515 | 0
6953 | 442.969 | 0
6954 | 442.7905 | 0
6955 | 440.8103 | 0
6956 | 437.884 | 0
6957 | 436.2411 | 0
6958 | 433.4498 | 0
6959 | 433.137 | 0
6960 | 432.662 | 0
6961 | 431.2 | 0
6962 | 426.0894 | 0
6963 | 424 | 0
6964 | 423.3979 | 0
6965 | 423.123 | 0
6966 | 422.9472 | 0
6967 | 421.6 | 0
6968 | 419.9601 | 0
6969 | 416.8 | 0
6970 | 415.99 | 0
6971 | 414.3719 | 0
6972 | 413.609 | 0
6973 | 413.157 | 0
6974 | 412.0002 | 0
6975 | 410.829 | 0
6976 | 410.4 | 0
6977 | 408.8037 | 0
6978 | 408.03 | 0
6979 | 407.546 | 0
6980 | 406.4615 | 0
6981 | 406.4429 | 0
6982 | 403.1901 | 0
6983 | 402.4 | 0
6984 | 400.8348 | 0
6985 | 399.101 | 0
6986 | 397.7894 | 0
6987 | 397.6 | 0
6988 | 396.46 | 0
6989 | 395.2318 | 0
6990 | 394.4 | 0
6991 | 393.167 | 0
6992 | 392.5583 | 0
6993 | 390.9227 | 0
6994 | 390.4 | 0
6995 | 390.1049 | 0
6996 | 389.912 | 0
6997 | 389.328 | 0
6998 | 388.4692 | 0
6999 | 387.2 | 0
7000 | 386.8335 | 0
7001 | 385.6939 | 0
7002 | 385.522 | 0
7003 | 384.0224 | 0
7004 | 384 | 0
7005 | 382.4 | 0
7006 | 382.4 | 0
7007 | 381.8331 | 0
7008 | 381.6 | 0
7009 | 380.8 | 0
7010 | 380 | 0
7011 | 378.6719 | 0
7012 | 378.4 | 0
7013 | 378.4 | 0
7014 | 378.0493 | 0
7015 | 376.9281 | 0
7016 | 375.588 | 0
7017 | 375.3839 | 0
7018 | 375.337 | 0
7019 | 371.3765 | 0
7020 | 369.6591 | 0
7021 | 369.6 | 0
7022 | 368.8 | 0
7023 | 368.1624 | 0
7024 | 367.3655 | 0
7025 | 367.2 | 0
7026 | 365.57 | 0
7027 | 364.7608 | 0
7028 | 364.693 | 0
7029 | 364.5171 | 0
7030 | 364.5053 | 0
7031 | 362.2986 | 0
7032 | 361.6 | 0
7033 | 357.9482 | 0
7034 | 357.6 | 0
7035 | 355.547 | 0
7036 | 354.6912 | 0
7037 | 354.4 | 0
7038 | 354.4 | 0
7039 | 353.747 | 0
7040 | 352 | 0
7041 | 348.83 | 0
7042 | 345.786 | 0
7043 | 345.2975 | 0
7044 | 344.9167 | 0
7045 | 344.1836 | 0
7046 | 343.658 | 0
7047 | 342.4 | 0
7048 | 341.8528 | 0
7049 | 341.456 | 0
7050 | 341.0682 | 0
7051 | 339.258 | 0
7052 | 338.7742 | 0
7053 | 337.397 | 0
7054 | 335.666 | 0
7055 | 335.2 | 0
7056 | 334.3604 | 0
7057 | 333.8962 | 0
7058 | 333.853 | 0
7059 | 333.7513 | 0
7060 | 332.224 | 0
7061 | 332.0389 | 0
7062 | 331.6128 | 0
7063 | 331.2 | 0
7064 | 330.448 | 0
7065 | 329.9117 | 0
7066 | 329.489 | 0
7067 | 329.02 | 0
7068 | 328.2074 | 0
7069 | 325.6 | 0
7070 | 324.8 | 0
7071 | 324.56 | 0
7072 | 324.3335 | 0
7073 | 324.2289 | 0
7074 | 323.0428 | 0
7075 | 322.859 | 0
7076 | 322.6469 | 0
7077 | 320.018 | 0
7078 | 318.7732 | 0
7079 | 318.4 | 0
7080 | 318.4 | 0
7081 | 317.159 | 0
7082 | 316 | 0
7083 | 315.607 | 0
7084 | 315.351 | 0
7085 | 315.114 | 0
7086 | 314.692 | 0
7087 | 313.792 | 0
7088 | 313.222 | 0
7089 | 311.517 | 0
7090 | 311.492 | 0
7091 | 309.6 | 0
7092 | 309.2214 | 0
7093 | 308.8 | 0
7094 | 308.0162 | 0
7095 | 307.5989 | 0
7096 | 307.348 | 0
7097 | 307.065 | 0
7098 | 306.2691 | 0
7099 | 306.2603 | 0
7100 | 305.8684 | 0
7101 | 305.6 | 0
7102 | 305.6 | 0
7103 | 304.539 | 0
7104 | 304.4113 | 0
7105 | 304.1927 | 0
7106 | 303.9311 | 0
7107 | 303.4149 | 0
7108 | 303.4149 | 0
7109 | 303.3544 | 0
7110 | 302.7034 | 0
7111 | 302.5368 | 0
7112 | 302.4 | 0
7113 | 302.112 | 0
7114 | 301.357 | 0
7115 | 301.2237 | 0
7116 | 300.6751 | 0
7117 | 299.716 | 0
7118 | 299.592 | 0
7119 | 299.2 | 0
7120 | 298.518 | 0
7121 | 298.5079 | 0
7122 | 298.4 | 0
7123 | 298.368 | 0
7124 | 298.2132 | 0
7125 | 297.305 | 0
7126 | 296.8 | 0
7127 | 296.8 | 0
7128 | 296.8 | 0
7129 | 296.7904 | 0
7130 | 296.104 | 0
7131 | 296 | 0
7132 | 296 | 0
7133 | 295.6455 | 0
7134 | 295.44 | 0
7135 | 294.906 | 0
7136 | 293.6009 | 0
7137 | 293.6 | 0
7138 | 293.458 | 0
7139 | 292.8 | 0
7140 | 292.731 | 0
7141 | 292.6697 | 0
7142 | 292 | 0
7143 | 292 | 0
7144 | 291.2 | 0
7145 | 291.2 | 0
7146 | 291.076 | 0
7147 | 290.153 | 0
7148 | 289.9125 | 0
7149 | 289.7979 | 0
7150 | 288.999 | 0
7151 | 288.8 | 0
7152 | 288.152 | 0
7153 | 287.755 | 0
7154 | 287.6502 | 0
7155 | 287.4671 | 0
7156 | 287.4345 | 0
7157 | 287.2 | 0
7158 | 287.2 | 0
7159 | 287.073 | 0
7160 | 286.4047 | 0
7161 | 286.349 | 0
7162 | 285.6 | 0
7163 | 285.1363 | 0
7164 | 285.122 | 0
7165 | 284.8 | 0
7166 | 284.3594 | 0
7167 | 284.243 | 0
7168 | 284.013 | 0
7169 | 283.6922 | 0
7170 | 283.5824 | 0
7171 | 283.379 | 0
7172 | 282.8055 | 0
7173 | 282.4089 | 0
7174 | 282.4 | 0
7175 | 282.1513 | 0
7176 | 281.969 | 0
7177 | 281.7887 | 0
7178 | 281.691 | 0
7179 | 281.379 | 0
7180 | 281.28 | 0
7181 | 281.168 | 0
7182 | 280.8 | 0
7183 | 280.4747 | 0
7184 | 280.4042 | 0
7185 | 280.1859 | 0
7186 | 279.8454 | 0
7187 | 279.7078 | 0
7188 | 279.4598 | 0
7189 | 279.2 | 0
7190 | 279.2 | 0
7191 | 278.9208 | 0
7192 | 278.114 | 0
7193 | 276.424 | 0
7194 | 276.33 | 0
7195 | 276.252 | 0
7196 | 276.049 | 0
7197 | 276 | 0
7198 | 275.21 | 0
7199 | 275.2 | 0
7200 | 274.8922 | 0
7201 | 274.4 | 0
7202 | 274.291 | 0
7203 | 273.5706 | 0
7204 | 273.494 | 0
7205 | 273.0489 | 0
7206 | 272.738 | 0
7207 | 272 | 0
7208 | 272 | 0
7209 | 271.406 | 0
7210 | 270.4 | 0
7211 | 270.3306 | 0
7212 | 269.8053 | 0
7213 | 269.6 | 0
7214 | 269.3482 | 0
7215 | 269.159 | 0
7216 | 269.004 | 0
7217 | 268.4554 | 0
7218 | 268.3642 | 0
7219 | 268 | 0
7220 | 268 | 0
7221 | 267.984 | 0
7222 | 267.282 | 0
7223 | 267.096 | 0
7224 | 266.4 | 0
7225 | 265.6099 | 0
7226 | 264.8 | 0
7227 | 264.437 | 0
7228 | 264 | 0
7229 | 263.906 | 0
7230 | 262.5234 | 0
7231 | 261.8282 | 0
7232 | 261.6 | 0
7233 | 261.3999 | 0
7234 | 261.2493 | 0
7235 | 260.8 | 0
7236 | 260.5825 | 0
7237 | 260.2743 | 0
7238 | 259.577 | 0
7239 | 259.2 | 0
7240 | 258.885 | 0
7241 | 258.7204 | 0
7242 | 258.151 | 0
7243 | 257.376 | 0
7244 | 257.187 | 0
7245 | 256.8 | 0
7246 | 256.165 | 0
7247 | 256.129 | 0
7248 | 255.553 | 0
7249 | 255.342 | 0
7250 | 255.2 | 0
7251 | 254.785 | 0
7252 | 254.4 | 0
7253 | 251.848 | 0
7254 | 251.672 | 0
7255 | 251.6319 | 0
7256 | 251.4089 | 0
7257 | 250.683 | 0
7258 | 249.9566 | 0
7259 | 248.7805 | 0
7260 | 248.715 | 0
7261 | 247.8433 | 0
7262 | 247.4402 | 0
7263 | 246.5742 | 0
7264 | 246.4 | 0
7265 | 246.146 | 0
7266 | 245.6 | 0
7267 | 244.5879 | 0
7268 | 244.417 | 0
7269 | 243.992 | 0
7270 | 243.8114 | 0
7271 | 243.7133 | 0
7272 | 243.4565 | 0
7273 | 243.2 | 0
7274 | 243.2 | 0
7275 | 242.4 | 0
7276 | 241.5452 | 0
7277 | 241.0487 | 0
7278 | 240.544 | 0
7279 | 239.297 | 0
7280 | 239.2 | 0
7281 | 238.4 | 0
7282 | 237.6 | 0
7283 | 237.6 | 0
7284 | 237.6 | 0
7285 | 237.5953 | 0
7286 | 236.4577 | 0
7287 | 236.2455 | 0
7288 | 236.1892 | 0
7289 | 236.1892 | 0
7290 | 236.032 | 0
7291 | 236 | 0
7292 | 235.767 | 0
7293 | 235.761 | 0
7294 | 235.535 | 0
7295 | 235.4123 | 0
7296 | 235.207 | 0
7297 | 235.0545 | 0
7298 | 234.947 | 0
7299 | 234.8325 | 0
7300 | 234.8325 | 0
7301 | 234.813 | 0
7302 | 234.455 | 0
7303 | 234.4 | 0
7304 | 234.4 | 0
7305 | 234.3197 | 0
7306 | 233.76 | 0
7307 | 233.4883 | 0
7308 | 233.438 | 0
7309 | 233.034 | 0
7310 | 232.2637 | 0
7311 | 231.2 | 0
7312 | 231.095 | 0
7313 | 230.7506 | 0
7314 | 230.7506 | 0
7315 | 230.684 | 0
7316 | 230.659 | 0
7317 | 230.4 | 0
7318 | 230.4 | 0
7319 | 229.93 | 0
7320 | 229.1968 | 0
7321 | 228.8 | 0
7322 | 228.6164 | 0
7323 | 228.4266 | 0
7324 | 228.211 | 0
7325 | 227.9257 | 0
7326 | 227.8445 | 0
7327 | 227.812 | 0
7328 | 227.6429 | 0
7329 | 227.2 | 0
7330 | 227.0213 | 0
7331 | 226.7086 | 0
7332 | 226.4 | 0
7333 | 226.3163 | 0
7334 | 226.1197 | 0
7335 | 225.957 | 0
7336 | 225.678 | 0
7337 | 225.6 | 0
7338 | 225.1445 | 0
7339 | 224.739 | 0
7340 | 224.5351 | 0
7341 | 224.458 | 0
7342 | 224.034 | 0
7343 | 224.0097 | 0
7344 | 224 | 0
7345 | 223.7816 | 0
7346 | 223.7582 | 0
7347 | 223.5096 | 0
7348 | 223.2 | 0
7349 | 223.2 | 0
7350 | 222.3318 | 0
7351 | 222.2043 | 0
7352 | 221.6323 | 0
7353 | 221.6 | 0
7354 | 221.19 | 0
7355 | 220.4508 | 0
7356 | 220.236 | 0
7357 | 220 | 0
7358 | 219.8735 | 0
7359 | 219.6375 | 0
7360 | 218.574 | 0
7361 | 218.4 | 0
7362 | 217.414 | 0
7363 | 216.663 | 0
7364 | 216.305 | 0
7365 | 216.0103 | 0
7366 | 215.288 | 0
7367 | 215.2119 | 0
7368 | 213.658 | 0
7369 | 212.04 | 0
7370 | 211.973 | 0
7371 | 211.252 | 0
7372 | 211.1465 | 0
7373 | 210.894 | 0
7374 | 210.6517 | 0
7375 | 210.4 | 0
7376 | 210.344 | 0
7377 | 210.0695 | 0
7378 | 209.928 | 0
7379 | 209.7018 | 0
7380 | 209.6 | 0
7381 | 209.471 | 0
7382 | 209.159 | 0
7383 | 207.884 | 0
7384 | 207.7449 | 0
7385 | 207.6748 | 0
7386 | 207.2309 | 0
7387 | 207.2 | 0
7388 | 207.0754 | 0
7389 | 206.5145 | 0
7390 | 206.4 | 0
7391 | 206.3667 | 0
7392 | 205.8624 | 0
7393 | 205.306 | 0
7394 | 205.1622 | 0
7395 | 205.1331 | 0
7396 | 205.13 | 0
7397 | 204.826 | 0
7398 | 204.693 | 0
7399 | 204.599 | 0
7400 | 204 | 0
7401 | 204 | 0
7402 | 203.7794 | 0
7403 | 203.767 | 0
7404 | 203.5578 | 0
7405 | 203.5454 | 0
7406 | 203.2065 | 0
7407 | 203.2 | 0
7408 | 203.03 | 0
7409 | 202.7269 | 0
7410 | 202.713 | 0
7411 | 202.4179 | 0
7412 | 201.4499 | 0
7413 | 200.9569 | 0
7414 | 200.8 | 0
7415 | 200 | 0
7416 | 199.8194 | 0
7417 | 199.5505 | 0
7418 | 199.3876 | 0
7419 | 199.2 | 0
7420 | 199.2 | 0
7421 | 199.0353 | 0
7422 | 198.9214 | 0
7423 | 198.7923 | 0
7424 | 198.151 | 0
7425 | 198.1192 | 0
7426 | 197.9358 | 0
7427 | 197.6 | 0
7428 | 197.3423 | 0
7429 | 197.097 | 0
7430 | 197.082 | 0
7431 | 197.058 | 0
7432 | 196.406 | 0
7433 | 195.7169 | 0
7434 | 195.463 | 0
7435 | 195.2 | 0
7436 | 195.0115 | 0
7437 | 194.8402 | 0
7438 | 194.696 | 0
7439 | 194.577 | 0
7440 | 193.991 | 0
7441 | 193.831 | 0
7442 | 193.6 | 0
7443 | 193.3915 | 0
7444 | 193.0078 | 0
7445 | 192.8 | 0
7446 | 192.7008 | 0
7447 | 192.296 | 0
7448 | 192 | 0
7449 | 191.45 | 0
7450 | 191.3722 | 0
7451 | 191.2 | 0
7452 | 189.7642 | 0
7453 | 189.5525 | 0
7454 | 188.5567 | 0
7455 | 187.2 | 0
7456 | 186.914 | 0
7457 | 186.6658 | 0
7458 | 186.4652 | 0
7459 | 186.389 | 0
7460 | 186.0829 | 0
7461 | 185.868 | 0
7462 | 185.6882 | 0
7463 | 185.42 | 0
7464 | 185.3969 | 0
7465 | 185.2027 | 0
7466 | 184.122 | 0
7467 | 183.582 | 0
7468 | 183.44 | 0
7469 | 183.1445 | 0
7470 | 183.063 | 0
7471 | 182.8679 | 0
7472 | 182.0764 | 0
7473 | 182.026 | 0
7474 | 182.01 | 0
7475 | 181.7586 | 0
7476 | 181.6734 | 0
7477 | 181.6499 | 0
7478 | 181.636 | 0
7479 | 181.6015 | 0
7480 | 181.355 | 0
7481 | 181.302 | 0
7482 | 181.165 | 0
7483 | 181.0159 | 0
7484 | 180.5099 | 0
7485 | 180 | 0
7486 | 180 | 0
7487 | 178.8941 | 0
7488 | 178.8871 | 0
7489 | 178.704 | 0
7490 | 177.796 | 0
7491 | 176.7969 | 0
7492 | 176.3999 | 0
7493 | 175.9232 | 0
7494 | 174.4073 | 0
7495 | 173.99 | 0
7496 | 173.6 | 0
7497 | 173.54 | 0
7498 | 172.671 | 0
7499 | 171.9803 | 0
7500 | 171.8487 | 0
7501 | 171.2 | 0
7502 | 170.769 | 0
7503 | 170.644 | 0
7504 | 170.605 | 0
7505 | 169.6 | 0
7506 | 169.2818 | 0
7507 | 168.6547 | 0
7508 | 168.473 | 0
7509 | 168.345 | 0
7510 | 168.3081 | 0
7511 | 168 | 0
7512 | 167.4831 | 0
7513 | 167.046 | 0
7514 | 164.8 | 0
7515 | 164.7109 | 0
7516 | 163.4921 | 0
7517 | 163.2 | 0
7518 | 163.157 | 0
7519 | 162.5652 | 0
7520 | 160.8 | 0
7521 | 160.732 | 0
7522 | 160.3938 | 0
7523 | 160.064 | 0
7524 | 159.9664 | 0
7525 | 159.6078 | 0
7526 | 159.508 | 0
7527 | 158.4 | 0
7528 | 158.372 | 0
7529 | 157.4013 | 0
7530 | 156.96 | 0
7531 | 156.897 | 0
7532 | 156.1646 | 0
7533 | 155.6841 | 0
7534 | 155.4039 | 0
7535 | 155.4039 | 0
7536 | 154.285 | 0
7537 | 153.6 | 0
7538 | 152.6909 | 0
7539 | 152.29 | 0
7540 | 152.1164 | 0
7541 | 151.282 | 0
7542 | 151.211 | 0
7543 | 150.5308 | 0
7544 | 150.4 | 0
7545 | 149.6 | 0
7546 | 149.362 | 0
7547 | 148.8 | 0
7548 | 148.8 | 0
7549 | 148 | 0
7550 | 147.3263 | 0
7551 | 147.249 | 0
7552 | 147.1628 | 0
7553 | 145.633 | 0
7554 | 145.6072 | 0
7555 | 144.5105 | 0
7556 | 144.11 | 0
7557 | 142.4 | 0
7558 | 142.371 | 0
7559 | 141.4846 | 0
7560 | 141.382 | 0
7561 | 140.8 | 0
7562 | 140 | 0
7563 | 139.948 | 0
7564 | 139.8489 | 0
7565 | 139.2 | 0
7566 | 138.7688 | 0
7567 | 138.494 | 0
7568 | 138.479 | 0
7569 | 138.4 | 0
7570 | 138.295 | 0
7571 | 138.2778 | 0
7572 | 138.2668 | 0
7573 | 137.6387 | 0
7574 | 137.6 | 0
7575 | 137.552 | 0
7576 | 137.5422 | 0
7577 | 136.8 | 0
7578 | 136.8 | 0
7579 | 136.2679 | 0
7580 | 136.0712 | 0
7581 | 135.9137 | 0
7582 | 135.7598 | 0
7583 | 135.505 | 0
7584 | 135.46 | 0
7585 | 135.2 | 0
7586 | 135.1872 | 0
7587 | 134.638 | 0
7588 | 132.8 | 0
7589 | 132.6113 | 0
7590 | 132.4947 | 0
7591 | 132.424 | 0
7592 | 131.3026 | 0
7593 | 130.6101 | 0
7594 | 130.5488 | 0
7595 | 129.9866 | 0
7596 | 129.537 | 0
7597 | 128.8 | 0
7598 | 128.716 | 0
7599 | 127.2 | 0
7600 | 127.2 | 0
7601 | 127.2 | 0
7602 | 126.773 | 0
7603 | 126.647 | 0
7604 | 126.4653 | 0
7605 | 126.4 | 0
7606 | 125.6 | 0
7607 | 124.8 | 0
7608 | 124.5833 | 0
7609 | 124 | 0
7610 | 123.5332 | 0
7611 | 123.2 | 0
7612 | 123.1185 | 0
7613 | 122.7562 | 0
7614 | 122.6745 | 0
7615 | 122.023 | 0
7616 | 121.2024 | 0
7617 | 120.4254 | 0
7618 | 120 | 0
7619 | 120 | 0
7620 | 120 | 0
7621 | 119.9634 | 0
7622 | 119.641 | 0
7623 | 119.5695 | 0
7624 | 119.4032 | 0
7625 | 118.7976 | 0
7626 | 118.4 | 0
7627 | 118.4 | 0
7628 | 118.4 | 0
7629 | 117.6 | 0
7630 | 117.6 | 0
7631 | 117.348 | 0
7632 | 116.9497 | 0
7633 | 116.8 | 0
7634 | 116.5407 | 0
7635 | 116.1318 | 0
7636 | 116 | 0
7637 | 116 | 0
7638 | 116 | 0
7639 | 115.4766 | 0
7640 | 115.2 | 0
7641 | 115.2 | 0
7642 | 115.054 | 0
7643 | 114.9869 | 0
7644 | 114.9869 | 0
7645 | 114.4 | 0
7646 | 114.4 | 0
7647 | 113.6784 | 0
7648 | 113.6 | 0
7649 | 112.8605 | 0
7650 | 112.8605 | 0
7651 | 112.7164 | 0
7652 | 112.656 | 0
7653 | 112.5998 | 0
7654 | 111.8791 | 0
7655 | 111.2 | 0
7656 | 111.2 | 0
7657 | 110.407 | 0
7658 | 110.4 | 0
7659 | 110.4 | 0
7660 | 110.4 | 0
7661 | 110.4 | 0
7662 | 110.4 | 0
7663 | 110.328 | 0
7664 | 110.259 | 0
7665 | 110.145 | 0
7666 | 109.8187 | 0
7667 | 109.6 | 0
7668 | 109.6 | 0
7669 | 109.6 | 0
7670 | 108.8 | 0
7671 | 108.8 | 0
7672 | 108.8 | 0
7673 | 108.8 | 0
7674 | 108.4667 | 0
7675 | 108.3768 | 0
7676 | 108.1214 | 0
7677 | 108 | 0
7678 | 108 | 0
7679 | 108 | 0
7680 | 107.9944 | 0
7681 | 107.2175 | 0
7682 | 107.2175 | 0
7683 | 107.2175 | 0
7684 | 107.2 | 0
7685 | 107.2 | 0
7686 | 107.2 | 0
7687 | 107.1357 | 0
7688 | 106.6504 | 0
7689 | 106.6504 | 0
7690 | 106.4 | 0
7691 | 106.4 | 0
7692 | 106.3653 | 0
7693 | 106.186 | 0
7694 | 106.102 | 0
7695 | 105.9861 | 0
7696 | 105.9149 | 0
7697 | 105.6 | 0
7698 | 105.6 | 0
7699 | 105.6 | 0
7700 | 105.5001 | 0
7701 | 105.3492 | 0
7702 | 105.232 | 0
7703 | 105.1892 | 0
7704 | 105.1892 | 0
7705 | 105.1794 | 0
7706 | 104.8867 | 0
7707 | 104.8867 | 0
7708 | 104.8 | 0
7709 | 104.8 | 0
7710 | 104.8 | 0
7711 | 104.8 | 0
7712 | 104.269 | 0
7713 | 104.1097 | 0
7714 | 104.1097 | 0
7715 | 104 | 0
7716 | 104 | 0
7717 | 103.8644 | 0
7718 | 103.3328 | 0
7719 | 103.2926 | 0
7720 | 103.221 | 0
7721 | 103.2 | 0
7722 | 103.2 | 0
7723 | 103.2 | 0
7724 | 103.2 | 0
7725 | 102.491 | 0
7726 | 102.4 | 0
7727 | 102.4 | 0
7728 | 102.4 | 0
7729 | 102.2287 | 0
7730 | 102.2287 | 0
7731 | 102.2287 | 0
7732 | 102.2212 | 0
7733 | 102.069 | 0
7734 | 101.7789 | 0
7735 | 101.7789 | 0
7736 | 101.7789 | 0
7737 | 101.6 | 0
7738 | 101.6 | 0
7739 | 101.6 | 0
7740 | 101.6 | 0
7741 | 101.6 | 0
7742 | 101.6 | 0
7743 | 101.6 | 0
7744 | 101.6 | 0
7745 | 101.6 | 0
7746 | 101.4733 | 0
7747 | 101.2048 | 0
7748 | 101.182 | 0
7749 | 101.002 | 0
7750 | 100.984 | 0
7751 | 100.8 | 0
7752 | 100.8 | 0
7753 | 100.8 | 0
7754 | 100.7662 | 0
7755 | 100.7662 | 0
7756 | 100.7662 | 0
7757 | 100.5931 | 0
7758 | 100.5931 | 0
7759 | 100.5931 | 0
7760 | 100.5931 | 0
7761 | 100.2454 | 0
7762 | 100.225 | 0
7763 | 100.225 | 0
7764 | 100.0307 | 0
7765 | 100.0307 | 0
7766 | 100.012 | 0
7767 | 100 | 0
7768 | 100 | 0
7769 | 100 | 0
7770 | 100 | 0
7771 | 100 | 0
7772 | 100 | 0
7773 | 100 | 0
7774 | 99.7752 | 0
7775 | 99.5365 | 0
7776 | 99.4481 | 0
7777 | 99.261 | 0
7778 | 99.2 | 0
7779 | 99.2 | 0
7780 | 99.2 | 0
7781 | 99.2 | 0
7782 | 99.2 | 0
7783 | 99.2 | 0
7784 | 99.1266 | 0
7785 | 98.9574 | 0
7786 | 98.9574 | 0
7787 | 98.9574 | 0
7788 | 98.846 | 0
7789 | 98.6711 | 0
7790 | 98.6711 | 0
7791 | 98.6711 | 0
7792 | 98.6711 | 0
7793 | 98.6711 | 0
7794 | 98.5597 | 0
7795 | 98.4 | 0
7796 | 98.4 | 0
7797 | 98.4 | 0
7798 | 98.4 | 0
7799 | 98.4 | 0
7800 | 98.4 | 0
7801 | 98.4 | 0
7802 | 98.4 | 0
7803 | 98.247 | 0
7804 | 97.636 | 0
7805 | 97.6 | 0
7806 | 97.6 | 0
7807 | 97.3218 | 0
7808 | 97.2562 | 0
7809 | 97.2204 | 0
7810 | 97.1173 | 0
7811 | 96.821 | 0
7812 | 96.805 | 0
7813 | 96.8 | 0
7814 | 96.8 | 0
7815 | 96.8 | 0
7816 | 96.8 | 0
7817 | 96.8 | 0
7818 | 96.8 | 0
7819 | 96.8 | 0
7820 | 96.8 | 0
7821 | 96.5407 | 0
7822 | 96.5039 | 0
7823 | 96.4444 | 0
7824 | 96.4285 | 0
7825 | 96.4235 | 0
7826 | 96.3403 | 0
7827 | 96.007 | 0
7828 | 96 | 0
7829 | 96 | 0
7830 | 96 | 0
7831 | 96 | 0
7832 | 96 | 0
7833 | 95.6861 | 0
7834 | 95.6336 | 0
7835 | 95.6266 | 0
7836 | 95.6176 | 0
7837 | 95.4148 | 0
7838 | 95.362 | 0
7839 | 95.215 | 0
7840 | 95.2 | 0
7841 | 95.2 | 0
7842 | 95.2 | 0
7843 | 95.2 | 0
7844 | 95.06 | 0
7845 | 94.9911 | 0
7846 | 94.896 | 0
7847 | 94.8821 | 0
7848 | 94.8683 | 0
7849 | 94.8683 | 0
7850 | 94.8683 | 0
7851 | 94.8446 | 0
7852 | 94.8297 | 0
7853 | 94.8297 | 0
7854 | 94.791 | 0
7855 | 94.436 | 0
7856 | 94.4 | 0
7857 | 94.4 | 0
7858 | 94.4 | 0
7859 | 94.4 | 0
7860 | 94.4 | 0
7861 | 94.4 | 0
7862 | 94.4 | 0
7863 | 94.4 | 0
7864 | 94.4 | 0
7865 | 94.1466 | 0
7866 | 94.1466 | 0
7867 | 94.05 | 0
7868 | 94.0328 | 0
7869 | 94.0328 | 0
7870 | 94.0328 | 0
7871 | 94.0328 | 0
7872 | 94.0328 | 0
7873 | 94.0095 | 0
7874 | 93.6 | 0
7875 | 93.6 | 0
7876 | 93.6 | 0
7877 | 93.6 | 0
7878 | 93.6 | 0
7879 | 93.6 | 0
7880 | 93.6 | 0
7881 | 93.6 | 0
7882 | 93.6 | 0
7883 | 93.6 | 0
7884 | 93.6 | 0
7885 | 93.6 | 0
7886 | 93.6 | 0
7887 | 93.6 | 0
7888 | 93.6 | 0
7889 | 93.6 | 0
7890 | 93.6 | 0
7891 | 93.411 | 0
7892 | 93.411 | 0
7893 | 93.277 | 0
7894 | 93.2359 | 0
7895 | 93.2359 | 0
7896 | 93.2359 | 0
7897 | 93.2359 | 0
7898 | 93.2359 | 0
7899 | 93.2359 | 0
7900 | 93.2359 | 0
7901 | 93.2359 | 0
7902 | 93.2359 | 0
7903 | 93.2359 | 0
7904 | 93.2326 | 0
7905 | 93.2326 | 0
7906 | 93.2326 | 0
7907 | 92.8447 | 0
7908 | 92.8 | 0
7909 | 92.8 | 0
7910 | 92.8 | 0
7911 | 92.8 | 0
7912 | 92.8 | 0
7913 | 92.8 | 0
7914 | 92.8 | 0
7915 | 92.8 | 0
7916 | 92.8 | 0
7917 | 92.8 | 0
7918 | 92.8 | 0
7919 | 92.8 | 0
7920 | 92.708 | 0
7921 | 92.6755 | 0
7922 | 92.6755 | 0
7923 | 92.439 | 0
7924 | 92.439 | 0
7925 | 92.439 | 0
7926 | 92.439 | 0
7927 | 92.439 | 0
7928 | 92.439 | 0
7929 | 92.4148 | 0
7930 | 92.4148 | 0
7931 | 92.1604 | 0
7932 | 92.13 | 0
7933 | 92 | 0
7934 | 92 | 0
7935 | 92 | 0
7936 | 92 | 0
7937 | 92 | 0
7938 | 91.951 | 0
7939 | 91.94 | 0
7940 | 91.94 | 0
7941 | 91.689 | 0
7942 | 91.6762 | 0
7943 | 91.6421 | 0
7944 | 91.6421 | 0
7945 | 91.5969 | 0
7946 | 91.5969 | 0
7947 | 91.2045 | 0
7948 | 91.2045 | 0
7949 | 91.2 | 0
7950 | 91.2 | 0
7951 | 91.2 | 0
7952 | 91.2 | 0
7953 | 91.2 | 0
7954 | 91.2 | 0
7955 | 91.2 | 0
7956 | 91.2 | 0
7957 | 91.2 | 0
7958 | 91.2 | 0
7959 | 91.2 | 0
7960 | 91.2 | 0
7961 | 91.2 | 0
7962 | 91.2 | 0
7963 | 91.2 | 0
7964 | 91.2 | 0
7965 | 91.1703 | 0
7966 | 90.8526 | 0
7967 | 90.8453 | 0
7968 | 90.8453 | 0
7969 | 90.8453 | 0
7970 | 90.8453 | 0
7971 | 90.8453 | 0
7972 | 90.8453 | 0
7973 | 90.638 | 0
7974 | 90.469 | 0
7975 | 90.469 | 0
7976 | 90.455 | 0
7977 | 90.4 | 0
7978 | 90.4 | 0
7979 | 90.4 | 0
7980 | 90.4 | 0
7981 | 90.4 | 0
7982 | 90.093 | 0
7983 | 90.0484 | 0
7984 | 90.0484 | 0
7985 | 90.0355 | 0
7986 | 90.0212 | 0
7987 | 89.7711 | 0
7988 | 89.7426 | 0
7989 | 89.69 | 0
7990 | 89.626 | 0
7991 | 89.61 | 0
7992 | 89.6 | 0
7993 | 89.6 | 0
7994 | 89.6 | 0
7995 | 89.6 | 0
7996 | 89.6 | 0
7997 | 89.6 | 0
7998 | 89.6 | 0
7999 | 89.6 | 0
8000 | 89.6 | 0
8001 | 89.6 | 0
8002 | 89.6 | 0
8003 | 89.489 | 0
8004 | 89.4741 | 0
8005 | 89.332 | 0
8006 | 89.2515 | 0
8007 | 89.172 | 0
8008 | 89.1435 | 0
8009 | 89.1435 | 0
8010 | 89.121 | 0
8011 | 88.9979 | 0
8012 | 88.9979 | 0
8013 | 88.9845 | 0
8014 | 88.8 | 0
8015 | 88.8 | 0
8016 | 88.8 | 0
8017 | 88.8 | 0
8018 | 88.8 | 0
8019 | 88.8 | 0
8020 | 88.6732 | 0
8021 | 88.652 | 0
8022 | 88.61 | 0
8023 | 88.4546 | 0
8024 | 88.4546 | 0
8025 | 88.4546 | 0
8026 | 88.4546 | 0
8027 | 88.4546 | 0
8028 | 88.3635 | 0
8029 | 88.3256 | 0
8030 | 88.3256 | 0
8031 | 88.3256 | 0
8032 | 88.3256 | 0
8033 | 88.3072 | 0
8034 | 88.307 | 0
8035 | 88.2653 | 0
8036 | 88.264 | 0
8037 | 88.2624 | 0
8038 | 88.2624 | 0
8039 | 88.262 | 0
8040 | 88.18 | 0
8041 | 88.082 | 0
8042 | 88.0252 | 0
8043 | 88 | 0
8044 | 88 | 0
8045 | 88 | 0
8046 | 88 | 0
8047 | 88 | 0
8048 | 88 | 0
8049 | 88 | 0
8050 | 88 | 0
8051 | 87.9635 | 0
8052 | 87.886 | 0
8053 | 87.8474 | 0
8054 | 87.814 | 0
8055 | 87.738 | 0
8056 | 87.682 | 0
8057 | 87.6577 | 0
8058 | 87.6577 | 0
8059 | 87.6577 | 0
8060 | 87.6577 | 0
8061 | 87.6577 | 0
8062 | 87.6577 | 0
8063 | 87.6577 | 0
8064 | 87.642 | 0
8065 | 87.5078 | 0
8066 | 87.356 | 0
8067 | 87.3011 | 0
8068 | 87.2 | 0
8069 | 87.2 | 0
8070 | 87.2 | 0
8071 | 87.2 | 0
8072 | 87.2 | 0
8073 | 87.2 | 0
8074 | 87.2 | 0
8075 | 87.2 | 0
8076 | 87.2 | 0
8077 | 87.2 | 0
8078 | 87.2 | 0
8079 | 87.2 | 0
8080 | 87.2 | 0
8081 | 87.2 | 0
8082 | 87.2 | 0
8083 | 87.2 | 0
8084 | 87.089 | 0
8085 | 87.0262 | 0
8086 | 86.9093 | 0
8087 | 86.8608 | 0
8088 | 86.8608 | 0
8089 | 86.8608 | 0
8090 | 86.8608 | 0
8091 | 86.8608 | 0
8092 | 86.8608 | 0
8093 | 86.8608 | 0
8094 | 86.8608 | 0
8095 | 86.8608 | 0
8096 | 86.8608 | 0
8097 | 86.8608 | 0
8098 | 86.8608 | 0
8099 | 86.801 | 0
8100 | 86.7914 | 0
8101 | 86.787 | 0
8102 | 86.785 | 0
8103 | 86.7502 | 0
8104 | 86.74 | 0
8105 | 86.69 | 0
8106 | 86.69 | 0
8107 | 86.655 | 0
8108 | 86.617 | 0
8109 | 86.5519 | 0
8110 | 86.4494 | 0
8111 | 86.437 | 0
8112 | 86.4 | 0
8113 | 86.4 | 0
8114 | 86.4 | 0
8115 | 86.4 | 0
8116 | 86.4 | 0
8117 | 86.4 | 0
8118 | 86.4 | 0
8119 | 86.4 | 0
8120 | 86.4 | 0
8121 | 86.4 | 0
8122 | 86.4 | 0
8123 | 86.3179 | 0
8124 | 86.2801 | 0
8125 | 86.0639 | 0
8126 | 86.0639 | 0
8127 | 86.0639 | 0
8128 | 86.0639 | 0
8129 | 86.0639 | 0
8130 | 86.0558 | 0
8131 | 86.0558 | 0
8132 | 86.0558 | 0
8133 | 86.02 | 0
8134 | 85.97 | 0
8135 | 85.8721 | 0
8136 | 85.749 | 0
8137 | 85.7196 | 0
8138 | 85.6854 | 0
8139 | 85.6448 | 0
8140 | 85.6448 | 0
8141 | 85.638 | 0
8142 | 85.6 | 0
8143 | 85.6 | 0
8144 | 85.6 | 0
8145 | 85.6 | 0
8146 | 85.6 | 0
8147 | 85.6 | 0
8148 | 85.6 | 0
8149 | 85.6 | 0
8150 | 85.5428 | 0
8151 | 85.467 | 0
8152 | 85.3392 | 0
8153 | 85.3203 | 0
8154 | 85.3203 | 0
8155 | 85.2782 | 0
8156 | 85.267 | 0
8157 | 85.267 | 0
8158 | 85.1346 | 0
8159 | 84.9541 | 0
8160 | 84.8 | 0
8161 | 84.8 | 0
8162 | 84.8 | 0
8163 | 84.8 | 0
8164 | 84.8 | 0
8165 | 84.741 | 0
8166 | 84.5848 | 0
8167 | 84.557 | 0
8168 | 84.507 | 0
8169 | 84.4702 | 0
8170 | 84.4702 | 0
8171 | 84.4702 | 0
8172 | 84.462 | 0
8173 | 84.446 | 0
8174 | 84.4114 | 0
8175 | 84.323 | 0
8176 | 84.2988 | 0
8177 | 84.2832 | 0
8178 | 84.2281 | 0
8179 | 84.1783 | 0
8180 | 84.042 | 0
8181 | 84 | 0
8182 | 84 | 0
8183 | 84 | 0
8184 | 83.995 | 0
8185 | 83.8493 | 0
8186 | 83.8493 | 0
8187 | 83.7151 | 0
8188 | 83.6733 | 0
8189 | 83.5728 | 0
8190 | 83.419 | 0
8191 | 83.4186 | 0
8192 | 83.4186 | 0
8193 | 83.4186 | 0
8194 | 83.396 | 0
8195 | 83.254 | 0
8196 | 83.2 | 0
8197 | 83.2 | 0
8198 | 83.0716 | 0
8199 | 82.933 | 0
8200 | 82.9302 | 0
8201 | 82.892 | 0
8202 | 82.8821 | 0
8203 | 82.8764 | 0
8204 | 82.775 | 0
8205 | 82.665 | 0
8206 | 82.654 | 0
8207 | 82.638 | 0
8208 | 82.6104 | 0
8209 | 82.6008 | 0
8210 | 82.453 | 0
8211 | 82.403 | 0
8212 | 82.4 | 0
8213 | 82.3874 | 0
8214 | 82.3782 | 0
8215 | 82.3782 | 0
8216 | 82.3782 | 0
8217 | 82.3782 | 0
8218 | 82.3435 | 0
8219 | 82.3325 | 0
8220 | 82.3166 | 0
8221 | 82.1914 | 0
8222 | 82.0825 | 0
8223 | 82.0795 | 0
8224 | 82.0705 | 0
8225 | 82.0117 | 0
8226 | 81.8383 | 0
8227 | 81.795 | 0
8228 | 81.783 | 0
8229 | 81.6427 | 0
8230 | 81.6 | 0
8231 | 81.6 | 0
8232 | 81.6 | 0
8233 | 81.6 | 0
8234 | 81.6 | 0
8235 | 81.6 | 0
8236 | 81.515 | 0
8237 | 81.5007 | 0
8238 | 81.5007 | 0
8239 | 81.435 | 0
8240 | 81.362 | 0
8241 | 81.2826 | 0
8242 | 81.253 | 0
8243 | 81.1985 | 0
8244 | 81.1979 | 0
8245 | 81.184 | 0
8246 | 81.1182 | 0
8247 | 81.102 | 0
8248 | 81.0455 | 0
8249 | 80.9652 | 0
8250 | 80.9652 | 0
8251 | 80.9369 | 0
8252 | 80.8682 | 0
8253 | 80.819 | 0
8254 | 80.81 | 0
8255 | 80.81 | 0
8256 | 80.81 | 0
8257 | 80.8 | 0
8258 | 80.7865 | 0
8259 | 80.774 | 0
8260 | 80.761 | 0
8261 | 80.6148 | 0
8262 | 80.579 | 0
8263 | 80.506 | 0
8264 | 80.485 | 0
8265 | 80.475 | 0
8266 | 80.4598 | 0
8267 | 80.4469 | 0
8268 | 80.2656 | 0
8269 | 80.1929 | 0
8270 | 80.162 | 0
8271 | 80.1193 | 0
8272 | 80.078 | 0
8273 | 80 | 0
8274 | 80 | 0
8275 | 80 | 0
8276 | 80 | 0
8277 | 79.923 | 0
8278 | 79.796 | 0
8279 | 79.7665 | 0
8280 | 79.6888 | 0
8281 | 79.6888 | 0
8282 | 79.6888 | 0
8283 | 79.66 | 0
8284 | 79.653 | 0
8285 | 79.4856 | 0
8286 | 79.4371 | 0
8287 | 79.4286 | 0
8288 | 79.4286 | 0
8289 | 79.3551 | 0
8290 | 79.3501 | 0
8291 | 79.3432 | 0
8292 | 79.281 | 0
8293 | 79.24 | 0
8294 | 79.2 | 0
8295 | 79.2 | 0
8296 | 79.067 | 0
8297 | 79.057 | 0
8298 | 78.9726 | 0
8299 | 78.9318 | 0
8300 | 78.901 | 0
8301 | 78.853 | 0
8302 | 78.8376 | 0
8303 | 78.7595 | 0
8304 | 78.738 | 0
8305 | 78.738 | 0
8306 | 78.738 | 0
8307 | 78.738 | 0
8308 | 78.7006 | 0
8309 | 78.5941 | 0
8310 | 78.5463 | 0
8311 | 78.5117 | 0
8312 | 78.42 | 0
8313 | 78.4 | 0
8314 | 78.4 | 0
8315 | 78.3215 | 0
8316 | 78.115 | 0
8317 | 78.0473 | 0
8318 | 77.6938 | 0
8319 | 77.625 | 0
8320 | 77.6 | 0
8321 | 77.379 | 0
8322 | 77.3566 | 0
8323 | 77.3566 | 0
8324 | 77.3566 | 0
8325 | 77.076 | 0
8326 | 76.9871 | 0
8327 | 76.876 | 0
8328 | 76.8 | 0
8329 | 76.8 | 0
8330 | 76.8 | 0
8331 | 76.8 | 0
8332 | 76.7762 | 0
8333 | 76.614 | 0
8334 | 76.5013 | 0
8335 | 76.2014 | 0
8336 | 76.02 | 0
8337 | 76 | 0
8338 | 76 | 0
8339 | 75.9752 | 0
8340 | 75.749 | 0
8341 | 75.7243 | 0
8342 | 75.611 | 0
8343 | 75.453 | 0
8344 | 75.3169 | 0
8345 | 75.2845 | 0
8346 | 75.2 | 0
8347 | 75.163 | 0
8348 | 75.1595 | 0
8349 | 74.961 | 0
8350 | 74.903 | 0
8351 | 74.8706 | 0
8352 | 74.6694 | 0
8353 | 74.649 | 0
8354 | 74.6116 | 0
8355 | 74.5939 | 0
8356 | 74.5939 | 0
8357 | 74.479 | 0
8358 | 74.454 | 0
8359 | 74.3586 | 0
8360 | 74.1644 | 0
8361 | 73.9979 | 0
8362 | 73.9032 | 0
8363 | 73.28 | 0
8364 | 73.0629 | 0
8365 | 73.0251 | 0
8366 | 72.995 | 0
8367 | 72.9207 | 0
8368 | 72.8 | 0
8369 | 72.8 | 0
8370 | 72.8 | 0
8371 | 72.771 | 0
8372 | 72.4879 | 0
8373 | 72 | 0
8374 | 71.8311 | 0
8375 | 71.5652 | 0
8376 | 71.47 | 0
8377 | 71.433 | 0
8378 | 70.538 | 0
8379 | 70.4498 | 0
8380 | 70.3334 | 0
8381 | 69.874 | 0
8382 | 69.845 | 0
8383 | 69.75 | 0
8384 | 69.556 | 0
8385 | 69.059 | 0
8386 | 68.887 | 0
8387 | 68.8 | 0
8388 | 68.6977 | 0
8389 | 68.404 | 0
8390 | 67.2 | 0
8391 | 66.9963 | 0
8392 | 66.9323 | 0
8393 | 66.865 | 0
8394 | 66.3057 | 0
8395 | 66.072 | 0
8396 | 65.492 | 0
8397 | 65.31 | 0
8398 | 64.271 | 0
8399 | 64.133 | 0
8400 | 63.569 | 0
8401 | 62.387 | 0
8402 | 62.252 | 0
8403 | 60.615 | 0
8404 | 60.338 | 0
8405 | 60.106 | 0
8406 | 59.935 | 0
8407 | 59.771 | 0
8408 | 59.139 | 0
8409 | 57.64 | 0
8410 | 57.444 | 0
8411 | 56.963 | 0
8412 | 44.716 | 0
8413 | 39.491 | 0
8414 | 37.99 | 0
8415 | 0 | 0
8416 | 0 | 0
8417 | 0 | 0
8418 | 0 | 0
8419 | 0 | 0
8420 | 0 | 0
8421 | 0 | 0
8422 | 0 | 0
8423 | 0 | 0
8424 | 0 | 0
8425 | 0 | 0
8426 | 0 | 0
8427 | 0 | 0
8428 | 0 | 0
8429 | 0 | 0
8430 | 0 | 0
8431 | 0 | 0
8432 | 0 | 0
8433 | 0 | 0
8434 | 0 | 0
8435 | 0 | 0
8436 | 0 | 0
8437 | 0 | 0
8438 | 0 | 0
8439 | 0 | 0
8440 | 0 | 0
8441 | 0 | 0
8442 | 0 | 0
8443 | 0 | 0
8444 | 0 | 0
8445 | 0 | 0
8446 | 0 | 0
8447 | 0 | 0
8448 | 0 | 0
8449 | 0 | 0
8450 | 0 | 0
8451 | 0 | 0
8452 | 0 | 0
8453 | 0 | 0
8454 | 0 | 0
8455 | 0 | 0
8456 | 0 | 0
8457 | 0 | 0
8458 | 0 | 0
8459 | 0 | 0
8460 | 0 | 0
8461 | 0 | 0
8462 | 0 | 0
8463 | 0 | 0
8464 | 0 | 0
8465 | 0 | 0
8466 | 0 | 0
8467 | 0 | 0
8468 | 0 | 0
8469 | 0 | 0
8470 | 0 | 0
8471 | 0 | 0
8472 | 0 | 0
8473 | 0 | 0
8474 | 0 | 0
8475 | 0 | 0
8476 | 0 | 0
8477 | 0 | 0
8478 | 0 | 0
8479 | 0 | 0
8480 | 0 | 0
8481 | 0 | 0
8482 | 0 | 0
8483 | 0 | 0
8484 | 0 | 0
8485 | 0 | 0
8486 | 0 | 0
8487 | 0 | 0
8488 | 0 | 0
8489 | 0 | 0
8490 | 0 | 0
8491 | 0 | 0
8492 | 0 | 0
8493 | 0 | 0
8494 | 0 | 0
8495 | 0 | 0
8496 | 0 | 0
8497 | 0 | 0
8498 | 0 | 0
8499 | 0 | 0
8500 | 0 | 0
8501 | 0 | 0
8502 | 0 | 0
8503 | 0 | 0
8504 | 0 | 0
8505 | 0 | 0
8506 | 0 | 0
8507 | 0 | 0
8508 | 0 | 0
8509 | 0 | 0
8510 | 0 | 0
8511 | 0 | 0
8512 | 0 | 0
8513 | 0 | 0
8514 | 0 | 0
8515 | 0 | 0
8516 | 0 | 0
8517 | 0 | 0
8518 | 0 | 0
8519 | 0 | 0
8520 | 0 | 0
8521 | 0 | 0
8522 | 0 | 0
8523 | 0 | 0
8524 | 0 | 0
8525 | 0 | 0
8526 | 0 | 0
8527 | 0 | 0
8528 | 0 | 0
8529 | 0 | 0
8530 | 0 | 0
8531 | 0 | 0
8532 | 0 | 0
8533 | 0 | 0
8534 | 0 | 0
8535 | 0 | 0
8536 | 0 | 0
8537 | 0 | 0
8538 | 0 | 0
8539 | 0 | 0
8540 | 0 | 0
8541 | 0 | 0
8542 | 0 | 0
8543 | 0 | 0
8544 | 0 | 0
8545 | 0 | 0
8546 | 0 | 0
8547 | 0 | 0
8548 | 0 | 0
8549 | 0 | 0
8550 | 0 | 0
8551 | 0 | 0
8552 | 0 | 0
8553 | 0 | 0
8554 | 0 | 0
8555 | 0 | 0
8556 | 0 | 0
8557 | 0 | 0
8558 | 0 | 0
8559 | 0 | 0
8560 | 0 | 0
8561 | 0 | 0
8562 | 0 | 0
8563 | 0 | 0
8564 | 0 | 0
8565 | 0 | 0
8566 | 0 | 0
8567 | 0 | 0
8568 | 0 | 0
8569 | 0 | 0
8570 | 0 | 0
8571 | 0 | 0
8572 | 0 | 0
8573 | 0 | 0
8574 | 0 | 0
8575 | 0 | 0
8576 | 0 | 0
8577 | 0 | 0
8578 | 0 | 0
8579 | 0 | 0
8580 | 0 | 0
8581 | 0 | 0
8582 | 0 | 0
8583 | 0 | 0
8584 | 0 | 0
8585 | 0 | 0
8586 | 0 | 0
8587 | 0 | 0
8588 | 0 | 0
8589 | 0 | 0
8590 | 0 | 0
8591 | 0 | 0
8592 | 0 | 0
8593 | 0 | 0
8594 | 0 | 0
8595 | 0 | 0
8596 | 0 | 0
8597 | 0 | 0
8598 | 0 | 0
8599 | 0 | 0
8600 | 0 | 0
8601 | 0 | 0
8602 | 0 | 0
8603 | 0 | 0
8604 | 0 | 0
8605 | 0 | 0
8606 | 0 | 0
8607 | 0 | 0
8608 | 0 | 0
8609 | 0 | 0
8610 | 0 | 0
8611 | 0 | 0
8612 | 0 | 0
8613 | 0 | 0
8614 | 0 | 0
8615 | 0 | 0
8616 | 0 | 0
8617 | 0 | 0
8618 | 0 | 0
8619 | 0 | 0
8620 | 0 | 0
8621 | 0 | 0
8622 | 0 | 0
8623 | 0 | 0
8624 | 0 | 0
8625 | 0 | 0
8626 | 0 | 0
8627 | 0 | 0
8628 | 0 | 0
8629 | 0 | 0
8630 | 0 | 0
8631 | 0 | 0
8632 | 0 | 0
8633 | 0 | 0
8634 | 0 | 0
8635 | 0 | 0
8636 | 0 | 0
8637 | 0 | 0
8638 | 0 | 0
8639 | 0 | 0
8640 | 0 | 0
8641 | 0 | 0
8642 | 0 | 0
8643 | 0 | 0
8644 | 0 | 0
8645 | 0 | 0
8646 | 0 | 0
8647 | 0 | 0
8648 | 0 | 0
8649 | 0 | 0
8650 | 0 | 0
8651 | 0 | 0
8652 | 0 | 0
8653 | 0 | 0
8654 | 0 | 0
8655 | 0 | 0
8656 | 0 | 0
8657 | 0 | 0
8658 | 0 | 0
8659 | 0 | 0
8660 | 0 | 0
8661 | 0 | 0
8662 | 0 | 0
8663 | 0 | 0
8664 | 0 | 0
8665 | 0 | 0
8666 | 0 | 0
8667 | 0 | 0
8668 | 0 | 0
8669 | 0 | 0
8670 | 0 | 0
8671 | 0 | 0
8672 | 0 | 0
8673 | 0 | 0
8674 | 0 | 0
8675 | 0 | 0
8676 | 0 | 0
8677 | 0 | 0
8678 | 0 | 0
8679 | 0 | 0
8680 | 0 | 0
8681 | 0 | 0
8682 | 0 | 0
8683 | 0 | 0
8684 | 0 | 0
8685 | 0 | 0
8686 | 0 | 0
8687 | 0 | 0
8688 | 0 | 0
8689 | 0 | 0
8690 | 0 | 0
8691 | 0 | 0
8692 | 0 | 0
8693 | 0 | 0
8694 | 0 | 0
8695 | 0 | 0
8696 | 0 | 0
8697 | 0 | 0
8698 | 0 | 0
8699 | 0 | 0
8700 | 0 | 0
8701 | 0 | 0
8702 | 0 | 0
8703 | 0 | 0
8704 | 0 | 0
8705 | 0 | 0
8706 | 0 | 0
8707 | 0 | 0
8708 | 0 | 0
8709 | 0 | 0
8710 | 0 | 0
8711 | 0 | 0
8712 | 0 | 0
8713 | 0 | 0
8714 | 0 | 0
8715 | 0 | 0
8716 | 0 | 0
8717 | 0 | 0
8718 | 0 | 0
8719 | 0 | 0
8720 | 0 | 0
8721 | 0 | 0
8722 | 0 | 0
8723 | 0 | 0
8724 | 0 | 0
8725 | 0 | 0
8726 | 0 | 0
8727 | 0 | 0
8728 | 0 | 0
8729 | 0 | 0
8730 | 0 | 0
8731 | 0 | 0
8732 | 0 | 0
8733 | 0 | 0
8734 | 0 | 0
8735 | 0 | 0
8736 | 0 | 0
8737 | 0 | 0
8738 | 0 | 0
8739 | 0 | 0
8740 | 0 | 0
8741 | 0 | 0
8742 | 0 | 0
8743 | 0 | 0
8744 | 0 | 0
8745 | 0 | 0
8746 | 0 | 0
8747 | 0 | 0
8748 | 0 | 0
8749 | 0 | 0
8750 | 0 | 0
8751 | 0 | 0
8752 | 0 | 0
8753 | 0 | 0
8754 | 0 | 0
8755 | 0 | 0
8756 | 0 | 0
8757 | 0 | 0
8758 | 0 | 0
8759 | 0 | 0
8760 | 0 | 0

## Year 1 BAU vs DPPA
Line Item | Year 1 (USD) | Side
Buyer (Factory) - Year 1 Outflow (USD)
BAU EVN energy + demand bill | 731030.93 | bau
C_DN spot energy (Q_Khc × CFMP × K_pp) | 223915.6322 | dppa
C_DPPA system service fee | 57602.8037 | dppa
C_CL settlement adder | 26129.2718 | dppa
C_BL retail shortfall (P_evn × shortfall) | 421520.9906 | dppa
CfD payment to ESCO (positive = pay) | 107535.7085 | dppa
Optimized demand charge (kept by EVN) | 0 | dppa
ESCO demand savings share charged back | 0 | dppa
Total buyer outflow | 836704.4068 | both
Buyer savings vs BAU | -105673.4768 | delta
Buyer savings as % of BAU | -0.14455 | delta_fraction
Seller (ESCO / Generator) - Year 1 Revenue (USD)
Discount-to-EVN energy revenue (Phase 2) | 0 | bau_esco
FMP market revenue (Q_re_meter × FMP) | 407238.2826 | dppa
CfD net (from buyer) | 107535.7085 | dppa
Demand savings share (80%) | 0 | both_esco
ESCO grid arbitrage revenue | 0 | both_esco
Total ESCO / generator revenue | 514773.9911 | both_esco
System Energy Flows (kWh / yr)
PV → load | 4012585.6539 | flow
PV → storage | 390846.4887 | flow
PV → grid (export at FMP) | 3923731.7224 | flow
Storage → load | 351548.9195 | flow
Q_re_meter (total generator injection) | 8287866.2958 | flow
Q_adj (loss-adjusted customer-side) | 8067910.8425 | flow
Q_Khc (matched consumption, settled) | 4211427.0929 | flow
EVN retail shortfall | 5128664.5332 | flow

## Monthly Settlement
Month | C_DN (VND) | C_DPPA (VND) | C_CL (VND) | C_BL (VND) | CfD Net (VND) | Generator Revenue (VND) | Customer Total (VND)
1 | 539003373.1416 | 129702843.9432 | 58834651.1553 | 972416667.5404 | 208753008.6727 | 1243297467.6967 | 1908710544.4531
2 | 463897184.4425 | 116881560.2102 | 53018774.3953 | 803430154.9792 | 212434846.2049 | 1206792150.6319 | 1649662520.2322
3 | 685923968.3131 | 144916570.2426 | 65735766.4462 | 934454694.3472 | 155491804.6641 | 1522181397.9246 | 1986522804.0133
4 | 654575809.3819 | 132537648.1716 | 60120549.8512 | 835380737.8426 | 114996551.5904 | 1390807033.1552 | 1797611296.8376
5 | 601829853.6549 | 140952831.6777 | 63937770.5916 | 792958720.7655 | 210977695.2432 | 1195480609.1858 | 1810656871.9328
6 | 295262658.4385 | 119457557.0074 | 54187275.1648 | 877041158.0162 | 382038458.3152 | 860827736.1901 | 1727987106.9421
7 | 333273651.3906 | 114969175.5014 | 52151295.4427 | 843792203.7821 | 322612068.2018 | 934793664.2948 | 1666798394.3186
8 | 458511465.5516 | 122260540.2281 | 55458739.4979 | 960884484.7009 | 246066221.8434 | 1145556320.9685 | 1843181451.8219
9 | 277468296.761 | 120063801.1606 | 54462274.2487 | 990819466.4572 | 403915609.862 | 869350833.9439 | 1846729448.4895
10 | 462008398.2137 | 118573690.7027 | 53786343.5882 | 1080817174.8902 | 220161648.211 | 958919070.7311 | 1935347255.6059
11 | 546606533.9725 | 128570124.3196 | 58320836.9483 | 1001006853.0541 | 194072703.8107 | 1082700037.8966 | 1928577052.1051
12 | 575129187.6137 | 127227410.286 | 57711766.9436 | 986766768.6386 | 156668517.185 | 1136050679.9711 | 1903503650.667

## Hourly Settlement
Hour | Load (kW) | Q_re_meter (kW) | Q_re_delivered (kW) | Q_adj (kW) | Q_Khc (kW) | FMP (VND/kWh) | C_DN (VND) | C_DPPA (VND) | C_CL (VND) | C_BL (VND) | CfD Payment (VND)
1 | 1020 | 0 | 0 | 0 | 0 | 1377.55 | 0 | 0 | 0 | 1213800 | 0
2 | 1078.4 | 0 | 0 | 0 | 0 | 1316 | 0 | 0 | 0 | 1283296 | 0
3 | 906.4 | 0 | 0 | 0 | 0 | 1367.3 | 0 | 0 | 0 | 1078616 | 0
4 | 860.8 | 0 | 0 | 0 | 0 | 1420.5 | 0 | 0 | 0 | 1024352 | 0
5 | 996.8 | 0 | 0 | 0 | 0 | 1423.7 | 0 | 0 | 0 | 1186192 | 0
6 | 983.2 | 0 | 0 | 0 | 0 | 1433.15 | 0 | 0 | 0 | 1170008 | 0
7 | 586.4 | 367.1146 | 367.1146 | 357.3716 | 357.3716 | 1460.05 | 553422.2614 | 128653.7812 | 58358.7847 | 419809.0306 | 190727.0785
8 | 104.269 | 108.3151 | 108.3151 | 105.4405 | 104.269 | 1481.35 | 163091.2283 | 37536.84 | 17027.1277 | 0 | 54079.1168
9 | 89.172 | 646.3672 | 92.6323 | 629.2129 | 89.172 | 1273.8 | 119873.5393 | 32101.92 | 14561.7876 | 0 | 64756.7064
10 | 105.232 | 2330.1637 | 109.3155 | 2268.3224 | 105.232 | 1251.7 | 139185.264 | 37883.52 | 17184.3856 | 0 | 78745.1056
11 | 89.626 | 2600.202 | 93.1039 | 2531.1941 | 89.626 | 1237.2 | 117193.7334 | 32265.36 | 14635.9258 | 0 | 68366.7128
12 | 119.641 | 2146.9715 | 124.2836 | 2089.9921 | 119.641 | 1241.95 | 156736.6262 | 43070.76 | 19537.3753 | 0 | 90693.86
13 | 82.892 | 1602.3272 | 86.1086 | 1559.8023 | 82.892 | 1235.6 | 107972.0863 | 29841.12 | 13536.2636 | 0 | 63362.6448
14 | 87.738 | 1490.4999 | 91.1427 | 1450.9429 | 87.738 | 1264.65 | 117158.1343 | 31585.68 | 14327.6154 | 0 | 64518.1383
15 | 106.186 | 1025.5589 | 110.3065 | 998.3412 | 106.186 | 1276.05 | 143198.56 | 38226.96 | 17340.1738 | 0 | 76873.3547
16 | 98.846 | 913.1634 | 102.6817 | 888.9285 | 98.846 | 1305.2 | 135970.4615 | 35584.56 | 16141.5518 | 0 | 68678.2008
17 | 88.262 | 529.8237 | 91.687 | 515.7624 | 88.262 | 1500 | 139423.6023 | 31774.32 | 14413.1846 | 0 | 44131
18 | 94.791 | 98.4693 | 98.4693 | 95.856 | 94.791 | 1650.7 | 164927.7534 | 34124.76 | 15479.3703 | 0 | 33110.4963
19 | 90.4 | 93.9079 | 93.9079 | 91.4157 | 90.4 | 1716.9 | 163464.585 | 32544 | 14762.32 | 0 | 25592.24
20 | 96 | 99.7253 | 99.7253 | 97.0786 | 96 | 1581.7 | 160185.6352 | 34560 | 15676.8 | 0 | 40156.8
21 | 87.2 | 90.5838 | 90.5838 | 88.1797 | 87.2 | 1571.05 | 144321.5493 | 31392 | 14239.76 | 0 | 37404.44
22 | 92 | 95.57 | 95.57 | 93.0337 | 92 | 1815.6 | 176161.9858 | 33120 | 15023.6 | 0 | 16964.8
23 | 88 | 91.4148 | 91.4148 | 88.9887 | 88 | 1675.85 | 156161.3606 | 31680 | 14370.4 | 0 | 28525.2
24 | 91.2 | 94.739 | 94.739 | 92.2247 | 91.2 | 1500.35 | 145078.2253 | 32832 | 14892.96 | 0 | 45568.08
25 | 86.4 | 0 | 0 | 0 | 0 | 1506.4 | 0 | 0 | 0 | 102816 | 0
26 | 93.6 | 0 | 0 | 0 | 0 | 1423.5 | 0 | 0 | 0 | 111384 | 0
27 | 86.4 | 0 | 0 | 0 | 0 | 1421.05 | 0 | 0 | 0 | 102816 | 0
28 | 89.6 | 43.5477 | 43.5477 | 42.392 | 42.392 | 1424.3 | 64845.9087 | 15261.1203 | 6922.6137 | 56177.5191 | 23925.5163
29 | 83.2 | 86.4286 | 86.4286 | 84.1348 | 83.2 | 1433.8 | 127900.0186 | 29952 | 13586.56 | 0 | 47107.84
30 | 92 | 95.57 | 95.57 | 93.0337 | 92 | 1443.25 | 141925.8197 | 33120 | 15023.6 | 0 | 51221
31 | 76.8 | 79.7802 | 79.7802 | 77.6629 | 76.8 | 1505.8 | 122345.756 | 27648 | 12541.44 | 0 | 37954.56
32 | 84.462 | 87.7395 | 87.7395 | 85.411 | 84.462 | 1754.3 | 156018.6853 | 30406.32 | 13792.6446 | 0 | 20752.3134
33 | 178.704 | 185.6386 | 185.6386 | 180.7118 | 178.704 | 1834.75 | 345354.5737 | 64333.44 | 29182.3632 | 0 | 29530.836
34 | 122.023 | 126.7581 | 126.7581 | 123.394 | 122.023 | 1841.6 | 237098.9804 | 43928.28 | 19926.3559 | 0 | 19328.4432
35 | 151.211 | 332.0965 | 157.0787 | 323.2829 | 151.211 | 1651.9 | 263770.436 | 54435.96 | 24692.7563 | 0 | 52636.5491
36 | 234.813 | 896.5508 | 243.9249 | 872.7569 | 234.813 | 1590.1 | 393094.9234 | 84532.68 | 38344.9629 | 0 | 96249.8487
37 | 410.829 | 1181.978 | 426.7711 | 1150.609 | 410.829 | 1500.55 | 648500.3296 | 147898.44 | 67088.3757 | 0 | 205188.544
38 | 797.587 | 861.4569 | 828.5372 | 838.5943 | 797.587 | 1617.15 | 1361281.607 | 287131.32 | 130245.9571 | 0 | 305356.1829
39 | 1144.168 | 570.7245 | 570.7245 | 555.5778 | 555.5778 | 1800.05 | 1056136.9589 | 200008.0098 | 90725.8556 | 1078885.8273 | 108738.0087
40 | 1195.968 | 129.5815 | 129.5815 | 126.1425 | 126.1425 | 1764.6 | 234634.3136 | 45411.3071 | 20599.0735 | 1960990.1056 | 29065.7796
41 | 1539.811 | 149.1807 | 149.1807 | 145.2215 | 145.2215 | 1794.05 | 274413.8928 | 52279.7395 | 23714.6707 | 2556282.5561 | 29275.7925
42 | 1385.46 | 0 | 0 | 0 | 0 | 1692.95 | 0 | 0 | 0 | 2539548.18 | 0
43 | 1622.4 | 0 | 0 | 0 | 0 | 1702.9 | 0 | 0 | 0 | 5512915.2 | 0
44 | 953.6 | 0 | 0 | 0 | 0 | 1619.95 | 0 | 0 | 0 | 3240332.8 | 0
45 | 1364 | 0 | 0 | 0 | 0 | 1665.7 | 0 | 0 | 0 | 4634872 | 0
46 | 1566.4 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1815.6 | 589679.3778 | 111351.8261 | 50510.4255 | 4271589.6863 | 56403.1656
47 | 1546.4 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1785 | 1128500.6932 | 215514.4963 | 97759.7701 | 3220449.8159 | 127280
48 | 1576 | 0 | 0 | 0 | 0 | 1633.1 | 0 | 0 | 0 | 2888808 | 0
49 | 1492 | 0 | 0 | 0 | 0 | 1449.35 | 0 | 0 | 0 | 1775480 | 0
50 | 1759.2 | 0 | 0 | 0 | 0 | 1474.1 | 0 | 0 | 0 | 2093448 | 0
51 | 1702.4 | 0 | 0 | 0 | 0 | 1424.85 | 0 | 0 | 0 | 2025856 | 0
52 | 1202.4 | 0 | 0 | 0 | 0 | 1313 | 0 | 0 | 0 | 1430856 | 0
53 | 1508.8 | 0 | 0 | 0 | 0 | 1387.75 | 0 | 0 | 0 | 1795472 | 0
54 | 1304 | 0 | 0 | 0 | 0 | 1436.95 | 0 | 0 | 0 | 1551760 | 0
55 | 1408 | 80.0752 | 80.0752 | 77.9501 | 77.9501 | 1460.05 | 119790.6627 | 28062.0261 | 12729.2468 | 2437981.5173 | 41198.725
56 | 1348.873 | 583.0499 | 583.0499 | 567.5761 | 567.5761 | 1485.15 | 885594.534 | 204327.4009 | 92685.1793 | 1432117.1929 | 286034.6997
57 | 1465.448 | 1280.8774 | 1280.8774 | 1246.8836 | 1246.8836 | 1514.75 | 1986213.0584 | 448878.1069 | 203616.0968 | 400628.4895 | 592251.507
58 | 1762.864 | 1735.1737 | 1735.1737 | 1689.1232 | 1689.1232 | 1521.6 | 2704961.857 | 608084.3444 | 275833.8151 | 135166.925 | 790982.7328
59 | 1691.064 | 1232.8504 | 1232.8504 | 1200.1312 | 1200.1312 | 1512.05 | 1915741.3639 | 432047.2257 | 195981.4221 | 899879.8545 | 573216.3348
60 | 1680.269 | 1763.9341 | 1745.4714 | 1717.1202 | 1680.269 | 1504.25 | 2654678.4978 | 604896.84 | 274387.9277 | 0 | 832993.3567
61 | 1623.593 | 1686.5961 | 1686.5961 | 1641.8348 | 1623.593 | 1490.45 | 2533397.9591 | 584493.48 | 265132.7369 | 0 | 827301.8131
62 | 1593.084 | 2126.1134 | 1654.9032 | 2069.6875 | 1593.084 | 1515.85 | 2543824.5511 | 573510.24 | 260150.6172 | 0 | 771291.6186
63 | 1600.536 | 595.2029 | 595.2029 | 579.4066 | 579.4066 | 1538.5 | 939126.7724 | 208586.3605 | 94617.0907 | 1871730.2692 | 261739.725
64 | 2071.826 | 896.5384 | 896.5384 | 872.7447 | 872.7447 | 1542.5 | 1418773.8256 | 314188.0996 | 142519.213 | 2197915.9842 | 390834.93
65 | 1766.78 | 758.1748 | 758.1748 | 738.0532 | 738.0532 | 1590.05 | 1235446.5631 | 265699.1582 | 120524.0904 | 1885656.193 | 296164.6879
66 | 1972.144 | 45.6388 | 45.6388 | 44.4276 | 44.4276 | 1599.7 | 74910.8679 | 15993.9424 | 7255.03 | 3533504.1288 | 17407.8461
67 | 1702.4 | 0 | 0 | 0 | 0 | 1658.4 | 0 | 0 | 0 | 5784755.2 | 0
68 | 1880.8 | 0 | 0 | 0 | 0 | 1576.2 | 0 | 0 | 0 | 6390958.4 | 0
69 | 1820 | 0 | 0 | 0 | 0 | 1509.75 | 0 | 0 | 0 | 6184360 | 0
70 | 1544 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1570.6 | 511137.9429 | 111351.8261 | 50510.4255 | 4195474.4863 | 131342.2956
71 | 1548 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1468.8 | 929177.4133 | 215514.4963 | 97759.7701 | 3225886.6159 | 314470.4
72 | 1748 | 0 | 0 | 0 | 0 | 1393.5 | 0 | 0 | 0 | 3204084 | 0
73 | 1668.8 | 0 | 0 | 0 | 0 | 1281.35 | 0 | 0 | 0 | 1985872 | 0
74 | 1640 | 0 | 0 | 0 | 0 | 1307.05 | 0 | 0 | 0 | 1951600 | 0
75 | 1404.8 | 0 | 0 | 0 | 0 | 1331.35 | 0 | 0 | 0 | 1671712 | 0
76 | 1329.6 | 0 | 0 | 0 | 0 | 1313 | 0 | 0 | 0 | 1582224 | 0
77 | 1424 | 0 | 0 | 0 | 0 | 1358.25 | 0 | 0 | 0 | 1694560 | 0
78 | 1144.8 | 0 | 0 | 0 | 0 | 1433.15 | 0 | 0 | 0 | 1362312 | 0
79 | 1503.2 | 127.3814 | 127.3814 | 124.0007 | 124.0007 | 1434.05 | 187426.6936 | 44640.2603 | 20249.3181 | 2528072.2748 | 68693.8791
80 | 1213.663 | 950.3505 | 950.3505 | 925.1287 | 925.1287 | 1477.55 | 1439166.9825 | 333046.3461 | 151073.5231 | 528883.3001 | 473109.2996
81 | 1603.942 | 1679.766 | 1666.1826 | 1635.1859 | 1603.942 | 1507.15 | 2544812.6983 | 577419.12 | 261923.7286 | 0 | 790502.8147
82 | 1563.398 | 2480.6283 | 1624.0653 | 2414.7938 | 1563.398 | 1406.5 | 2310248.7828 | 562823.28 | 255302.8934 | 0 | 927876.713
83 | 1507.155 | 3587.2785 | 1565.6398 | 3492.0741 | 1507.155 | 1297.65 | 2061085.8464 | 542575.8 | 246118.4115 | 0 | 1058550.3143
84 | 1580.699 | 3514.0458 | 1642.0376 | 3420.785 | 1580.699 | 1294.7 | 2151906.9171 | 569051.64 | 258128.1467 | 0 | 1114867.0047
85 | 1729.469 | 3414.3829 | 1796.5806 | 3323.7671 | 1729.469 | 1382.95 | 2504598.1123 | 622608.84 | 282422.2877 | 0 | 1067168.8465
86 | 1487.795 | 3583.813 | 1545.5285 | 3488.7006 | 1487.795 | 1404.55 | 2197923.059 | 535606.2 | 242956.9235 | 0 | 885907.5328
87 | 1353.09 | 2622.4927 | 1405.5963 | 2552.8932 | 1353.09 | 1423.4 | 2024724.5927 | 487112.4 | 220959.597 | 0 | 780191.694
88 | 1713.845 | 2341.5771 | 1780.3503 | 2279.4329 | 1713.845 | 1485.8 | 2679954.7021 | 616984.2 | 279870.8885 | 0 | 881259.099
89 | 1749.959 | 1160.6347 | 1160.6347 | 1129.8321 | 1129.8321 | 1551.25 | 1842493.2508 | 406739.5623 | 184501.5848 | 1136692.5758 | 496286.985
90 | 1614.836 | 85.7357 | 85.7357 | 83.4603 | 83.4603 | 1599.7 | 140340.3044 | 30045.7059 | 13629.0661 | 2807011.6686 | 32702.1082
91 | 1603.201 | 0 | 0 | 0 | 0 | 1620.9 | 0 | 0 | 0 | 5447676.998 | 0
92 | 1192 | 0 | 0 | 0 | 0 | 1529.9 | 0 | 0 | 0 | 4050416 | 0
93 | 1322.4 | 0 | 0 | 0 | 0 | 1477.8 | 0 | 0 | 0 | 4493515.2 | 0
94 | 1403.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1581.6 | 513140.6656 | 111351.8261 | 50510.4255 | 3717036.0863 | 127977.6816
95 | 1576.8 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1547.6 | 975051.6426 | 215514.4963 | 97759.7701 | 3323749.0159 | 267820.8
96 | 1240.8 | 0 | 0 | 0 | 0 | 1393.5 | 0 | 0 | 0 | 2274386.4 | 0
97 | 1476 | 0 | 0 | 0 | 0 | 1395.35 | 0 | 0 | 0 | 2705508 | 0
98 | 1014.4 | 0 | 0 | 0 | 0 | 1334.6 | 0 | 0 | 0 | 1859395.2 | 0
99 | 1200.8 | 0 | 0 | 0 | 0 | 1343.9 | 0 | 0 | 0 | 2201066.4 | 0
100 | 1056 | 0 | 0 | 0 | 0 | 1313 | 0 | 0 | 0 | 1935648 | 0
101 | 1512.8 | 0 | 0 | 0 | 0 | 1423.7 | 0 | 0 | 0 | 2772962.4 | 0
102 | 1194.4 | 0 | 0 | 0 | 0 | 1391.95 | 0 | 0 | 0 | 2189335.2 | 0
103 | 1352.8 | 124.3003 | 124.3003 | 121.0014 | 121.0014 | 1456.25 | 185262.1255 | 43560.5035 | 19759.5284 | 2257886.8363 | 64402.8375
104 | 1276.497 | 1256.5652 | 1256.5652 | 1223.2167 | 1223.2167 | 1436.35 | 1845222.7163 | 440358.0035 | 199751.2832 | 97662.8334 | 674881.8183
105 | 1178.106 | 1841.644 | 1223.8221 | 1792.7677 | 1178.106 | 1430 | 1771846.5988 | 424118.16 | 192384.7098 | 0 | 671520.42
106 | 1381.448 | 2917.0053 | 1435.0547 | 2839.5896 | 1381.448 | 1462.1 | 2124827.1529 | 497321.28 | 225590.4584 | 0 | 743080.8792
107 | 1214.49 | 3918.1669 | 1261.618 | 3814.1809 | 1214.49 | 1481.95 | 1902806.8572 | 437216.4 | 198326.217 | 0 | 629166.5445
108 | 1201.671 | 4215.7772 | 1248.3015 | 4103.8927 | 1201.671 | 1360.7 | 1725800.1378 | 432601.56 | 196232.8743 | 0 | 768228.2703
109 | 1248.417 | 4200.3353 | 1296.8615 | 4088.8607 | 1248.417 | 1291.9 | 1699214.0921 | 449430.12 | 203866.4961 | 0 | 884004.0777
110 | 1246.649 | 3881.9791 | 1295.0249 | 3778.9535 | 1246.649 | 1409.7 | 1857130.2656 | 448793.64 | 203577.7817 | 0 | 735896.9047
111 | 987.594 | 3290.5138 | 1025.9173 | 3203.1853 | 987.594 | 1429.45 | 1489070.8993 | 355533.84 | 161274.1002 | 0 | 563471.7567
112 | 489.888 | 2406.4774 | 508.898 | 2342.6108 | 489.888 | 1484.35 | 766711.3022 | 176359.68 | 79998.7104 | 0 | 252610.7472
113 | 193.991 | 1210.2823 | 201.5188 | 1178.1621 | 193.991 | 1540.55 | 314871.1631 | 69836.76 | 31678.7303 | 0 | 89129.165
114 | 170.644 | 177.2658 | 177.2658 | 172.5613 | 170.644 | 1564.7 | 280876.5191 | 61431.84 | 27866.1652 | 0 | 74281.3332
115 | 118.4 | 122.9945 | 122.9945 | 119.7303 | 118.4 | 1655.4 | 206449.8993 | 42624 | 19334.72 | 0 | 40800.64
116 | 127.2 | 132.136 | 132.136 | 128.6291 | 127.2 | 1529.9 | 205147.1187 | 45792 | 20771.76 | 0 | 59796.72
117 | 100.8 | 104.7115 | 104.7115 | 101.9325 | 100.8 | 1499.05 | 159099.7176 | 36288 | 16460.64 | 0 | 50495.76
118 | 94.4 | 98.0632 | 98.0632 | 95.4606 | 94.4 | 1495.6 | 148368.5053 | 33984 | 15415.52 | 0 | 47615.36
119 | 94.4 | 98.0632 | 98.0632 | 95.4606 | 94.4 | 1472.6 | 146480.7614 | 33984 | 15415.52 | 0 | 49786.56
120 | 99.2 | 103.0494 | 103.0494 | 100.3146 | 99.2 | 1454.85 | 152262.4775 | 35712 | 16199.36 | 0 | 54078.88
121 | 92.8 | 0 | 0 | 0 | 0 | 1425.85 | 0 | 0 | 0 | 110432 | 0
122 | 91.2 | 0 | 0 | 0 | 0 | 1303.15 | 0 | 0 | 0 | 108528 | 0
123 | 85.6 | 0 | 0 | 0 | 0 | 1312.6 | 0 | 0 | 0 | 101864 | 0
124 | 93.6 | 0 | 0 | 0 | 0 | 1311.9 | 0 | 0 | 0 | 111384 | 0
125 | 89.6 | 92.866 | 92.866 | 90.4014 | 89.6 | 1336.7 | 126028.3744 | 32256 | 14631.68 | 0 | 58689.4473
126 | 93.6 | 97.2321 | 97.2321 | 94.6516 | 93.6 | 1321.1 | 130112.8719 | 33696 | 15284.88 | 0 | 63545.04
127 | 81.6 | 84.7665 | 84.7665 | 82.5168 | 81.6 | 1435.95 | 123268.8437 | 29376 | 13325.28 | 0 | 46026.48
128 | 95.06 | 407.2509 | 98.7488 | 396.4427 | 95.06 | 1476.3 | 147330.3776 | 34221.6 | 15523.298 | 0 | 49782.922
129 | 615.277 | 1884.2194 | 639.1537 | 1834.2132 | 615.277 | 1507 | 974245.4959 | 221499.72 | 100474.7341 | 0 | 303331.561
130 | 1487.855 | 2057.2915 | 1545.5908 | 2002.6921 | 1487.855 | 1577.65 | 2470376.7332 | 535627.8 | 242966.7215 | 0 | 628395.5592
131 | 1570.749 | 3859.9377 | 1631.7015 | 3757.4971 | 1570.749 | 1508.35 | 2499987.1987 | 565469.64 | 256503.3117 | 0 | 772258.7459
132 | 1374.539 | 4106.2851 | 1427.8776 | 3997.3065 | 1374.539 | 1443.6 | 2088100.4842 | 494834.04 | 224462.2187 | 0 | 764793.4996
133 | 1744.337 | 3403.9388 | 1812.0256 | 3313.6001 | 1744.337 | 1429.3 | 2619315.2512 | 627961.32 | 284850.2321 | 0 | 995493.1259
134 | 1288.096 | 1968.0665 | 1338.0802 | 1915.8351 | 1288.096 | 1503.95 | 2038293.6251 | 463714.56 | 210346.0768 | 0 | 638960.0208
135 | 1540.824 | 3086.3564 | 1600.6153 | 3004.4462 | 1540.824 | 1526.2 | 2475124.7751 | 554696.64 | 251616.5592 | 0 | 730042.4112
136 | 1378.996 | 1810.512 | 1432.5076 | 1762.462 | 1378.996 | 1546.6 | 2245177.6981 | 496438.56 | 225190.0468 | 0 | 625236.7864
137 | 1206.845 | 799.5369 | 799.5369 | 778.3176 | 778.3176 | 1625.3 | 1329613.3953 | 280194.3283 | 127099.2606 | 785490.7636 | 285466.6938
138 | 1353.643 | 88.1893 | 88.1893 | 85.8488 | 85.8488 | 1542.4 | 139197.885 | 30905.5797 | 14019.1143 | 2323866.7092 | 38453.5008
139 | 1672.005 | 0 | 0 | 0 | 0 | 1545.2 | 0 | 0 | 0 | 5681472.99 | 0
140 | 1202.4 | 0 | 0 | 0 | 0 | 1501.35 | 0 | 0 | 0 | 4085755.2 | 0
141 | 1490.4 | 0 | 0 | 0 | 0 | 1449.05 | 0 | 0 | 0 | 5064379.2 | 0
142 | 825.6 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1477.45 | 481153.3507 | 111351.8261 | 50510.4255 | 1754351.2863 | 159834.4587
143 | 1327.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1454.45 | 919528.7963 | 215514.4963 | 97759.7701 | 2475608.2159 | 322965.6
144 | 1368.8 | 0 | 0 | 0 | 0 | 1438.95 | 0 | 0 | 0 | 2509010.4 | 0
145 | 1056 | 0 | 0 | 0 | 0 | 1363.3 | 0 | 0 | 0 | 1256640 | 0
146 | 1168.8 | 0 | 0 | 0 | 0 | 1418.1 | 0 | 0 | 0 | 1390872 | 0
147 | 1128 | 0 | 0 | 0 | 0 | 1415.25 | 0 | 0 | 0 | 1342320 | 0
148 | 982.4 | 0 | 0 | 0 | 0 | 1414.15 | 0 | 0 | 0 | 1169056 | 0
149 | 904 | 0 | 0 | 0 | 0 | 1418.2 | 0 | 0 | 0 | 1075760 | 0
150 | 892.8 | 0 | 0 | 0 | 0 | 1425.1 | 0 | 0 | 0 | 1062432 | 0
151 | 1122.4 | 134.1647 | 134.1647 | 130.6041 | 130.6041 | 1430.05 | 196419.8463 | 47017.4725 | 21327.648 | 1817961.9024 | 72863.5479
152 | 820.686 | 852.5325 | 852.5325 | 829.9068 | 820.686 | 1439.1 | 1241225.7057 | 295446.96 | 134018.0238 | 0 | 460322.7774
153 | 1276.219 | 2004.6303 | 1325.7434 | 1951.4286 | 1276.219 | 1443.7 | 1938340.6773 | 459438.84 | 208406.5627 | 0 | 709960.6297
154 | 1102.819 | 3418.7656 | 1145.6136 | 3328.0335 | 1102.819 | 1350.65 | 1571975.4881 | 397014.84 | 180090.3427 | 0 | 716115.5177
155 | 1394.158 | 3982.1739 | 1448.258 | 3876.4891 | 1394.158 | 1329 | 1960508.1872 | 501896.88 | 227666.0014 | 0 | 935480.018
156 | 1343.063 | 4248.5525 | 1395.1802 | 4135.7982 | 1343.063 | 1348.7 | 1918539.791 | 483502.68 | 219322.1879 | 0 | 874736.9319
157 | 1117.045 | 4225.5762 | 1160.3917 | 4113.4317 | 1117.045 | 1251.05 | 1482364.2025 | 402136.2 | 182413.4485 | 0 | 836610.8527
158 | 1320.721 | 3894.6473 | 1371.9712 | 3791.2855 | 1320.721 | 1196.9 | 1678278.8608 | 475459.56 | 215673.7393 | 0 | 1060671.0351
159 | 965.839 | 3300.2609 | 1003.3181 | 3212.6737 | 965.839 | 1169.15 | 1193134.8941 | 347702.04 | 157721.5087 | 0 | 802467.3331
160 | 1201.115 | 2443.5939 | 1247.724 | 2378.7423 | 1201.115 | 1288.4 | 1630372.2428 | 432401.4 | 196142.0795 | 0 | 854713.434
161 | 1181.242 | 1257.7006 | 1227.0798 | 1224.322 | 1181.242 | 1407.4 | 1746298.208 | 425247.12 | 192896.8186 | 0 | 700004.0092
162 | 1081.511 | 121.0062 | 121.0062 | 117.7948 | 117.7948 | 1518.15 | 187549.1476 | 42406.1176 | 19235.8861 | 1766491.8476 | 55558.7505
163 | 1008 | 0 | 0 | 0 | 0 | 1609.65 | 0 | 0 | 0 | 3425184 | 0
164 | 1229.6 | 0 | 0 | 0 | 0 | 1532.25 | 0 | 0 | 0 | 4178180.8 | 0
165 | 845.6 | 0 | 0 | 0 | 0 | 1466.05 | 0 | 0 | 0 | 2873348.8 | 0
166 | 1182.4 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1416.65 | 462471.0748 | 111351.8261 | 50510.4255 | 2966757.6863 | 178431.5979
167 | 1105.6 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1314.65 | 830567.6081 | 215514.4963 | 97759.7701 | 1722611.4159 | 405727.2
168 | 876.8 | 0 | 0 | 0 | 0 | 1274.6 | 0 | 0 | 0 | 1607174.4 | 0
169 | 1152.8 | 0 | 0 | 0 | 0 | 1358.9 | 0 | 0 | 0 | 1371832 | 0
170 | 1130.4 | 0 | 0 | 0 | 0 | 1333.8 | 0 | 0 | 0 | 1345176 | 0
171 | 1128.8 | 0 | 0 | 0 | 0 | 1313.55 | 0 | 0 | 0 | 1343272 | 0
172 | 1064.8 | 0 | 0 | 0 | 0 | 1305.55 | 0 | 0 | 0 | 1267112 | 0
173 | 1179.2 | 0 | 0 | 0 | 0 | 1233.8 | 0 | 0 | 0 | 1403248 | 0
174 | 769.6 | 0 | 0 | 0 | 0 | 1283.2 | 0 | 0 | 0 | 915824 | 0
175 | 1032.8 | 122.0003 | 122.0003 | 118.7625 | 118.7625 | 1455.15 | 182286.2147 | 42754.5084 | 19393.9201 | 1675430.6946 | 63338.8125
176 | 1022.571 | 979.4589 | 979.4589 | 953.4646 | 953.4646 | 1481.35 | 1488975.9647 | 343247.2442 | 155700.7638 | 126672.091 | 484053.9704
177 | 1349.006 | 1097.2126 | 1097.2126 | 1068.0932 | 1068.0932 | 1514.75 | 1704701.4752 | 384513.5377 | 174419.6131 | 514913.2352 | 507328.3897
178 | 1477.914 | 820.4968 | 820.4968 | 798.7213 | 798.7213 | 1514 | 1274243.1352 | 287539.6593 | 130431.1844 | 1244960.2633 | 379966.95
179 | 1484.496 | 654.5852 | 654.5852 | 637.2128 | 637.2128 | 1452.1 | 976723.6948 | 229396.615 | 104056.8534 | 1553070.0701 | 341743.8586
180 | 1349.631 | 1043.5905 | 1043.5905 | 1015.8942 | 1015.8942 | 1343.3 | 1437887.9785 | 365721.9114 | 165895.5226 | 611739.5576 | 653025.1068
181 | 1462.071 | 1462.7929 | 1462.7929 | 1423.9712 | 1423.9712 | 1334.35 | 1997500.1482 | 512629.6248 | 232534.4937 | 69836.9699 | 927815.5869
182 | 1295.145 | 2241.6139 | 1345.4028 | 2182.1227 | 1295.145 | 1505.85 | 2054534.7191 | 466252.2 | 211497.1785 | 0 | 639995.9018
183 | 1332.189 | 2476.0867 | 1383.8843 | 2410.3727 | 1332.189 | 1530.9 | 2146407.0361 | 479588.04 | 217546.4637 | 0 | 624929.8599
184 | 1434.587 | 1109.3012 | 1109.3012 | 1079.8609 | 1079.8609 | 1542.5 | 1749934.5846 | 388749.9265 | 176341.2861 | 650212.9284 | 483585.735
185 | 1105.581 | 688.8626 | 688.8626 | 670.5806 | 670.5806 | 1598.05 | 1126420.7009 | 241408.9998 | 109505.8046 | 797355.8155 | 263838.3722
186 | 1217.803 | 24.3537 | 24.3537 | 23.7074 | 23.7074 | 1647.7 | 41087.6146 | 8534.6653 | 3871.419 | 2188777.2282 | 8175.4738
187 | 1003.211 | 0 | 0 | 0 | 0 | 1658.9 | 0 | 0 | 0 | 3408910.978 | 0
188 | 1195.2 | 0 | 0 | 0 | 0 | 1541.4 | 0 | 0 | 0 | 4061289.6 | 0
189 | 1054.4 | 0 | 0 | 0 | 0 | 1508.65 | 0 | 0 | 0 | 3582851.2 | 0
190 | 1257.6 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1581.6 | 513400.0078 | 111351.8261 | 50510.4255 | 3222287.2863 | 127977.6816
191 | 1286.4 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1558.6 | 981719.1525 | 215514.4963 | 97759.7701 | 2336969.8159 | 261308.8
192 | 1148 | 0 | 0 | 0 | 0 | 1451.05 | 0 | 0 | 0 | 2104284 | 0
193 | 1193.6 | 0 | 0 | 0 | 0 | 1431.3 | 0 | 0 | 0 | 1420384 | 0
194 | 937.6 | 0 | 0 | 0 | 0 | 1427.3 | 0 | 0 | 0 | 1115744 | 0
195 | 1222.4 | 0 | 0 | 0 | 0 | 1428.65 | 0 | 0 | 0 | 1454656 | 0
196 | 1073.6 | 0 | 0 | 0 | 0 | 1428.1 | 0 | 0 | 0 | 1277584 | 0
197 | 942.4 | 0 | 0 | 0 | 0 | 1431.3 | 0 | 0 | 0 | 1121456 | 0
198 | 1051.2 | 0 | 0 | 0 | 0 | 1480.75 | 0 | 0 | 0 | 1250928 | 0
199 | 951.2 | 111.0233 | 111.0233 | 108.0768 | 108.0768 | 1540.05 | 175072.606 | 38907.6475 | 17648.9412 | 1545444.8283 | 48658.5704
200 | 1114.771 | 1105.2966 | 1105.2966 | 1075.9626 | 1075.9626 | 1565.15 | 1770145.9971 | 387346.534 | 175704.6917 | 71135.8074 | 457985.3246
201 | 1167.854 | 1856.7191 | 1213.1723 | 1807.4428 | 1167.854 | 1600.75 | 1970467.0076 | 420427.44 | 190710.5582 | 0 | 466265.7095
202 | 1664.173 | 2878.2984 | 1728.7508 | 2801.9099 | 1664.173 | 1561.6 | 2739676.5347 | 599102.28 | 271759.4509 | 0 | 729573.4432
203 | 1338.632 | 3841.0304 | 1390.5773 | 3739.0916 | 1338.632 | 1512.05 | 2139123.9799 | 481907.52 | 218598.6056 | 0 | 653185.4844
204 | 1317.153 | 4111.7616 | 1368.2648 | 4002.6377 | 1317.153 | 1503.15 | 2083772.1898 | 474175.08 | 215091.0849 | 0 | 654427.468
205 | 1355.422 | 4082.4933 | 1408.0188 | 3974.1462 | 1355.422 | 1489.35 | 2120019.3059 | 487951.92 | 221340.4126 | 0 | 692146.2443
206 | 1226.996 | 2949.7972 | 1274.6093 | 2871.5112 | 1226.996 | 1555.85 | 2008971.2172 | 441718.56 | 200368.4468 | 0 | 544970.2734
207 | 1258.144 | 2371.8333 | 1306.966 | 2308.8861 | 1258.144 | 1621.5 | 2145784.5476 | 452931.84 | 205454.9152 | 0 | 476207.504
208 | 1216.588 | 1243.9801 | 1243.9801 | 1210.9656 | 1210.9656 | 1542.5 | 1964381.4001 | 435947.6012 | 197750.6758 | 10305.9345 | 542297.625
209 | 1274.12 | 995.953 | 995.953 | 969.521 | 969.521 | 1598.05 | 1628071.7697 | 349027.5469 | 158322.7734 | 558330.0337 | 381455.3734
210 | 1113.621 | 102.2828 | 102.2828 | 99.5683 | 99.5683 | 1651.2 | 172800.905 | 35844.5749 | 16259.4974 | 1858758.6659 | 33994.7456
211 | 1163.2 | 0 | 0 | 0 | 0 | 1746.15 | 0 | 0 | 0 | 3952553.6 | 0
212 | 1064 | 0 | 0 | 0 | 0 | 1619.95 | 0 | 0 | 0 | 3615472 | 0
213 | 1449.6 | 0 | 0 | 0 | 0 | 1556.55 | 0 | 0 | 0 | 4925740.8 | 0
214 | 1246.4 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1605.6 | 521786.2582 | 111351.8261 | 50510.4255 | 3184229.6863 | 120636.7056
215 | 1491.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1558.85 | 983259.9056 | 215514.4963 | 97759.7701 | 3032880.2159 | 261160.8
216 | 1336.8 | 0 | 0 | 0 | 0 | 1497.85 | 0 | 0 | 0 | 2450354.4 | 0
217 | 1711.2 | 0 | 0 | 0 | 0 | 1439.15 | 0 | 0 | 0 | 2036328 | 0
218 | 1122.4 | 0 | 0 | 0 | 0 | 1436.1 | 0 | 0 | 0 | 1335656 | 0
219 | 1392 | 0 | 0 | 0 | 0 | 1433.65 | 0 | 0 | 0 | 1656480 | 0
220 | 1262.4 | 0 | 0 | 0 | 0 | 1428.1 | 0 | 0 | 0 | 1502256 | 0
221 | 1117.6 | 0 | 0 | 0 | 0 | 1431.3 | 0 | 0 | 0 | 1329944 | 0
222 | 1514.4 | 0 | 0 | 0 | 0 | 1440.75 | 0 | 0 | 0 | 1802136 | 0
223 | 1350.4 | 98.7051 | 98.7051 | 96.0856 | 96.0856 | 1460.05 | 148066.0237 | 34590.8047 | 15690.7734 | 2299158.3525 | 50783.9174
224 | 1353.11 | 1271.9894 | 1271.9894 | 1238.2315 | 1238.2315 | 1485.15 | 1938982.2037 | 445763.34 | 202203.204 | 210572.2905 | 624017.7643
225 | 1445.428 | 1874.4494 | 1501.5175 | 1824.7025 | 1445.428 | 1554.75 | 2371670.1403 | 520354.08 | 236038.3924 | 0 | 643576.817
226 | 1336.752 | 2903.5393 | 1388.6243 | 2826.4809 | 1336.752 | 1521.6 | 2145603.727 | 481230.72 | 218291.6016 | 0 | 639502.1568
227 | 1366.848 | 3864.6331 | 1419.8882 | 3762.0678 | 1366.848 | 1512.05 | 2186443.063 | 492065.28 | 223206.2784 | 0 | 666953.4816
228 | 1423.45 | 4155.7446 | 1478.6866 | 4045.4534 | 1423.45 | 1438.05 | 2165263.1159 | 512442 | 232449.385 | 0 | 799907.7275
229 | 1626.909 | 2387.5172 | 1690.0408 | 2324.1538 | 1626.909 | 1458.15 | 2507240.2259 | 585687.24 | 265674.2397 | 0 | 881540.6416
230 | 1552.301 | 2945.267 | 1612.5376 | 2867.1012 | 1552.301 | 1515.85 | 2488461.777 | 558828.36 | 253490.7533 | 0 | 751546.5292
231 | 1372.937 | 3179.5383 | 1426.2135 | 3095.155 | 1372.937 | 1533.6 | 2221304.335 | 494257.32 | 224200.6121 | 0 | 640337.8168
232 | 1588.328 | 2379.0779 | 1649.9627 | 2315.9385 | 1588.328 | 1473.9 | 2468112.6655 | 571798.08 | 259373.9624 | 0 | 835619.3608
233 | 1609.75 | 909.8745 | 909.8745 | 885.727 | 885.727 | 1555.05 | 1450260.6563 | 318861.7062 | 144639.2128 | 1327134.2293 | 385767.6455
234 | 1634.626 | 106.0911 | 106.0911 | 103.2755 | 103.2755 | 1564.7 | 170446.1855 | 37179.163 | 16864.8814 | 2806965.5533 | 44004.9123
235 | 1760.002 | 0 | 0 | 0 | 0 | 1615.9 | 0 | 0 | 0 | 5980486.796 | 0
236 | 1500 | 0 | 0 | 0 | 0 | 1529.9 | 0 | 0 | 0 | 5097000 | 0
237 | 1500 | 0 | 0 | 0 | 0 | 1496.05 | 0 | 0 | 0 | 5097000 | 0
238 | 1466.4 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1535.6 | 500157.6406 | 111351.8261 | 50510.4255 | 3931789.6863 | 142047.8856
239 | 1682.4 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1472.6 | 932112.336 | 215514.4963 | 97759.7701 | 3682577.8159 | 312220.8
240 | 1397.6 | 0 | 0 | 0 | 0 | 1446.15 | 0 | 0 | 0 | 2561800.8 | 0
241 | 1472.8 | 0 | 0 | 0 | 0 | 1434 | 0 | 0 | 0 | 1752632 | 0
242 | 1350.4 | 0 | 0 | 0 | 0 | 1423.5 | 0 | 0 | 0 | 1606976 | 0
243 | 1287.2 | 0 | 0 | 0 | 0 | 1406.25 | 0 | 0 | 0 | 1531768 | 0
244 | 1179.2 | 0 | 0 | 0 | 0 | 1348.6 | 0 | 0 | 0 | 1403248 | 0
245 | 1111.2 | 0 | 0 | 0 | 0 | 1321.55 | 0 | 0 | 0 | 1322328 | 0
246 | 1189.6 | 0 | 0 | 0 | 0 | 1365.85 | 0 | 0 | 0 | 1415624 | 0
247 | 1056 | 77.4325 | 77.4325 | 75.3775 | 75.3775 | 1415.4 | 112517.2487 | 27135.8962 | 12309.144 | 1797481.0618 | 43133.5418
248 | 1007.057 | 967.3765 | 967.3765 | 941.7029 | 941.7029 | 1390.95 | 1379722.78 | 339013.0397 | 153780.0816 | 119794.0873 | 561411.9361
249 | 1526.413 | 1044.1941 | 1044.1941 | 1016.4817 | 1016.4817 | 1504.95 | 1611495.6468 | 365933.4214 | 165991.4659 | 934704.0251 | 492564.3539
250 | 1751.451 | 2041.3189 | 1819.4156 | 1987.1434 | 1751.451 | 1499.2 | 2767539.0033 | 630522.36 | 286011.9483 | 0 | 877126.6608
251 | 1601.404 | 3355.1503 | 1663.5471 | 3266.1064 | 1601.404 | 1321.65 | 2244296.8514 | 576505.44 | 261509.2732 | 0 | 1086312.4034
252 | 1468.113 | 3484.7713 | 1525.0828 | 3392.2874 | 1468.113 | 1402.1 | 2182555.7835 | 528520.68 | 239742.8529 | 0 | 877784.7627
253 | 1613.967 | 2747.195 | 1676.5966 | 2674.2859 | 1613.967 | 1440.85 | 2460486.1473 | 581028.12 | 263560.8111 | 0 | 902449.648
254 | 1643.485 | 1707.26 | 1707.26 | 1661.9503 | 1643.485 | 1444.9 | 2516959.6237 | 591654.6 | 268381.1005 | 0 | 912298.5235
255 | 1670.927 | 2680.5172 | 1735.7669 | 2609.3778 | 1670.927 | 1371.5 | 2420930.6139 | 601533.72 | 272862.3791 | 0 | 1050177.6195
256 | 1625.599 | 891.9313 | 891.9313 | 868.2599 | 868.2599 | 1400.4 | 1282873.8051 | 312573.5611 | 141786.8404 | 1388202.5851 | 509596.4424
257 | 1615.953 | 435.8025 | 435.8025 | 424.2365 | 424.2365 | 1551.25 | 693376.4728 | 152725.1487 | 69277.8244 | 2184416.3004 | 186349.2712
258 | 1849.735 | 46.2538 | 46.2538 | 45.0263 | 45.0263 | 1564.7 | 74242.0158 | 16209.4569 | 7352.7897 | 3308031.1038 | 19184.9769
259 | 1528.006 | 0 | 0 | 0 | 0 | 1572.9 | 0 | 0 | 0 | 5192164.388 | 0
260 | 1338.4 | 0 | 0 | 0 | 0 | 1529.9 | 0 | 0 | 0 | 4547883.2 | 0
261 | 1358.4 | 0 | 0 | 0 | 0 | 1508.65 | 0 | 0 | 0 | 4615843.2 | 0
262 | 1418.4 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1495.6 | 486787.1969 | 111351.8261 | 50510.4255 | 3768685.6863 | 154282.8456
263 | 1347.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1472.6 | 932603.3287 | 215514.4963 | 97759.7701 | 2543568.2159 | 312220.8
264 | 1475.2 | 0 | 0 | 0 | 0 | 1451.05 | 0 | 0 | 0 | 2704041.6 | 0
265 | 1247.2 | 0 | 0 | 0 | 0 | 1332.75 | 0 | 0 | 0 | 2286117.6 | 0
266 | 1436 | 0 | 0 | 0 | 0 | 1336.9 | 0 | 0 | 0 | 2632188 | 0
267 | 1268.8 | 0 | 0 | 0 | 0 | 1281.5 | 0 | 0 | 0 | 2325710.4 | 0
268 | 1268.8 | 0 | 0 | 0 | 0 | 1280.95 | 0 | 0 | 0 | 2325710.4 | 0
269 | 1345.6 | 0 | 0 | 0 | 0 | 1294.3 | 0 | 0 | 0 | 2466484.8 | 0
270 | 1118.4 | 0 | 0 | 0 | 0 | 1366 | 0 | 0 | 0 | 2050027.2 | 0
271 | 1312.8 | 29.8002 | 29.8002 | 29.0093 | 29.0093 | 1452.45 | 44412.8815 | 10443.3519 | 4737.2205 | 2353188.333 | 15548.2298
272 | 1080.054 | 1121.9652 | 1121.9652 | 1092.1889 | 1080.054 | 1477.55 | 1681588.1295 | 388819.44 | 176372.8182 | 0 | 564274.2123
273 | 1017.97 | 1394.8239 | 1057.4721 | 1357.806 | 1017.97 | 1514.75 | 1625105.9352 | 366469.2 | 166234.501 | 0 | 493969.9425
274 | 1165.131 | 1210.3436 | 1210.3436 | 1178.2218 | 1165.131 | 1517.8 | 1867082.3858 | 419447.16 | 190265.8923 | 0 | 561826.1682
275 | 1340.908 | 1392.9416 | 1392.9416 | 1355.9737 | 1340.908 | 1372.5 | 1953303.8419 | 482726.88 | 218970.2764 | 0 | 841419.77
276 | 1421.717 | 2788.797 | 1476.8864 | 2714.7839 | 1421.717 | 1366.7 | 2061476.7285 | 511818.12 | 232166.3861 | 0 | 900373.3761
277 | 1076.722 | 2436.8043 | 1118.5039 | 2372.1328 | 1076.722 | 1350.9 | 1540308.3615 | 387619.92 | 175828.7026 | 0 | 698900.2502
278 | 1233.429 | 3029.2575 | 1281.2919 | 2948.8626 | 1233.429 | 1369.35 | 1791114.8481 | 444034.44 | 201418.9557 | 0 | 777861.9989
279 | 966.192 | 899.5197 | 899.5197 | 875.647 | 875.647 | 1388.2 | 1286409.5642 | 315232.908 | 142993.1497 | 165969.0458 | 524388.4632
280 | 1205.397 | 1016.0487 | 1016.0487 | 989.0833 | 989.0833 | 1383.8 | 1443448.4956 | 356069.9927 | 161517.305 | 396502.988 | 596580.8082
281 | 1237.532 | 16.009 | 16.009 | 15.5841 | 15.5841 | 1555.05 | 25543.1465 | 5610.2938 | 2544.8916 | 2239830.4103 | 6787.7122
282 | 859.624 | 1.0232 | 1.0232 | 0.99607 | 0.99607 | 1564.7 | 1643.5725 | 358.5841 | 162.6577 | 1573865.0014 | 424.4175
283 | 1175.2 | 0 | 0 | 0 | 0 | 1572.9 | 0 | 0 | 0 | 2154141.6 | 0
284 | 1189.6 | 0 | 0 | 0 | 0 | 1529.9 | 0 | 0 | 0 | 2180536.8 | 0
285 | 1346.4 | 0 | 0 | 0 | 0 | 1509.75 | 0 | 0 | 0 | 2467951.2 | 0
286 | 1161.6 | 175.6349 | 175.6349 | 170.9736 | 170.9736 | 1495.6 | 269015.507 | 61550.5033 | 27919.9922 | 1815818.1542 | 85280.9256
287 | 1086.4 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1465 | 925909.5422 | 215514.4963 | 97759.7701 | 894043.2233 | 316720
288 | 136.8 | 142.1085 | 142.1085 | 138.337 | 136.8 | 1344.7 | 194173.7344 | 49248 | 22339.44 | 0 | 89645.04
289 | 106.4 | 0 | 0 | 0 | 0 | 1271.1 | 0 | 0 | 0 | 126616 | 0
290 | 88 | 0 | 0 | 0 | 0 | 1253.2 | 0 | 0 | 0 | 104720 | 0
291 | 92 | 0 | 0 | 0 | 0 | 1274.7 | 0 | 0 | 0 | 109480 | 0
292 | 88 | 0 | 0 | 0 | 0 | 1267 | 0 | 0 | 0 | 104720 | 0
293 | 92 | 0 | 0 | 0 | 0 | 1232.7 | 0 | 0 | 0 | 109480 | 0
294 | 84.8 | 0 | 0 | 0 | 0 | 1271.2 | 0 | 0 | 0 | 100912 | 0
295 | 82.4 | 85.5975 | 85.5975 | 83.3258 | 82.4 | 1296.75 | 112614.593 | 29664 | 13455.92 | 0 | 57947.8
296 | 81.362 | 603.5539 | 84.5192 | 587.5359 | 81.362 | 1472.5 | 126051.6882 | 29290.32 | 13286.4146 | 0 | 42918.455
297 | 804.961 | 1992.0805 | 836.1973 | 1939.2118 | 804.961 | 1507 | 1276293.79 | 289785.96 | 131450.1313 | 0 | 396845.773
298 | 971.201 | 3198.5453 | 1008.8882 | 3113.6576 | 971.201 | 1508.85 | 1542705.6043 | 349632.36 | 158597.1233 | 0 | 477005.3712
299 | 1378.581 | 3704.0744 | 1432.0765 | 3605.7703 | 1378.581 | 1413.45 | 2063993.9578 | 496289.16 | 225122.2773 | 0 | 808606.6856
300 | 1301.865 | 3965.6205 | 1352.3835 | 3860.3751 | 1301.865 | 1326.9 | 1829995.4612 | 468671.4 | 212594.5545 | 0 | 876285.3315
301 | 1411.199 | 3814.4297 | 1465.9602 | 3713.1969 | 1411.199 | 1319.75 | 1967083.9697 | 508031.64 | 230448.7967 | 0 | 959968.1197
302 | 1430.445 | 2791.367 | 1485.9531 | 2717.2857 | 1430.445 | 1358.55 | 2059792.9314 | 514960.2 | 233591.6685 | 0 | 917558.9453
303 | 1147.683 | 1710.8906 | 1192.2185 | 1665.4845 | 1147.683 | 1348.45 | 1634234.2969 | 413165.88 | 187416.6339 | 0 | 747772.8587
304 | 1193.172 | 991.0145 | 991.0145 | 964.7136 | 964.7136 | 1370.1 | 1394998.7405 | 347296.8781 | 157537.7228 | 418764.3382 | 594818.9793
305 | 1254.203 | 631.639 | 631.639 | 614.8756 | 614.8756 | 1521.8 | 986116.3367 | 221355.2303 | 100409.192 | 1171887.0512 | 287813.7558
306 | 1409.776 | 81.382 | 81.382 | 79.2222 | 79.2222 | 1542.4 | 128908.3827 | 28519.9944 | 12936.9863 | 2438905.1033 | 35485.5072
307 | 1164.8 | 0 | 0 | 0 | 0 | 1545.2 | 0 | 0 | 0 | 3957990.4 | 0
308 | 1167.2 | 0 | 0 | 0 | 0 | 1470.15 | 0 | 0 | 0 | 3966145.6 | 0
309 | 1375.2 | 0 | 0 | 0 | 0 | 1416.1 | 0 | 0 | 0 | 4672929.6 | 0
310 | 1362.4 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1477.45 | 481328.4101 | 111351.8261 | 50510.4255 | 3578397.6863 | 159834.4587
311 | 1214.4 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1436.05 | 907486.3863 | 215514.4963 | 97759.7701 | 2092313.8159 | 333858.4
312 | 949.6 | 0 | 0 | 0 | 0 | 1282.6 | 0 | 0 | 0 | 1740616.8 | 0
313 | 1832.8 | 0 | 0 | 0 | 0 | 1338.7 | 0 | 0 | 0 | 2181032 | 0
314 | 1784.8 | 0 | 0 | 0 | 0 | 1298.2 | 0 | 0 | 0 | 2123912 | 0
315 | 1888 | 0 | 0 | 0 | 0 | 1288.85 | 0 | 0 | 0 | 2246720 | 0
316 | 2028.8 | 0 | 0 | 0 | 0 | 1287.75 | 0 | 0 | 0 | 2414272 | 0
317 | 2156.8 | 0 | 0 | 0 | 0 | 1294.5 | 0 | 0 | 0 | 2566592 | 0
318 | 2129.6 | 0 | 0 | 0 | 0 | 1281.1 | 0 | 0 | 0 | 2534224 | 0
319 | 1976.8 | 104.8434 | 104.8434 | 102.061 | 102.061 | 1278.05 | 137450.7899 | 36741.9452 | 16666.5546 | 3436396.6623 | 72124.2489
320 | 1127.549 | 1171.3033 | 1171.3033 | 1140.2175 | 1127.549 | 1339.4 | 1590235.774 | 405917.64 | 184128.7517 | 0 | 744858.8694
321 | 1638.403 | 1875.2711 | 1701.9808 | 1825.5024 | 1638.403 | 1431.5 | 2465815.9874 | 589825.08 | 267551.2099 | 0 | 931432.1055
322 | 1940.862 | 2869.4332 | 2016.1767 | 2793.28 | 1940.862 | 1408.55 | 2885545.5464 | 698710.32 | 316942.7646 | 0 | 1147922.8299
323 | 2188.553 | 3734.0699 | 2273.4792 | 3634.9697 | 2188.553 | 1408 | 3266342.194 | 787879.08 | 357390.7049 | 0 | 1295623.376
324 | 2025.649 | 3271.8849 | 2104.2538 | 3185.0508 | 2025.649 | 1447.75 | 3113032.522 | 729233.64 | 330788.4817 | 0 | 1118664.6602
325 | 1943.684 | 2784.7966 | 2019.1082 | 2710.8896 | 1943.684 | 1307.8 | 2699551.4972 | 699726.24 | 317403.5972 | 0 | 1345418.0648
326 | 2335.268 | 2845.415 | 2425.8875 | 2769.8993 | 2335.268 | 1291.9 | 3202303.4378 | 840696.48 | 381349.2644 | 0 | 1653603.2708
327 | 2168.745 | 2059.5904 | 2059.5904 | 2004.93 | 2004.93 | 1268.65 | 2692824.4281 | 721774.794 | 327405.0663 | 300272.9255 | 1422116.6572
328 | 1973.613 | 2050.1986 | 2050.1986 | 1995.7874 | 1973.613 | 1411.95 | 2934524.8107 | 710500.68 | 322291.0029 | 0 | 1160583.1246
329 | 2279.797 | 1304.8001 | 1304.8001 | 1270.1714 | 1270.1714 | 1480.4 | 1976435.9474 | 457261.6937 | 207418.9849 | 1850643.7774 | 646020.2388
330 | 1609.172 | 175.5923 | 175.5923 | 170.9322 | 170.9322 | 1518.15 | 272714.8648 | 61535.5774 | 27913.2217 | 2636293.6275 | 80621.6964
331 | 2156.812 | 0 | 0 | 0 | 0 | 1529.15 | 0 | 0 | 0 | 7328847.176 | 0
332 | 2172.8 | 0 | 0 | 0 | 0 | 1492.25 | 0 | 0 | 0 | 7383174.4 | 0
333 | 2000 | 0 | 0 | 0 | 0 | 1473.65 | 0 | 0 | 0 | 6796000 | 0
334 | 1667.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1460.2 | 476512.0841 | 111351.8261 | 50510.4255 | 4614108.0863 | 165110.7852
335 | 2352 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1434.6 | 906912.502 | 215514.4963 | 97759.7701 | 5957878.6159 | 334716.8
336 | 2075.2 | 0 | 0 | 0 | 0 | 1401.15 | 0 | 0 | 0 | 3803841.6 | 0
337 | 1518.4 | 0 | 0 | 0 | 0 | 1381.7 | 0 | 0 | 0 | 1806896 | 0
338 | 1494.4 | 0 | 0 | 0 | 0 | 1336.2 | 0 | 0 | 0 | 1778336 | 0
339 | 1260 | 0 | 0 | 0 | 0 | 1333.75 | 0 | 0 | 0 | 1499400 | 0
340 | 1234.4 | 0 | 0 | 0 | 0 | 1340.9 | 0 | 0 | 0 | 1468936 | 0
341 | 1272 | 0 | 0 | 0 | 0 | 1344.1 | 0 | 0 | 0 | 1513680 | 0
342 | 1414.4 | 0 | 0 | 0 | 0 | 1240.75 | 0 | 0 | 0 | 1683136 | 0
343 | 1373.6 | 68.1643 | 68.1643 | 66.3552 | 66.3552 | 1408.8 | 98642.7791 | 23887.8889 | 10835.8118 | 2396179.6325 | 38399.6224
344 | 996.612 | 1034.0626 | 1034.0626 | 1006.6191 | 996.612 | 1485.15 | 1560303.9851 | 358780.32 | 162746.7396 | 0 | 507295.0911
345 | 1176.84 | 980.4759 | 980.4759 | 954.4546 | 954.4546 | 1596.25 | 1604262.687 | 343603.6441 | 155862.4308 | 407632.499 | 377209.4937
346 | 1297.88 | 1348.2439 | 1348.2439 | 1312.4622 | 1297.88 | 1551.6 | 2123719.864 | 467236.8 | 211943.804 | 0 | 581969.392
347 | 1357.844 | 1665.3598 | 1410.5348 | 1621.1621 | 1357.844 | 1501.35 | 2152294.7028 | 488823.84 | 221735.9252 | 0 | 677088.9106
348 | 1435.047 | 2728.6908 | 1490.7326 | 2656.2728 | 1435.047 | 1460.6 | 2211053.2883 | 516616.92 | 234343.1751 | 0 | 774064.3518
349 | 1435.033 | 2358.7225 | 1490.7191 | 2296.1233 | 1435.033 | 1428.4 | 2164400.8355 | 516611.88 | 234340.8889 | 0 | 820264.8628
350 | 1087.883 | 2596.1694 | 1130.098 | 2527.2685 | 1087.883 | 1501.35 | 1724430.6134 | 391637.88 | 177651.2939 | 0 | 542472.858
351 | 1211.392 | 1742.2761 | 1258.3998 | 1696.037 | 1211.392 | 1530.9 | 1953567.8507 | 436101.12 | 197820.3136 | 0 | 568263.9872
352 | 1440.601 | 486.7694 | 486.7694 | 473.8508 | 473.8508 | 1546.3 | 772087.4343 | 170586.2766 | 77379.8305 | 1772053.1747 | 210438.3099
353 | 1275.894 | 84.6532 | 84.6532 | 82.4066 | 82.4066 | 1555.05 | 134932.8596 | 29666.3713 | 13456.9957 | 2187662.4281 | 35891.0019
354 | 1244.187 | 0 | 0 | 0 | 0 | 1564.7 | 0 | 0 | 0 | 2280594.771 | 0
355 | 798.4 | 0 | 0 | 0 | 0 | 1647.9 | 0 | 0 | 0 | 2712963.2 | 0
356 | 1210.4 | 0 | 0 | 0 | 0 | 1533.7 | 0 | 0 | 0 | 4112939.2 | 0
357 | 1458.4 | 0 | 0 | 0 | 0 | 1491.35 | 0 | 0 | 0 | 4955643.2 | 0
358 | 1131.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1495.6 | 487503.4575 | 111351.8261 | 50510.4255 | 2792780.0863 | 154282.8456
359 | 1050.4 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1472.6 | 932194.2005 | 215514.4963 | 97759.7701 | 1535041.8159 | 312220.8
360 | 949.6 | 0 | 0 | 0 | 0 | 1428.85 | 0 | 0 | 0 | 1740616.8 | 0
361 | 1194.4 | 0 | 0 | 0 | 0 | 1257.1 | 0 | 0 | 0 | 1421336 | 0
362 | 1084.8 | 0 | 0 | 0 | 0 | 1378.4 | 0 | 0 | 0 | 1290912 | 0
363 | 1221.6 | 0 | 0 | 0 | 0 | 1309.2 | 0 | 0 | 0 | 1453704 | 0
364 | 1077.6 | 0 | 0 | 0 | 0 | 1247.6 | 0 | 0 | 0 | 1282344 | 0
365 | 1200.8 | 0 | 0 | 0 | 0 | 1241.3 | 0 | 0 | 0 | 1428952 | 0
366 | 1140 | 0 | 0 | 0 | 0 | 1250.25 | 0 | 0 | 0 | 1356600 | 0
367 | 1037.6 | 11.1474 | 11.1474 | 10.8516 | 10.8516 | 1373.05 | 15705.4679 | 3906.5643 | 1772.061 | 1882029.8768 | 6659.4629
368 | 866.892 | 562.5689 | 562.5689 | 547.6386 | 547.6386 | 1481.35 | 854309.0221 | 197149.8944 | 89429.3827 | 585191.4902 | 278024.9258
369 | 1066.826 | 1108.2239 | 1108.2239 | 1078.8123 | 1066.826 | 1514.75 | 1705546.3324 | 384057.36 | 174212.6858 | 0 | 517677.3165
370 | 1366.055 | 1900.1359 | 1419.0644 | 1849.7074 | 1366.055 | 1472.3 | 2124952.3381 | 491779.8 | 223076.7815 | 0 | 720867.2235
371 | 1574.613 | 3324.9335 | 1635.7155 | 3236.6916 | 1574.613 | 1139.65 | 1902521.2841 | 566860.68 | 257134.3029 | 0 | 1354718.2945
372 | 1515.751 | 2994.6424 | 1574.5693 | 2915.1663 | 1515.751 | 1241.85 | 1995243.5608 | 545670.36 | 247522.1383 | 0 | 1149166.6206
373 | 1570.042 | 1826.8701 | 1630.9671 | 1778.3859 | 1570.042 | 1292.05 | 2144444.8856 | 565215.12 | 256387.8586 | 0 | 1111511.2339
374 | 1584.014 | 3399.1717 | 1645.4813 | 3308.9595 | 1584.014 | 1361.2 | 2281670.7334 | 570245.04 | 258669.4862 | 0 | 1011868.1432
375 | 1443.606 | 2120.0156 | 1499.6248 | 2063.7515 | 1443.606 | 1530.9 | 2331612.0627 | 519698.16 | 235740.8598 | 0 | 677195.5746
376 | 1857.159 | 1943.2453 | 1929.2256 | 1891.6726 | 1857.159 | 1520.3 | 2978457.8115 | 668577.24 | 303274.0647 | 0 | 888240.3426
377 | 2051.354 | 631.8343 | 631.8343 | 615.0658 | 615.0658 | 1547.45 | 1003370.8138 | 221423.6708 | 100440.2373 | 2632716.3584 | 272459.9902
378 | 1864.668 | 70.5068 | 70.5068 | 68.6356 | 68.6356 | 1560.9 | 113039.0593 | 24708.8098 | 11208.1907 | 3292127.4207 | 29500.4944
379 | 1687.2 | 0 | 0 | 0 | 0 | 1572.9 | 0 | 0 | 0 | 5733105.6 | 0
380 | 1437.6 | 0 | 0 | 0 | 0 | 1529.9 | 0 | 0 | 0 | 4884964.8 | 0
381 | 1798.4 | 0 | 0 | 0 | 0 | 1549.75 | 0 | 0 | 0 | 6110963.2 | 0
382 | 1439.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1537.1 | 499840.045 | 111351.8261 | 50510.4255 | 3839364.0863 | 141589.0746
383 | 1318.4 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1446.6 | 913147.3217 | 215514.4963 | 97759.7701 | 2445705.8159 | 327612.8
384 | 1333.6 | 0 | 0 | 0 | 0 | 1224.85 | 0 | 0 | 0 | 2444488.8 | 0
385 | 1427.2 | 0 | 0 | 0 | 0 | 1242.4 | 0 | 0 | 0 | 1698368 | 0
386 | 1464.8 | 0 | 0 | 0 | 0 | 1219.95 | 0 | 0 | 0 | 1743112 | 0
387 | 1109.6 | 0 | 0 | 0 | 0 | 1218.65 | 0 | 0 | 0 | 1320424 | 0
388 | 1159.2 | 0 | 0 | 0 | 0 | 1228.1 | 0 | 0 | 0 | 1379448 | 0
389 | 1433.6 | 0 | 0 | 0 | 0 | 1241.3 | 0 | 0 | 0 | 1705984 | 0
390 | 1189.6 | 0 | 0 | 0 | 0 | 1250.25 | 0 | 0 | 0 | 1415624 | 0
391 | 1440 | 64.0787 | 64.0787 | 62.3781 | 62.3781 | 1381.7 | 90812.9093 | 22456.1008 | 10186.3369 | 2525181.0199 | 37752.1614
392 | 1042.494 | 988.3531 | 988.3531 | 962.1228 | 962.1228 | 1477.55 | 1497300.1648 | 346364.1955 | 157114.6476 | 147320.4735 | 492028.259
393 | 1260.412 | 1755.8314 | 1309.322 | 1709.2326 | 1260.412 | 1514.75 | 2009739.5836 | 453748.32 | 205825.2796 | 0 | 611614.923
394 | 1528.29 | 2692.9237 | 1587.5949 | 2621.4549 | 1528.29 | 1517.8 | 2443903.4241 | 550184.4 | 249569.757 | 0 | 736941.438
395 | 1634.053 | 3680.5839 | 1697.462 | 3582.9032 | 1634.053 | 1329.15 | 2295759.2626 | 588259.08 | 266840.8549 | 0 | 1096204.455
396 | 1747.764 | 4125.8842 | 1815.5855 | 4016.3855 | 1747.764 | 1300.7 | 2401984.4684 | 629195.04 | 285409.8612 | 0 | 1222211.3652
397 | 1461.828 | 2339.0289 | 1518.5539 | 2276.9523 | 1461.828 | 1317.55 | 2027887.2099 | 526258.08 | 238716.5124 | 0 | 997624.5186
398 | 1421.187 | 2718.4762 | 1476.3358 | 2646.3293 | 1421.187 | 1309.65 | 1960490.371 | 511627.32 | 232079.8371 | 0 | 981116.4454
399 | 1580.373 | 2700.2618 | 1641.699 | 2628.5983 | 1580.373 | 1327.35 | 2205803.8551 | 568934.28 | 258074.9109 | 0 | 1063037.8984
400 | 1462.36 | 361.1031 | 361.1031 | 351.5196 | 351.5196 | 1346.3 | 498193.4772 | 126547.0542 | 57403.1499 | 2036170.4622 | 224927.7108
401 | 1717.244 | 115.7249 | 115.7249 | 112.6537 | 112.6537 | 1540.55 | 182711.3 | 40555.314 | 18396.3411 | 2941214.1113 | 50664.011
402 | 1611.558 | 28.671 | 28.671 | 27.9101 | 27.9101 | 1564.7 | 46041.8079 | 10047.6353 | 4557.719 | 2902826.6043 | 11892.396
403 | 1616.357 | 0 | 0 | 0 | 0 | 1655.9 | 0 | 0 | 0 | 5492381.086 | 0
404 | 1480.8 | 0 | 0 | 0 | 0 | 1571.4 | 0 | 0 | 0 | 5031758.4 | 0
405 | 1845.6 | 0 | 0 | 0 | 0 | 1531.35 | 0 | 0 | 0 | 6271348.8 | 0
406 | 1497.6 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1580.1 | 513825.5163 | 111351.8261 | 50510.4255 | 4037807.2863 | 128436.4926
407 | 1532 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1468.8 | 925924.8673 | 215514.4963 | 97759.7701 | 3171518.6159 | 314470.4
408 | 1503.2 | 0 | 0 | 0 | 0 | 1303.2 | 0 | 0 | 0 | 2755365.6 | 0
409 | 1740.8 | 0 | 0 | 0 | 0 | 1395.35 | 0 | 0 | 0 | 2071552 | 0
410 | 1453.6 | 0 | 0 | 0 | 0 | 1318.8 | 0 | 0 | 0 | 1729784 | 0
411 | 1256 | 0 | 0 | 0 | 0 | 1343.4 | 0 | 0 | 0 | 1494640 | 0
412 | 1274.4 | 0 | 0 | 0 | 0 | 1383.1 | 0 | 0 | 0 | 1516536 | 0
413 | 1436.8 | 0 | 0 | 0 | 0 | 1402.3 | 0 | 0 | 0 | 1709792 | 0
414 | 1512.8 | 0 | 0 | 0 | 0 | 1433.15 | 0 | 0 | 0 | 1800232 | 0
415 | 1361.6 | 58.2292 | 58.2292 | 56.6838 | 56.6838 | 1456.25 | 86710.1462 | 20406.1648 | 9256.4631 | 2391911.4108 | 30169.9688
416 | 1307.476 | 1234.9612 | 1234.9612 | 1202.186 | 1202.186 | 1485.15 | 1877177.0669 | 432786.9646 | 196316.9759 | 192996.5464 | 605852.8266
417 | 1117.404 | 1843.1222 | 1160.7646 | 1794.2067 | 1117.404 | 1549.75 | 1824362.3284 | 402265.44 | 182472.0732 | 0 | 503111.151
418 | 1558.331 | 2829.0227 | 1618.8016 | 2753.942 | 1558.331 | 1521.6 | 2497719.5055 | 560999.16 | 254475.4523 | 0 | 745505.5504
419 | 1635.582 | 3867.6612 | 1699.0503 | 3765.0156 | 1635.582 | 1475.25 | 2552330.3101 | 588809.52 | 267090.5406 | 0 | 858271.6545
420 | 1614.236 | 4168.4295 | 1676.876 | 4057.8016 | 1614.236 | 1433.5 | 2443183.6025 | 581124.96 | 263604.7388 | 0 | 914464.694
421 | 1599.883 | 3747.7665 | 1661.9661 | 3648.3028 | 1599.883 | 1385.75 | 2331679.2063 | 575957.88 | 261260.8939 | 0 | 982728.1327
422 | 1534.321 | 3544.0767 | 1593.8599 | 3450.0188 | 1534.321 | 1484.15 | 2402907.8905 | 552355.56 | 250554.6193 | 0 | 791479.4879
423 | 1869.297 | 3096.8899 | 1941.8346 | 3014.7001 | 1869.297 | 1512.5 | 2979139.7478 | 672946.92 | 305256.2001 | 0 | 911282.2875
424 | 1731.41 | 2484.099 | 1798.5969 | 2418.1724 | 1731.41 | 1538.7 | 2803887.0877 | 623307.6 | 282739.253 | 0 | 798699.433
425 | 1852.086 | 1323.1807 | 1323.1807 | 1288.0642 | 1288.0642 | 1555.05 | 2105109.2833 | 463703.1016 | 210340.8791 | 1033852.0124 | 561000.5241
426 | 1824.781 | 125.3941 | 125.3941 | 122.0662 | 122.0662 | 1604.7 | 206241.1004 | 43943.8426 | 19933.4153 | 3121076.1742 | 47232.4205
427 | 1772.851 | 0 | 0 | 0 | 0 | 1655.9 | 0 | 0 | 0 | 6024147.698 | 0
428 | 1725.6 | 0 | 0 | 0 | 0 | 1576.2 | 0 | 0 | 0 | 5863588.8 | 0
429 | 1548.8 | 0 | 0 | 0 | 0 | 1513.55 | 0 | 0 | 0 | 5262822.4 | 0
430 | 1660 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1578.6 | 512313.1745 | 111351.8261 | 50510.4255 | 4589642.4863 | 128895.3036
431 | 1914.4 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1554.1 | 979386.7694 | 215514.4963 | 97759.7701 | 4470913.8159 | 263972.8
432 | 1842.4 | 0 | 0 | 0 | 0 | 1454.85 | 0 | 0 | 0 | 3377119.2 | 0
433 | 1708 | 0 | 0 | 0 | 0 | 1481.9 | 0 | 0 | 0 | 3130764 | 0
434 | 1356.8 | 0 | 0 | 0 | 0 | 1431.1 | 0 | 0 | 0 | 2487014.4 | 0
435 | 1073.6 | 0 | 0 | 0 | 0 | 1421.05 | 0 | 0 | 0 | 1967908.8 | 0
436 | 1288.8 | 0 | 0 | 0 | 0 | 1424.3 | 0 | 0 | 0 | 2362370.4 | 0
437 | 1396.8 | 0 | 0 | 0 | 0 | 1431.3 | 0 | 0 | 0 | 2560334.4 | 0
438 | 1372 | 0 | 0 | 0 | 0 | 1440.75 | 0 | 0 | 0 | 2514876 | 0
439 | 1415.2 | 90.6856 | 90.6856 | 88.2788 | 88.2788 | 1460.05 | 135527.9521 | 31780.3792 | 14415.9331 | 2432246.5025 | 46657.6194
440 | 1131.076 | 1174.9671 | 1174.9671 | 1143.7841 | 1131.076 | 1485.15 | 1765848.2987 | 407187.36 | 184704.7108 | 0 | 582334.4786
441 | 1241.663 | 1863.2542 | 1289.8454 | 1813.8045 | 1241.663 | 1514.75 | 1978526.1756 | 446998.68 | 202763.5679 | 0 | 602516.9708
442 | 856.555 | 2981.4288 | 889.7934 | 2902.3033 | 856.555 | 1521.6 | 1371944.2753 | 308359.8 | 139875.4315 | 0 | 409775.912
443 | 1284.095 | 3863.078 | 1333.924 | 3760.554 | 1284.095 | 1493.65 | 2027610.4021 | 462274.2 | 209692.7135 | 0 | 650201.5032
444 | 1493.401 | 4103.0263 | 1551.352 | 3994.1342 | 1493.401 | 1485.85 | 2349097.1363 | 537624.36 | 243872.3833 | 0 | 767832.1242
445 | 1383.033 | 4017.1078 | 1436.7012 | 3910.496 | 1383.033 | 1479.75 | 2163126.3183 | 497891.88 | 225849.2889 | 0 | 719522.9183
446 | 1395.108 | 3093.3891 | 1449.2448 | 3011.2923 | 1395.108 | 1515.85 | 2237539.9152 | 502238.88 | 227821.1364 | 0 | 675441.5382
447 | 1147.015 | 2324.7339 | 1191.5246 | 2263.0367 | 1147.015 | 1538.5 | 1861355.8974 | 412925.4 | 187307.5495 | 0 | 529347.4225
448 | 1254.993 | 1492.4747 | 1303.6927 | 1452.8652 | 1254.993 | 1542.5 | 2040106.5441 | 451797.48 | 204940.3569 | 0 | 574159.2975
449 | 1593.632 | 454.0003 | 454.0003 | 441.9513 | 441.9513 | 1595.05 | 741198.3405 | 159102.4847 | 72170.6549 | 2111030.6379 | 175182.1799
450 | 1540.045 | 62.0914 | 62.0914 | 60.4436 | 60.4436 | 1564.7 | 99627.0382 | 21759.6832 | 9870.4341 | 2712109.4312 | 25754.5245
451 | 1594.407 | 0 | 0 | 0 | 0 | 1657.4 | 0 | 0 | 0 | 2922548.031 | 0
452 | 1601.6 | 0 | 0 | 0 | 0 | 1575.2 | 0 | 0 | 0 | 2935732.8 | 0
453 | 1628.8 | 0 | 0 | 0 | 0 | 1555.05 | 0 | 0 | 0 | 2985590.4 | 0
454 | 1475.2 | 0 | 0 | 0 | 0 | 1581.6 | 0 | 0 | 0 | 2704041.6 | 0
455 | 1756 | 0 | 0 | 0 | 0 | 1558.85 | 0 | 0 | 0 | 3218748 | 0
456 | 1347.2 | 144.0272 | 144.0272 | 140.2048 | 140.2048 | 1571.35 | 232002.4503 | 50473.7134 | 22895.4372 | 2212422.2757 | 54387.9693
457 | 1464 | 0 | 0 | 0 | 0 | 1426.35 | 0 | 0 | 0 | 1742160 | 0
458 | 1484 | 0 | 0 | 0 | 0 | 1516.95 | 0 | 0 | 0 | 1765960 | 0
459 | 1376.8 | 0 | 0 | 0 | 0 | 1510.2 | 0 | 0 | 0 | 1638392 | 0
460 | 1298.4 | 0 | 0 | 0 | 0 | 1497 | 0 | 0 | 0 | 1545096 | 0
461 | 1472 | 0 | 0 | 0 | 0 | 1510.75 | 0 | 0 | 0 | 1751680 | 0
462 | 1540.8 | 0 | 0 | 0 | 0 | 1520.7 | 0 | 0 | 0 | 1833552 | 0
463 | 1121.6 | 689.7612 | 689.7612 | 671.4553 | 671.4553 | 1485.95 | 1053067.9641 | 241723.8985 | 109648.6462 | 825115.2832 | 340950.8592
464 | 1325.723 | 1377.1673 | 1377.1673 | 1340.6181 | 1325.723 | 1468.7 | 2052210.8041 | 477260.28 | 216490.5659 | 0 | 704356.6299
465 | 1431.814 | 1789.9437 | 1487.3752 | 1742.4396 | 1431.814 | 1498.2 | 2260802.4271 | 515453.04 | 233815.2262 | 0 | 718484.2652
466 | 1750.511 | 2771.5685 | 1818.4402 | 2698.0125 | 1750.511 | 1340.6 | 2474444.0551 | 630183.96 | 285858.4463 | 0 | 1154286.9534
467 | 1780.377 | 2681.1592 | 1849.4641 | 2610.0027 | 1780.377 | 1302.15 | 2457821.1447 | 640935.72 | 290735.5641 | 0 | 1242436.0895
468 | 1557.127 | 2436.396 | 1617.5509 | 2371.7354 | 1557.127 | 1254.95 | 2075028.5559 | 560565.72 | 254278.8391 | 0 | 1160137.4714
469 | 1473.887 | 2427.2182 | 1531.0808 | 2362.8011 | 1473.887 | 302.25 | 472103.6562 | 530599.32 | 240685.7471 | 0 | 2502291.6543
470 | 1373.544 | 3187.1911 | 1426.844 | 3102.6048 | 1373.544 | 812.05 | 1181734.8303 | 494475.84 | 224299.7352 | 0 | 1631701.5948
471 | 1430.954 | 1884.744 | 1486.4818 | 1834.7239 | 1430.954 | 1348.45 | 2036998.5716 | 515143.44 | 233674.7882 | 0 | 932338.0787
472 | 1796.545 | 1758.871 | 1758.871 | 1712.1915 | 1712.1915 | 1344.1 | 2423180.501 | 616388.9334 | 279600.869 | 154619.999 | 1099270.6907
473 | 1678.349 | 1131.088 | 1131.088 | 1101.0695 | 1101.0695 | 1366.25 | 1580948.5435 | 396385.0372 | 179804.6572 | 1058153.2358 | 683041.8075
474 | 1629.66 | 152.108 | 152.108 | 148.0712 | 148.0712 | 1364.65 | 212450.0002 | 53305.6176 | 24180.0204 | 2715752.3436 | 92086.9936
475 | 1404.8 | 0 | 0 | 0 | 0 | 1455.9 | 0 | 0 | 0 | 4773510.4 | 0
476 | 1388.8 | 0 | 0 | 0 | 0 | 1295.95 | 0 | 0 | 0 | 4719142.4 | 0
477 | 1344.8 | 0 | 0 | 0 | 0 | 811.55 | 0 | 0 | 0 | 4569630.4 | 0
478 | 1680.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1517.45 | 493068.2978 | 111351.8261 | 50510.4255 | 4660320.8863 | 147599.4987
479 | 1447.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1454.45 | 915705.8818 | 215514.4963 | 97759.7701 | 2883368.2159 | 322965.6
480 | 1506.4 | 0 | 0 | 0 | 0 | 1361.3 | 0 | 0 | 0 | 2761231.2 | 0
481 | 1360.8 | 0 | 0 | 0 | 0 | 784.65 | 0 | 0 | 0 | 1619352 | 0
482 | 1408 | 0 | 0 | 0 | 0 | 1347.15 | 0 | 0 | 0 | 1675520 | 0
483 | 1103.2 | 0 | 0 | 0 | 0 | 1317.35 | 0 | 0 | 0 | 1312808 | 0
484 | 1368 | 0 | 0 | 0 | 0 | 1271.8 | 0 | 0 | 0 | 1627920 | 0
485 | 1242.4 | 0 | 0 | 0 | 0 | 1218.5 | 0 | 0 | 0 | 1478456 | 0
486 | 1268.8 | 0 | 0 | 0 | 0 | 1215.6 | 0 | 0 | 0 | 1509872 | 0
487 | 1385.6 | 6.0209 | 6.0209 | 5.8611 | 5.8611 | 1239.55 | 7637.1656 | 2110.0034 | 957.121 | 2529061.366 | 4362.7016
488 | 1391.679 | 506.57 | 506.57 | 493.1259 | 493.1259 | 1275.9 | 662522.2265 | 177525.3337 | 80527.4639 | 1647047.7829 | 349518.7254
489 | 1424.117 | 1479.3795 | 1479.3795 | 1440.1176 | 1424.117 | 1251.5 | 1881179.7641 | 512682.12 | 232558.3061 | 0 | 1065951.5745
490 | 1612.774 | 2440.2001 | 1675.3573 | 2375.4386 | 1612.774 | 276.75 | 472689.0306 | 580598.64 | 263365.9942 | 0 | 2779212.7955
491 | 1401.019 | 3563.9625 | 1455.3852 | 3469.3769 | 1401.019 | 1219.55 | 1819791.427 | 504366.84 | 228786.4027 | 0 | 1093425.2785
492 | 1755.972 | 4039.2448 | 1824.1121 | 3932.0454 | 1755.972 | 1264.25 | 2364569.8791 | 632149.92 | 286750.2276 | 0 | 1291956.399
493 | 1074.33 | 4091.3107 | 1116.0191 | 3982.7295 | 1074.33 | 1170.55 | 1337262.2294 | 386758.8 | 175438.089 | 0 | 891103.0185
494 | 1159.81 | 3835.6307 | 1204.8161 | 3733.8352 | 1159.81 | 280.9 | 346319.5844 | 417531.6 | 189396.973 | 0 | 1993829.371
495 | 1567.968 | 2358.0245 | 1628.8126 | 2295.4438 | 1567.968 | 295.65 | 492511.37 | 564468.48 | 256049.1744 | 0 | 2672366.2608
496 | 1342.539 | 2051.442 | 1394.6359 | 1996.9979 | 1342.539 | 308.9 | 438157.319 | 483314.04 | 219236.6187 | 0 | 2270367.7029
497 | 1562.161 | 1276.9268 | 1276.9268 | 1243.0379 | 1243.0379 | 719.4 | 939856.6376 | 447493.6447 | 202988.0894 | 584952.6386 | 1558162.3664
498 | 1560.409 | 190.6788 | 190.6788 | 185.6183 | 185.6183 | 1415.85 | 275622.1192 | 66822.5994 | 30311.4736 | 2519991.2948 | 106135.3818
499 | 918.411 | 0 | 0 | 0 | 0 | 1516.55 | 0 | 0 | 0 | 3120760.578 | 0
500 | 1270.4 | 0 | 0 | 0 | 0 | 1393.45 | 0 | 0 | 0 | 4316819.2 | 0
501 | 1204 | 0 | 0 | 0 | 0 | 1183.65 | 0 | 0 | 0 | 4091192 | 0
502 | 1369.6 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1384.4 | 449995.1228 | 111351.8261 | 50510.4255 | 3602863.2863 | 188296.0344
503 | 1345.6 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1363.65 | 857807.3375 | 215514.4963 | 97759.7701 | 2538131.4159 | 376719.2
504 | 1280 | 0 | 0 | 0 | 0 | 1183.65 | 0 | 0 | 0 | 2346240 | 0
505 | 2330.4 | 0 | 0 | 0 | 0 | 741.4 | 0 | 0 | 0 | 2773176 | 0
506 | 2057.6 | 0 | 0 | 0 | 0 | 1217.1 | 0 | 0 | 0 | 2448544 | 0
507 | 2428 | 0 | 0 | 0 | 0 | 1253.2 | 0 | 0 | 0 | 2889320 | 0
508 | 2208.8 | 0 | 0 | 0 | 0 | 1243.15 | 0 | 0 | 0 | 2628472 | 0
509 | 2004 | 0 | 0 | 0 | 0 | 1217.3 | 0 | 0 | 0 | 2384760 | 0
510 | 2379.2 | 0 | 0 | 0 | 0 | 1250.75 | 0 | 0 | 0 | 2831248 | 0
511 | 2040.8 | 74.2143 | 74.2143 | 72.2447 | 72.2447 | 1331.9 | 101418.5502 | 26008.0855 | 11797.5566 | 3608361.8978 | 47246.0277
512 | 1723.786 | 1061.433 | 1061.433 | 1033.2632 | 1033.2632 | 1477.55 | 1610110.2816 | 371974.7441 | 168731.877 | 1265728.3325 | 528409.0647
513 | 1825.298 | 1896.1282 | 1896.1282 | 1845.806 | 1825.298 | 1515.95 | 2920859.657 | 657107.28 | 298071.1634 | 0 | 883535.4969
514 | 2095.805 | 2627.1538 | 2177.1322 | 2557.4306 | 2095.805 | 1512.8 | 3348900.6936 | 754489.8 | 342244.9565 | 0 | 1021076.196
515 | 2297.304 | 3623.5816 | 2386.4513 | 3527.4137 | 2297.304 | 1309.65 | 3191870.6815 | 827029.44 | 375149.7432 | 0 | 1585943.8164
516 | 2286.452 | 3998.0416 | 2375.1772 | 3891.9358 | 2286.452 | 1311.85 | 3183997.4921 | 823122.72 | 373377.6116 | 0 | 1573421.9438
517 | 2261.298 | 3949.1264 | 2349.0471 | 3844.3187 | 2261.298 | 1369.9 | 3279771.904 | 814067.28 | 369269.9634 | 0 | 1424843.8698
518 | 2390.381 | 3180.4898 | 2483.1391 | 3096.0813 | 2390.381 | 1331.15 | 3371597.3869 | 860537.16 | 390349.2173 | 0 | 1598806.3318
519 | 2181.431 | 2266.0809 | 2266.0809 | 2205.9403 | 2181.431 | 1371.5 | 3156126.1609 | 785315.16 | 356227.6823 | 0 | 1371029.3835
520 | 1853.049 | 2289.0873 | 1924.9561 | 2228.3362 | 1853.049 | 816.8 | 1592348.1189 | 667097.64 | 302602.9017 | 0 | 2192527.5768
521 | 2387.844 | 1038.0256 | 1038.0256 | 1010.477 | 1010.477 | 1456.25 | 1547318.4864 | 363771.7236 | 165010.8957 | 2524713.6926 | 537824.2125
522 | 2256.255 | 170.9322 | 170.9322 | 166.3958 | 166.3958 | 1557.1 | 272732.6367 | 59902.4727 | 27172.4272 | 3830711.9917 | 72137.7804
523 | 2414.4 | 0 | 0 | 0 | 0 | 1607.9 | 0 | 0 | 0 | 8204131.2 | 0
524 | 1896.8 | 0 | 0 | 0 | 0 | 1434.9 | 0 | 0 | 0 | 6445326.4 | 0
525 | 2389.6 | 0 | 0 | 0 | 0 | 1364.25 | 0 | 0 | 0 | 8119860.8 | 0
526 | 2215.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1496.8 | 487399.3416 | 111351.8261 | 50510.4255 | 6476212.0863 | 153915.7968
527 | 2295.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1347.6 | 850569.2137 | 215514.4963 | 97759.7701 | 5764872.2159 | 386220.8
528 | 1956 | 0 | 0 | 0 | 0 | 1208.85 | 0 | 0 | 0 | 3585348 | 0
529 | 1812 | 0 | 0 | 0 | 0 | 1232.9 | 0 | 0 | 0 | 2156280 | 0
530 | 1850.4 | 0 | 0 | 0 | 0 | 1218.8 | 0 | 0 | 0 | 2201976 | 0
531 | 1248.8 | 0 | 0 | 0 | 0 | 1216.35 | 0 | 0 | 0 | 1486072 | 0
532 | 1303.2 | 0 | 0 | 0 | 0 | 1210.95 | 0 | 0 | 0 | 1550808 | 0
533 | 1569.6 | 0 | 0 | 0 | 0 | 1214.15 | 0 | 0 | 0 | 1867824 | 0
534 | 1165.6 | 0 | 0 | 0 | 0 | 1228.45 | 0 | 0 | 0 | 1387064 | 0
535 | 1127.2 | 51.4759 | 51.4759 | 50.1097 | 50.1097 | 1248.9 | 65933.5233 | 18039.5099 | 8182.9221 | 1974306.429 | 36840.7039
536 | 845.369 | 878.1733 | 878.1733 | 854.8671 | 845.369 | 1441.6 | 1283909.4375 | 304332.84 | 138048.7577 | 0 | 472054.0496
537 | 1178.36 | 1319.3724 | 1224.086 | 1284.357 | 1178.36 | 1515.95 | 1883170.352 | 424209.6 | 192426.188 | 0 | 570385.158
538 | 1572.128 | 2581.0974 | 1633.133 | 2512.5965 | 1572.128 | 1514 | 2509150.6758 | 565966.08 | 256728.5024 | 0 | 764054.208
539 | 1408.437 | 3830.847 | 1463.091 | 3729.1784 | 1408.437 | 1394.15 | 2076134.6913 | 507037.32 | 229997.7621 | 0 | 853301.5565
540 | 1438.896 | 4111.2173 | 1494.732 | 4002.1078 | 1438.896 | 1344.85 | 2041520.4845 | 518002.56 | 234971.7168 | 0 | 942692.7144
541 | 1516.32 | 4108.8582 | 1575.1604 | 3999.8113 | 1516.32 | 1367.05 | 2180370.7659 | 545875.2 | 247615.056 | 0 | 959754.744
542 | 1377.594 | 2355.3454 | 1431.0512 | 2292.8358 | 1377.594 | 1411.65 | 2055237.1058 | 495933.84 | 224961.1002 | 0 | 810507.4299
543 | 1550.943 | 2707.7422 | 1611.127 | 2635.8802 | 1550.943 | 1421.3 | 2330380.3085 | 558339.48 | 253268.9919 | 0 | 897530.7141
544 | 1543.534 | 2340.7315 | 1603.4304 | 2278.6097 | 1543.534 | 1338.3 | 2178171.8223 | 555672.24 | 252059.1022 | 0 | 1021356.4478
545 | 1201.14 | 1275.1474 | 1247.7499 | 1241.3057 | 1201.14 | 1437.85 | 1821009.0837 | 432410.4 | 196146.162 | 0 | 675220.851
546 | 1293.095 | 207.7474 | 207.7474 | 202.2339 | 202.2339 | 1557.1 | 331483.6652 | 72804.2189 | 33024.8026 | 1999548.3207 | 87674.7124
547 | 1413.61 | 0 | 0 | 0 | 0 | 1640.4 | 0 | 0 | 0 | 4803446.78 | 0
548 | 1265.6 | 0 | 0 | 0 | 0 | 1498.95 | 0 | 0 | 0 | 4300508.8 | 0
549 | 1180.8 | 0 | 0 | 0 | 0 | 1385.2 | 0 | 0 | 0 | 4012358.4 | 0
550 | 1695.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1555.6 | 506456.8854 | 111351.8261 | 50510.4255 | 4709252.0863 | 135930.4056
551 | 1346.4 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1465 | 925027.6619 | 215514.4963 | 97759.7701 | 2540849.8159 | 316720
552 | 1211.2 | 0 | 0 | 0 | 0 | 1337.65 | 0 | 0 | 0 | 2220129.6 | 0
553 | 1408 | 0 | 0 | 0 | 0 | 1404.6 | 0 | 0 | 0 | 1675520 | 0
554 | 1139.2 | 0 | 0 | 0 | 0 | 1290.6 | 0 | 0 | 0 | 1355648 | 0
555 | 1446.4 | 0 | 0 | 0 | 0 | 1218.65 | 0 | 0 | 0 | 1721216 | 0
556 | 1142.4 | 0 | 0 | 0 | 0 | 1215.8 | 0 | 0 | 0 | 1359456 | 0
557 | 880 | 0 | 0 | 0 | 0 | 1239.65 | 0 | 0 | 0 | 1047200 | 0
558 | 1145.6 | 0 | 0 | 0 | 0 | 1296.75 | 0 | 0 | 0 | 1363264 | 0
559 | 943.2 | 24.3122 | 24.3122 | 23.667 | 23.667 | 1433.75 | 35777.2544 | 8520.1035 | 3864.8136 | 1685504.073 | 13118.3137
560 | 1274.438 | 1050.6637 | 1050.6637 | 1022.7797 | 1022.7797 | 1477.55 | 1591337.6224 | 368200.6921 | 167019.9251 | 461289.6632 | 523047.6828
561 | 1429.443 | 1915.4157 | 1484.9122 | 1864.5816 | 1429.443 | 1507.15 | 2269500.7563 | 514599.48 | 233428.0419 | 0 | 704500.9825
562 | 1547.522 | 2979.4395 | 1607.5732 | 2900.3668 | 1547.522 | 1517.8 | 2475739.9233 | 557107.92 | 252710.3426 | 0 | 746215.1084
563 | 1405.725 | 3907.1607 | 1460.2738 | 3803.4668 | 1405.725 | 1475.25 | 2189766.6917 | 506061 | 229554.8925 | 0 | 737654.1938
564 | 1431.852 | 4184.1487 | 1487.4147 | 4073.1036 | 1431.852 | 1504.25 | 2275040.7307 | 515466.72 | 233821.4316 | 0 | 709840.629
565 | 1367.56 | 4183.2854 | 1420.6278 | 4072.2633 | 1367.56 | 1490.45 | 2149154.1246 | 492321.6 | 223322.548 | 0 | 696840.198
566 | 1673.787 | 3920.071 | 1738.7379 | 3816.0344 | 1673.787 | 1510.85 | 2668408.4403 | 602563.32 | 273329.4171 | 0 | 818732.9111
567 | 1642.84 | 3397.7942 | 1706.59 | 3307.6186 | 1642.84 | 1530.9 | 2652603.9674 | 591422.4 | 268275.772 | 0 | 770656.244
568 | 1902.457 | 2580.3785 | 1976.2814 | 2511.8967 | 1902.457 | 1538.7 | 3085689.9157 | 684884.52 | 310671.2281 | 0 | 877603.4141
569 | 1899.267 | 1434.606 | 1434.606 | 1396.5323 | 1396.5323 | 1555.05 | 2287777.246 | 502751.6344 | 228053.7275 | 921512.6726 | 608242.6455
570 | 1621.58 | 229.0606 | 229.0606 | 222.9815 | 222.9815 | 1564.7 | 367483.238 | 80273.3251 | 36412.8722 | 2563631.1262 | 95010.7545
571 | 1806.403 | 0 | 0 | 0 | 0 | 1612.9 | 0 | 0 | 0 | 6138157.394 | 0
572 | 1360.8 | 0 | 0 | 0 | 0 | 1571.2 | 0 | 0 | 0 | 4623998.4 | 0
573 | 1477.6 | 0 | 0 | 0 | 0 | 1555.05 | 0 | 0 | 0 | 5020884.8 | 0
574 | 1830.4 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1578.6 | 514539.8638 | 111351.8261 | 50510.4255 | 5168661.6863 | 128895.3036
575 | 1500.8 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1554.1 | 981022.4214 | 215514.4963 | 97759.7701 | 3065501.0159 | 263972.8
576 | 1522.4 | 0 | 0 | 0 | 0 | 1484.85 | 0 | 0 | 0 | 2790559.2 | 0
577 | 1083.2 | 0 | 0 | 0 | 0 | 1416.7 | 0 | 0 | 0 | 1289008 | 0
578 | 1204 | 0 | 0 | 0 | 0 | 1431.1 | 0 | 0 | 0 | 1432760 | 0
579 | 1488.8 | 0 | 0 | 0 | 0 | 1428.65 | 0 | 0 | 0 | 1771672 | 0
580 | 1076 | 0 | 0 | 0 | 0 | 1424.3 | 0 | 0 | 0 | 1280440 | 0
581 | 1073.6 | 0 | 0 | 0 | 0 | 1423.7 | 0 | 0 | 0 | 1277584 | 0
582 | 912 | 0 | 0 | 0 | 0 | 1433.15 | 0 | 0 | 0 | 1085280 | 0
583 | 964.8 | 57.7503 | 57.7503 | 56.2176 | 56.2176 | 1460.05 | 86483.2 | 20238.3402 | 9180.336 | 1665431.5179 | 29712.3686
584 | 1236.892 | 1186.8687 | 1186.8687 | 1155.3699 | 1155.3699 | 1490.15 | 1813080.2119 | 415933.1486 | 188671.8977 | 149430.0879 | 576604.6605
585 | 902.102 | 1788.3886 | 937.1078 | 1740.9257 | 902.102 | 1514.75 | 1440490.305 | 324756.72 | 147313.2566 | 0 | 437744.9955
586 | 1643.977 | 2819.9685 | 1707.7711 | 2745.128 | 1643.977 | 1514 | 2623443.8447 | 591831.72 | 268461.4441 | 0 | 798972.822
587 | 1404.929 | 3771.819 | 1459.4469 | 3671.717 | 1404.929 | 1402.15 | 2083457.916 | 505774.44 | 229424.9057 | 0 | 839936.8026
588 | 1257.977 | 4051.0134 | 1306.7925 | 3943.5017 | 1257.977 | 1466.85 | 1949916.3795 | 452871.72 | 205427.6441 | 0 | 670690.4375
589 | 1143.986 | 4021.3191 | 1188.3781 | 3914.5955 | 1143.986 | 1453.65 | 1751689.567 | 411834.96 | 186812.9138 | 0 | 625016.7511
590 | 1063.922 | 3718.9896 | 1105.2072 | 3620.2896 | 1063.922 | 1474.65 | 1657838.25 | 383011.92 | 173738.4626 | 0 | 558931.4227
591 | 1565.032 | 3210.6692 | 1625.7627 | 3125.4597 | 1565.032 | 1493.5 | 2467102.843 | 563411.52 | 255569.7256 | 0 | 792688.708
592 | 1529.519 | 2420.5179 | 1588.8716 | 2356.2787 | 1529.519 | 1493.3 | 2409109.1577 | 550626.84 | 249770.4527 | 0 | 775007.2773
593 | 1548.768 | 1208.0406 | 1208.0406 | 1175.9798 | 1175.9798 | 1532.85 | 1899071.5495 | 423352.7448 | 192037.5089 | 683320.6853 | 537738.2336
594 | 954.794 | 180.9452 | 180.9452 | 176.1431 | 176.1431 | 1564.7 | 290330.8224 | 63411.5001 | 28764.161 | 1427267.1808 | 75053.1201
595 | 979.933 | 0 | 0 | 0 | 0 | 1602.9 | 0 | 0 | 0 | 3329812.334 | 0
596 | 1248.8 | 0 | 0 | 0 | 0 | 1563.7 | 0 | 0 | 0 | 4243422.4 | 0
597 | 1226.4 | 0 | 0 | 0 | 0 | 1555.05 | 0 | 0 | 0 | 4167307.2 | 0
598 | 1332 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1577.1 | 513731.8821 | 111351.8261 | 50510.4255 | 3475098.4863 | 129354.1146
599 | 1236.8 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1532.6 | 966503.424 | 215514.4963 | 97759.7701 | 2168429.0159 | 276700.8
600 | 1285.6 | 0 | 0 | 0 | 0 | 1451.05 | 0 | 0 | 0 | 2356504.8 | 0
601 | 1532.8 | 0 | 0 | 0 | 0 | 1250.4 | 0 | 0 | 0 | 2809622.4 | 0
602 | 1344.8 | 0 | 0 | 0 | 0 | 1405.1 | 0 | 0 | 0 | 2465018.4 | 0
603 | 1204.8 | 0 | 0 | 0 | 0 | 1402.35 | 0 | 0 | 0 | 2208398.4 | 0
604 | 1120.8 | 0 | 0 | 0 | 0 | 1228.1 | 0 | 0 | 0 | 2054426.4 | 0
605 | 1085.6 | 0 | 0 | 0 | 0 | 1313.8 | 0 | 0 | 0 | 1989904.8 | 0
606 | 1070.4 | 0 | 0 | 0 | 0 | 1414.75 | 0 | 0 | 0 | 1962043.2 | 0
607 | 1341.6 | 38.3111 | 38.3111 | 37.2944 | 37.2944 | 1398.1 | 54783.2847 | 13425.9706 | 6090.1695 | 2390792.2328 | 21972.3595
608 | 915.255 | 927.1021 | 927.1021 | 902.4973 | 902.4973 | 1481.35 | 1405628.4347 | 324899.0244 | 147377.8075 | 23384.8822 | 458179.0405
609 | 1043.557 | 1084.052 | 1084.052 | 1055.2818 | 1043.557 | 1544.75 | 1697171.8685 | 375680.52 | 170412.8581 | 0 | 475079.3243
610 | 1135.797 | 1753.7206 | 1179.8713 | 1707.1778 | 1135.797 | 1512.8 | 1809385.424 | 408886.92 | 185475.6501 | 0 | 553360.2984
611 | 1052.302 | 3201.1277 | 1093.1363 | 3116.1715 | 1052.302 | 1362.15 | 1514020.7512 | 378828.72 | 171840.9166 | 0 | 671210.8307
612 | 1010.911 | 3421.8166 | 1050.1391 | 3331.0035 | 1010.911 | 1417.35 | 1511232.6951 | 363927.96 | 165081.7663 | 0 | 589007.2942
613 | 907.915 | 3486.9299 | 943.1464 | 3394.3887 | 907.915 | 1453.05 | 1386879.5213 | 326849.4 | 148262.5195 | 0 | 496584.1092
614 | 1041.693 | 3013.0999 | 1082.1156 | 2933.1339 | 1041.693 | 1474.95 | 1620138.5612 | 375009.48 | 170108.4669 | 0 | 546940.9097
615 | 1029.977 | 2376.2565 | 1069.945 | 2313.192 | 1029.977 | 1493.5 | 1619986.1279 | 370791.72 | 168195.2441 | 0 | 521683.3505
616 | 1033.486 | 1356.5294 | 1073.5902 | 1320.5279 | 1033.486 | 1501.3 | 1633553.9731 | 372054.96 | 168768.2638 | 0 | 515399.4682
617 | 1376.376 | 1210.3478 | 1210.3478 | 1178.2258 | 1178.2258 | 1551.25 | 1923701.6607 | 424161.2882 | 192404.2732 | 363209.3158 | 517544.2725
618 | 1168.446 | 223.8032 | 223.8032 | 217.8636 | 217.8636 | 1564.7 | 359005.7151 | 78430.8946 | 35577.1253 | 1742417.5462 | 92829.9015
619 | 1198.4 | 0 | 0 | 0 | 0 | 1572.9 | 0 | 0 | 0 | 2196667.2 | 0
620 | 1109.6 | 0 | 0 | 0 | 0 | 1533.7 | 0 | 0 | 0 | 2033896.8 | 0
621 | 1098.4 | 0 | 0 | 0 | 0 | 1539.75 | 0 | 0 | 0 | 2013367.2 | 0
622 | 1179.2 | 0 | 0 | 0 | 0 | 1495.6 | 0 | 0 | 0 | 2161473.6 | 0
623 | 1169.6 | 132.245 | 132.245 | 128.7353 | 128.7353 | 1472.6 | 199545.3446 | 46344.7178 | 21022.4789 | 1907904.9451 | 66807.3402
624 | 497.6 | 516.9092 | 516.9092 | 503.1908 | 497.6 | 1428.85 | 747182.3209 | 179136 | 81258.08 | 0 | 284204.24
625 | 369.6 | 0 | 0 | 0 | 0 | 1395.25 | 0 | 0 | 0 | 439824 | 0
626 | 342.4 | 0 | 0 | 0 | 0 | 1386.3 | 0 | 0 | 0 | 407456 | 0
627 | 378.4 | 0 | 0 | 0 | 0 | 1311.7 | 0 | 0 | 0 | 450296 | 0
628 | 387.2 | 0 | 0 | 0 | 0 | 1374.3 | 0 | 0 | 0 | 460768 | 0
629 | 368.8 | 0 | 0 | 0 | 0 | 1384.85 | 0 | 0 | 0 | 438872 | 0
630 | 325.6 | 0 | 0 | 0 | 0 | 1383.5 | 0 | 0 | 0 | 387464 | 0
631 | 335.2 | 348.2074 | 348.2074 | 338.9661 | 335.2 | 1316.75 | 464214.8424 | 120672 | 54738.16 | 0 | 229025.4
632 | 281.28 | 591.7084 | 292.195 | 576.0048 | 281.28 | 1472.5 | 435049.0489 | 101260.8 | 45933.024 | 0 | 148375.2
633 | 812.402 | 1949.5695 | 843.9271 | 1897.829 | 812.402 | 1537 | 1311495.9886 | 292464.72 | 132665.2466 | 0 | 376142.126
634 | 1193.029 | 3273.2457 | 1239.3242 | 3186.3756 | 1193.029 | 1508.85 | 1891082.5368 | 429490.44 | 194821.6357 | 0 | 585956.1934
635 | 997.388 | 3342.7231 | 1036.0914 | 3254.009 | 997.388 | 1409.65 | 1485153.2185 | 359059.68 | 162873.4604 | 0 | 588808.0058
636 | 1238.61 | 4030.2487 | 1286.6739 | 3923.2881 | 1238.61 | 1459.95 | 1909154.6486 | 445899.6 | 202265.013 | 0 | 668911.3305
637 | 1158.511 | 3991.2998 | 1203.4667 | 3885.3728 | 1158.511 | 1464.05 | 1785327.9357 | 417063.96 | 189184.8463 | 0 | 620903.9705
638 | 1234.863 | 3802.7847 | 1282.7815 | 3701.8609 | 1234.863 | 1503.95 | 1958992.0141 | 444550.68 | 201653.1279 | 0 | 612553.7911
639 | 1047.104 | 2365.6358 | 1087.7366 | 2302.8531 | 1047.104 | 1522.4 | 1680485.7777 | 376957.44 | 170992.0832 | 0 | 500096.8704
640 | 1281.661 | 2059.822 | 1331.3955 | 2005.1555 | 1281.661 | 1532.8 | 2069553.1109 | 461397.96 | 209295.2413 | 0 | 598792.0192
641 | 1055.169 | 1237.203 | 1096.1146 | 1204.3683 | 1055.169 | 1544 | 1713848.9747 | 379860.84 | 172309.0977 | 0 | 481157.064
642 | 1044.091 | 201.4128 | 201.4128 | 196.0674 | 196.0674 | 1546.2 | 319274.3538 | 70584.2739 | 32017.8109 | 1554427.2083 | 87093.296
643 | 1088.323 | 0 | 0 | 0 | 0 | 1605.2 | 0 | 0 | 0 | 3698121.554 | 0
644 | 898.4 | 459.0208 | 459.0208 | 446.8386 | 446.8386 | 1508.95 | 712084.616 | 160861.913 | 72968.7511 | 1534405.4764 | 216982.2277
645 | 270.4 | 280.8928 | 280.8928 | 273.4381 | 270.4 | 1492.6 | 425083.343 | 97344 | 44156.32 | 0 | 137200.96
646 | 91.2 | 94.739 | 94.739 | 92.2247 | 91.2 | 1481.25 | 142093.853 | 32832 | 14892.96 | 0 | 47310
647 | 94.4 | 98.0632 | 98.0632 | 95.4606 | 94.4 | 1462.05 | 145413.5578 | 33984 | 15415.52 | 0 | 50782.48
648 | 91.2 | 0 | 0 | 0 | 0 | 1438.95 | 0 | 0 | 0 | 167169.6 | 0
649 | 96 | 0 | 0 | 0 | 0 | 1420.85 | 0 | 0 | 0 | 114240 | 0
650 | 88 | 0 | 0 | 0 | 0 | 1425.7 | 0 | 0 | 0 | 104720 | 0
651 | 94.4 | 0 | 0 | 0 | 0 | 1422.85 | 0 | 0 | 0 | 112336 | 0
652 | 85.6 | 0 | 0 | 0 | 0 | 1414.15 | 0 | 0 | 0 | 101864 | 0
653 | 95.2 | 0 | 0 | 0 | 0 | 1414.4 | 0 | 0 | 0 | 113288 | 0
654 | 88 | 0 | 0 | 0 | 0 | 1425.1 | 0 | 0 | 0 | 104720 | 0
655 | 93.6 | 57.3005 | 57.3005 | 55.7797 | 55.7797 | 1426.25 | 83871.1511 | 20080.7088 | 9108.8326 | 69324.5243 | 31326.75
656 | 77.076 | 554.3914 | 80.0669 | 539.6782 | 77.076 | 1472.9 | 119442.9416 | 27747.36 | 12586.5108 | 0 | 40626.7596
657 | 83.396 | 1273.238 | 86.6322 | 1239.447 | 83.396 | 1453.7 | 127561.7706 | 30022.56 | 13618.5668 | 0 | 45559.2348
658 | 78.901 | 3180.8513 | 81.9627 | 3096.4332 | 78.901 | 1458.15 | 121243.1973 | 28404.36 | 12884.5333 | 0 | 42752.5069
659 | 86.02 | 3684.1023 | 89.358 | 3586.3283 | 86.02 | 1475.55 | 133688.1758 | 30967.2 | 14047.066 | 0 | 45113.189
660 | 80.475 | 3955.0112 | 83.5978 | 3850.0474 | 80.475 | 1473.75 | 125050.3458 | 28971 | 13141.5675 | 0 | 42349.9688
661 | 88.61 | 3961.3032 | 92.0485 | 3856.1724 | 88.61 | 1456.75 | 136216.3372 | 31899.6 | 14470.013 | 0 | 48137.3825
662 | 80.761 | 3713.7197 | 83.8949 | 3615.1596 | 80.761 | 1462.3 | 124774.4591 | 29073.96 | 13188.2713 | 0 | 43425.1897
663 | 95.362 | 3248.2822 | 99.0625 | 3162.0746 | 95.362 | 1462.85 | 147331.3181 | 34330.32 | 15572.6146 | 0 | 51223.6983
664 | 84.557 | 1851.7328 | 87.8382 | 1802.5889 | 84.557 | 1229.9 | 109728.8264 | 30440.52 | 13808.1581 | 0 | 65117.3457
665 | 90.093 | 1375.738 | 93.589 | 1339.2266 | 90.093 | 1462 | 138521.4297 | 32433.48 | 14712.1869 | 0 | 48470.034
666 | 80.774 | 232.4139 | 83.9084 | 226.2457 | 80.774 | 1514.35 | 128861.2528 | 29078.64 | 13190.3942 | 0 | 39227.8931
667 | 96.805 | 100.5615 | 100.5615 | 97.8926 | 96.805 | 1606.65 | 163894.1215 | 34849.8 | 15808.2565 | 0 | 38078.2467
668 | 86.4 | 89.7527 | 89.7527 | 87.3707 | 86.4 | 1563.75 | 142685.5988 | 31104 | 14109.12 | 0 | 37692
669 | 93.6 | 97.2321 | 97.2321 | 94.6516 | 93.6 | 1545.15 | 152747.6504 | 33696 | 15284.88 | 0 | 42573.96
670 | 87.2 | 90.5838 | 90.5838 | 88.1797 | 87.2 | 1490.2 | 137378.0039 | 31392 | 14239.76 | 0 | 44454.56
671 | 92.8 | 96.4011 | 96.4011 | 93.8426 | 92.8 | 1513.7 | 148509.5035 | 33408 | 15154.24 | 0 | 45128.64
672 | 87.2 | 90.5838 | 90.5838 | 88.1797 | 87.2 | 1427.15 | 131348.451 | 31392 | 14239.76 | 0 | 49952.52
673 | 93.6 | 0 | 0 | 0 | 0 | 1481.4 | 0 | 0 | 0 | 111384 | 0
674 | 88 | 0 | 0 | 0 | 0 | 1431.1 | 0 | 0 | 0 | 104720 | 0
675 | 92.8 | 59.1184 | 59.1184 | 57.5494 | 57.5494 | 1421.05 | 86356.4972 | 20717.7871 | 9397.8184 | 41948.2036 | 32642.9378
676 | 87.2 | 90.5838 | 90.5838 | 88.1797 | 87.2 | 1420.5 | 130647.9275 | 31392 | 14239.76 | 0 | 50532.4
677 | 93.6 | 97.2321 | 97.2321 | 94.6516 | 93.6 | 1423.7 | 140642.4472 | 33696 | 15284.88 | 0 | 53941.68
678 | 83.2 | 86.4286 | 86.4286 | 84.1348 | 83.2 | 1433.15 | 125904.7467 | 29952 | 13586.56 | 0 | 47161.92
679 | 84.8 | 88.0906 | 88.0906 | 85.7528 | 84.8 | 1460.05 | 130465.7168 | 30528 | 13847.84 | 0 | 45787.76
680 | 79.796 | 523.0174 | 82.8925 | 509.1368 | 79.796 | 1485.15 | 124695.6754 | 28726.56 | 13030.6868 | 0 | 41082.9706
681 | 84.042 | 1916.522 | 87.3032 | 1865.6586 | 84.042 | 1514.75 | 133954.6395 | 30255.12 | 13724.0586 | 0 | 40781.3805
682 | 80.506 | 3123.1415 | 83.63 | 3040.2551 | 80.506 | 1517.8 | 128756.77 | 28982.16 | 13146.6298 | 0 | 38819.9932
683 | 81.184 | 3549.6363 | 84.3343 | 3455.4309 | 81.184 | 1512.05 | 129620.6501 | 29226.24 | 13257.3472 | 0 | 39613.7328
684 | 80.078 | 3847.6663 | 83.1854 | 3745.5513 | 80.078 | 1504.25 | 127065.2404 | 28828.08 | 13076.7374 | 0 | 39698.6685
685 | 81.515 | 3706.1738 | 84.6782 | 3607.814 | 81.515 | 1494.25 | 128193.494 | 29345.4 | 13311.3995 | 0 | 41226.2112
686 | 74.649 | 2457.4744 | 77.5457 | 2392.2544 | 74.649 | 1512.05 | 119180.171 | 26873.64 | 12190.1817 | 0 | 36424.9795
687 | 88.307 | 2103.0426 | 91.7337 | 2047.229 | 88.307 | 1538.5 | 143263.0536 | 31790.52 | 14420.5331 | 0 | 40753.6805
688 | 79.067 | 1155.075 | 82.1352 | 1124.42 | 79.067 | 1542.5 | 128599.9931 | 28464.12 | 12911.6411 | 0 | 36173.1525
689 | 84.323 | 247.5243 | 87.5951 | 240.9552 | 84.323 | 1555.05 | 138174.6147 | 30356.28 | 13769.9459 | 0 | 37519.5189
690 | 79.24 | 174.2969 | 82.3149 | 169.6711 | 79.24 | 1564.7 | 130579.196 | 28526.4 | 12939.892 | 0 | 34493.172
691 | 95.215 | 98.9098 | 98.9098 | 96.2848 | 95.215 | 1572.9 | 157944.1676 | 34277.4 | 15548.6095 | 0 | 40666.3265
692 | 89.6 | 93.0769 | 93.0769 | 90.6067 | 89.6 | 1533.7 | 145017.8128 | 32256 | 14631.68 | 0 | 41780.48
693 | 93.6 | 97.2321 | 97.2321 | 94.6516 | 93.6 | 1513.55 | 149130.2317 | 33696 | 15284.88 | 0 | 45531.72
694 | 87.2 | 90.5838 | 90.5838 | 88.1797 | 87.2 | 1495.6 | 137282.2483 | 31392 | 14239.76 | 0 | 43983.68
695 | 96.8 | 100.5563 | 100.5563 | 97.8876 | 96.8 | 1515.1 | 154570.8357 | 34848 | 15807.44 | 0 | 46938.32
696 | 87.2 | 90.5838 | 90.5838 | 88.1797 | 87.2 | 1541.35 | 141436.3954 | 31392 | 14239.76 | 0 | 39994.28
697 | 93.6 | 0 | 0 | 0 | 0 | 1523.9 | 0 | 0 | 0 | 111384 | 0
698 | 88.8 | 0 | 0 | 0 | 0 | 1503.6 | 0 | 0 | 0 | 105672 | 0
699 | 87.2 | 0 | 0 | 0 | 0 | 1463.65 | 0 | 0 | 0 | 103768 | 0
700 | 87.2 | 86.6976 | 86.6976 | 84.3967 | 84.3967 | 1428.1 | 127075.452 | 30382.8114 | 13781.9808 | 3335.929 | 47730.2021
701 | 93.6 | 97.2321 | 97.2321 | 94.6516 | 93.6 | 1431.3 | 141157.8453 | 33696 | 15284.88 | 0 | 53230.32
702 | 84 | 87.2596 | 87.2596 | 84.9438 | 84 | 1445.75 | 127813.6667 | 30240 | 13717.2 | 0 | 46557
703 | 87.2 | 90.5838 | 90.5838 | 88.1797 | 87.2 | 1531.55 | 140335.3744 | 31392 | 14239.76 | 0 | 40848.84
704 | 76.02 | 78.9699 | 78.9699 | 76.8741 | 76.02 | 1485.15 | 118649.5815 | 27367.2 | 12414.066 | 0 | 39138.897
705 | 84.507 | 1477.5128 | 87.7863 | 1438.3004 | 84.507 | 1556.25 | 138322.5596 | 30422.52 | 13799.9931 | 0 | 37499.9812
706 | 72.771 | 2581.5264 | 75.5938 | 2513.0141 | 72.771 | 1594.1 | 122164.7269 | 26197.56 | 11883.5043 | 0 | 29537.7489
707 | 81.102 | 3867.709 | 84.2491 | 3765.0621 | 81.102 | 1519.65 | 129310.9644 | 29196.72 | 13243.9566 | 0 | 38957.3457
708 | 75.163 | 4009.2659 | 78.0797 | 3902.8622 | 75.163 | 1541.85 | 122424.1616 | 27058.68 | 12274.1179 | 0 | 34435.9285
709 | 86.617 | 4204.1675 | 89.9782 | 4092.5912 | 86.617 | 1498.05 | 136638.5045 | 31182.12 | 14144.5561 | 0 | 43477.4031
710 | 78.42 | 3557.4897 | 81.4631 | 3463.0759 | 78.42 | 1562.9 | 129081.4842 | 28231.2 | 12805.986 | 0 | 34277.382
711 | 78.853 | 2922.3437 | 81.9129 | 2844.7863 | 78.853 | 1625 | 134858.9635 | 28387.08 | 12876.6949 | 0 | 29569.875
712 | 79.653 | 2431.5178 | 82.7439 | 2366.9867 | 79.653 | 1588.8 | 133190.3811 | 28675.08 | 13007.3349 | 0 | 32753.3136
713 | 88.652 | 1032.7859 | 92.0921 | 1005.3763 | 88.652 | 1555.05 | 145116.1975 | 31914.72 | 14476.8716 | 0 | 39445.7074
714 | 82.665 | 240.6526 | 85.8728 | 234.2658 | 82.665 | 1564.7 | 136127.8729 | 29759.4 | 13499.1945 | 0 | 35984.0745
715 | 97.636 | 101.4247 | 101.4247 | 98.733 | 97.636 | 1614.4 | 166291.6424 | 35148.96 | 15943.9588 | 0 | 37648.4416
716 | 88.8 | 92.2459 | 92.2459 | 89.7977 | 88.8 | 1575.2 | 147580.8014 | 31968 | 14501.04 | 0 | 37722.24
717 | 94.4 | 98.0632 | 98.0632 | 95.4606 | 94.4 | 1555.05 | 154496.6743 | 33984 | 15415.52 | 0 | 42003.28
718 | 87.2 | 90.5838 | 90.5838 | 88.1797 | 87.2 | 1568.1 | 143905.9215 | 31392 | 14239.76 | 0 | 37661.68
719 | 91.2 | 94.739 | 94.739 | 92.2247 | 91.2 | 1624.25 | 156035.2493 | 32832 | 14892.96 | 0 | 34268.4
720 | 84.8 | 88.0906 | 88.0906 | 85.7528 | 84.8 | 1541.35 | 137611.602 | 30528 | 13847.84 | 0 | 38893.52
721 | 93.6 | 0 | 0 | 0 | 0 | 1482.15 | 0 | 0 | 0 | 111384 | 0
722 | 81.6 | 0 | 0 | 0 | 0 | 1431.1 | 0 | 0 | 0 | 97104 | 0
723 | 92.8 | 31.0758 | 31.0758 | 30.2511 | 30.2511 | 1428.65 | 45591.4141 | 10890.3989 | 4940.006 | 74433.1814 | 17017.6597
724 | 80 | 83.1044 | 83.1044 | 80.8988 | 80 | 1428.1 | 120622.2523 | 28800 | 13064 | 0 | 45752
725 | 90.4 | 93.9079 | 93.9079 | 91.4157 | 90.4 | 1431.3 | 136599.1289 | 32544 | 14762.32 | 0 | 51410.48
726 | 80 | 83.1044 | 83.1044 | 80.8988 | 80 | 1483.25 | 125204.2083 | 28800 | 13064 | 0 | 41340
727 | 86.4 | 89.7527 | 89.7527 | 87.3707 | 86.4 | 1546.55 | 140784.8523 | 31104 | 14109.12 | 0 | 39178.08
728 | 75.453 | 78.3809 | 78.3809 | 76.3007 | 75.453 | 1570.65 | 124720.1578 | 27163.08 | 12321.4749 | 0 | 32395.7455
729 | 85.467 | 1211.8613 | 88.7835 | 1179.6992 | 85.467 | 1599.75 | 144020.4513 | 30768.12 | 13956.7611 | 0 | 34208.1667
730 | 74.454 | 2657.2553 | 77.3432 | 2586.7332 | 74.454 | 1605.6 | 126040.968 | 26803.44 | 12158.3382 | 0 | 29364.6576
731 | 80.579 | 3691.7438 | 83.7058 | 3593.7669 | 80.579 | 1519.65 | 129659.5614 | 29008.44 | 13158.5507 | 0 | 38706.1226
732 | 73.28 | 3376.7346 | 76.1236 | 3287.1179 | 73.28 | 1511.85 | 117635.9831 | 26380.8 | 11966.624 | 0 | 35771.632
733 | 82.654 | 3550.6596 | 85.8614 | 3456.427 | 82.654 | 1498.05 | 131055.7399 | 29755.44 | 13497.3982 | 0 | 41488.1753
734 | 74.961 | 2123.238 | 77.8698 | 2066.8884 | 74.961 | 1561.15 | 123895.3192 | 26985.96 | 12241.1313 | 0 | 32896.6349
735 | 86.787 | 1625.451 | 90.1547 | 1582.3124 | 86.787 | 1624 | 149365.6563 | 31243.32 | 14172.3171 | 0 | 32631.912
736 | 81.253 | 1581.7766 | 84.406 | 1539.7971 | 81.253 | 1632.05 | 140137.4019 | 29251.08 | 13268.6149 | 0 | 29897.0414
737 | 87.089 | 680.7963 | 90.4685 | 662.7283 | 87.089 | 1555.05 | 142592.4133 | 31352.04 | 14221.6337 | 0 | 38750.2505
738 | 79.66 | 224.1876 | 82.7512 | 218.2378 | 79.66 | 1606.2 | 134631.4288 | 28677.6 | 13008.478 | 0 | 31370.108
739 | 96.821 | 100.5781 | 100.5781 | 97.9088 | 96.821 | 1658.4 | 169196.3482 | 34855.56 | 15810.8693 | 0 | 33074.0536
740 | 88 | 91.4148 | 91.4148 | 88.9887 | 88 | 1618.2 | 150038.2065 | 31680 | 14370.4 | 0 | 33598.4
741 | 91.2 | 94.739 | 94.739 | 92.2247 | 91.2 | 1556.55 | 149318.7303 | 32832 | 14892.96 | 0 | 40442.64
742 | 86.4 | 89.7527 | 89.7527 | 87.3707 | 86.4 | 1582.1 | 143803.2731 | 31104 | 14109.12 | 0 | 36106.56
743 | 92.8 | 96.4011 | 96.4011 | 93.8426 | 92.8 | 1588.85 | 155375.1104 | 33408 | 15154.24 | 0 | 38154.72
744 | 88 | 91.4148 | 91.4148 | 88.9887 | 88 | 1650.1 | 153149.1458 | 31680 | 14370.4 | 0 | 30791.2
745 | 94.4 | 0 | 0 | 0 | 0 | 1648.85 | 0 | 0 | 0 | 112336 | 0
746 | 87.2 | 0 | 0 | 0 | 0 | 1496.6 | 0 | 0 | 0 | 103768 | 0
747 | 93.6 | 66.6694 | 66.6694 | 64.9001 | 64.9001 | 1448.95 | 99528.1327 | 23364.0285 | 10598.1829 | 34152.9059 | 35066.0667
748 | 80 | 83.1044 | 83.1044 | 80.8988 | 80 | 1447.7 | 122560.3025 | 28800 | 13064 | 0 | 44184
749 | 88.8 | 92.2459 | 92.2459 | 89.7977 | 88.8 | 1471.45 | 138326.7521 | 31968 | 14501.04 | 0 | 46935.24
750 | 86.4 | 89.7527 | 89.7527 | 87.3707 | 86.4 | 1519.5 | 138882.1374 | 31104 | 14109.12 | 0 | 41515.2
751 | 88.8 | 92.2459 | 92.2459 | 89.7977 | 88.8 | 1552.95 | 145619.0221 | 31968 | 14501.04 | 0 | 39698.04
752 | 79.281 | 458.8089 | 82.3575 | 446.6324 | 79.281 | 1540.95 | 128813.3655 | 28541.16 | 12946.5873 | 0 | 36393.943
753 | 84.741 | 1840.8462 | 88.0294 | 1791.9911 | 84.741 | 1572.5 | 140718.1427 | 30506.76 | 13838.2053 | 0 | 36226.7775
754 | 75.611 | 3117.7959 | 78.5451 | 3035.0513 | 75.611 | 1555.75 | 124590.5176 | 27219.96 | 12347.2763 | 0 | 33590.1867
755 | 86.655 | 3673.5876 | 90.0176 | 3576.0925 | 86.655 | 1532.9 | 140901.7466 | 31195.8 | 14150.7615 | 0 | 40476.5505
756 | 74.903 | 3886.2132 | 77.8096 | 3783.0753 | 74.903 | 1526.95 | 121293.2508 | 26965.08 | 12231.6599 | 0 | 35432.8641
757 | 87.642 | 3865.9285 | 91.0429 | 3763.3289 | 87.642 | 1515.1 | 140573.8518 | 31551.12 | 14311.9386 | 0 | 42497.6058
758 | 82.638 | 3176.2671 | 85.8447 | 3091.9707 | 82.638 | 1526.6 | 133663.2753 | 29749.68 | 13494.7854 | 0 | 39120.8292
759 | 89.332 | 3150.9971 | 92.7985 | 3067.3713 | 89.332 | 1541.65 | 145770.0364 | 32159.52 | 14587.9156 | 0 | 40945.3222
760 | 81.435 | 2443.3633 | 84.5951 | 2378.5178 | 81.435 | 1554.8 | 134007.0746 | 29316.6 | 13298.3355 | 0 | 36254.862
761 | 83.254 | 1381.5698 | 86.4847 | 1344.9037 | 83.254 | 1602.35 | 140826.0267 | 29971.44 | 13595.3782 | 0 | 33105.9531
762 | 82.933 | 237.3461 | 86.1512 | 231.0471 | 82.933 | 1645.65 | 144258.775 | 29855.88 | 13542.9589 | 0 | 29387.3085
763 | 96.007 | 99.7325 | 99.7325 | 97.0857 | 96.007 | 1782.4 | 180934.9371 | 34562.52 | 15677.9431 | 0 | 20891.1232
764 | 91.2 | 94.739 | 94.739 | 92.2247 | 91.2 | 1634.05 | 157444.4167 | 32832 | 14892.96 | 0 | 33374.64
765 | 93.6 | 97.2321 | 97.2321 | 94.6516 | 93.6 | 1731.75 | 170786.1094 | 33696 | 15284.88 | 0 | 25108.2
766 | 88.8 | 92.2459 | 92.2459 | 89.7977 | 88.8 | 1836.55 | 171755.077 | 31968 | 14501.04 | 0 | 14514.36
767 | 97.6 | 101.3873 | 101.3873 | 98.6966 | 97.6 | 1812.5 | 186815.5889 | 35136 | 15938.08 | 0 | 18300
768 | 90.4 | 0 | 0 | 0 | 0 | 1798.7 | 0 | 0 | 0 | 165703.2 | 0
769 | 92.8 | 0 | 0 | 0 | 0 | 1773.85 | 0 | 0 | 0 | 170102.4 | 0
770 | 86.4 | 60.3629 | 60.3629 | 58.7609 | 58.7609 | 1540.4 | 95598.9954 | 21153.9128 | 9595.6499 | 50662.5276 | 26421.4848
771 | 91.2 | 94.739 | 94.739 | 92.2247 | 91.2 | 1531.45 | 147642.6361 | 32832 | 14892.96 | 0 | 42731.76
772 | 87.2 | 90.5838 | 90.5838 | 88.1797 | 87.2 | 1529.7 | 141097.7067 | 31392 | 14239.76 | 0 | 41010.16
773 | 92.8 | 96.4011 | 96.4011 | 93.8426 | 92.8 | 1530.6 | 150167.1783 | 33408 | 15154.24 | 0 | 43560.32
774 | 85.6 | 88.9217 | 88.9217 | 86.5618 | 85.6 | 1539.15 | 139357.0649 | 30816 | 13978.48 | 0 | 39448.76
775 | 76.8 | 79.7802 | 79.7802 | 77.6629 | 76.8 | 1782.95 | 145038.3805 | 27648 | 12541.44 | 0 | 16669.44
776 | 82.775 | 387.5396 | 85.9871 | 377.2545 | 82.775 | 1765.2 | 154556.2974 | 29799 | 13517.1575 | 0 | 19435.57
777 | 646.748 | 1710.7026 | 671.8449 | 1665.3015 | 646.748 | 1609.4 | 1102607.1728 | 232829.28 | 105613.9484 | 0 | 252619.7688
778 | 552.934 | 3243.6689 | 574.3905 | 3157.5837 | 552.934 | 1595.75 | 937750.1824 | 199056.24 | 90294.1222 | 0 | 223523.5695
779 | 876.383 | 3011.604 | 910.3908 | 2931.6777 | 876.383 | 1555.95 | 1459628.3995 | 315497.88 | 143113.3439 | 0 | 389157.8711
780 | 949.841 | 3356.7864 | 986.6993 | 3267.6991 | 949.841 | 1548.8 | 1570142.1137 | 341942.76 | 155109.0353 | 0 | 428568.2592
781 | 1244.374 | 3314.3356 | 1292.6616 | 3226.375 | 1244.374 | 1515.1 | 2005592.92 | 447974.64 | 203206.2742 | 0 | 603396.9526
782 | 1169.848 | 3170.3656 | 1215.2437 | 3086.2258 | 1169.848 | 1548.45 | 1927341.9883 | 421145.28 | 191036.1784 | 0 | 528244.8644
783 | 1381.741 | 3124.2188 | 1435.3591 | 3041.3037 | 1381.741 | 1588.7 | 2330296.4715 | 497426.76 | 225638.3053 | 0 | 568310.0733
784 | 889.368 | 2056.475 | 923.8797 | 2001.8973 | 889.368 | 1556.7 | 1466648.3352 | 320172.48 | 145233.7944 | 0 | 394256.8344
785 | 1360.953 | 987.413 | 987.413 | 961.2076 | 961.2076 | 1593.2 | 1620344.084 | 346034.735 | 156965.2006 | 732733.3235 | 382747.95
786 | 1095.157 | 209.3794 | 209.3794 | 203.8226 | 203.8226 | 1626.5 | 350993.9754 | 73376.1332 | 33284.2293 | 1633815.9696 | 74517.3585
787 | 1127.015 | 0 | 0 | 0 | 0 | 1782.4 | 0 | 0 | 0 | 2065818.495 | 0
788 | 1211.2 | 0 | 0 | 0 | 0 | 1749.55 | 0 | 0 | 0 | 2220129.6 | 0
789 | 1118.4 | 0 | 0 | 0 | 0 | 1729.6 | 0 | 0 | 0 | 2050027.2 | 0
790 | 1337.6 | 125.1583 | 125.1583 | 121.8367 | 121.8367 | 1835.55 | 235354.8671 | 43861.2045 | 19895.9297 | 2228494.1672 | 19704.8924
791 | 1112 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1810.35 | 1144281.4369 | 215514.4963 | 97759.7701 | 940968.0233 | 112272.8
792 | 163.2 | 169.5329 | 169.5329 | 165.0336 | 163.2 | 1790.85 | 309234.1373 | 58752 | 26650.56 | 0 | 34133.28
793 | 108.8 | 0 | 0 | 0 | 0 | 1766.5 | 0 | 0 | 0 | 129472 | 0
794 | 94.4 | 0 | 0 | 0 | 0 | 1602.6 | 0 | 0 | 0 | 112336 | 0
795 | 105.6 | 0 | 0 | 0 | 0 | 1506.8 | 0 | 0 | 0 | 125664 | 0
796 | 101.6 | 0 | 0 | 0 | 0 | 1484.75 | 0 | 0 | 0 | 120904 | 0
797 | 105.6 | 0 | 0 | 0 | 0 | 1484.7 | 0 | 0 | 0 | 125664 | 0
798 | 95.2 | 0 | 0 | 0 | 0 | 1491.45 | 0 | 0 | 0 | 113288 | 0
799 | 87.2 | 90.5838 | 90.5838 | 88.1797 | 87.2 | 1519.5 | 140485.0149 | 31392 | 14239.76 | 0 | 41899.6
800 | 82.403 | 553.096 | 85.6006 | 538.4171 | 82.403 | 1519.9 | 132735.7841 | 29665.08 | 13456.4099 | 0 | 39561.6803
801 | 835.519 | 1919.68 | 867.9411 | 1868.7327 | 835.519 | 1504.85 | 1335754.975 | 300786.84 | 136440.2527 | 0 | 413707.2328
802 | 1039.674 | 3207.239 | 1080.0183 | 3122.1206 | 1039.674 | 1502 | 1663899.9595 | 374282.64 | 169778.7642 | 0 | 517757.652
803 | 891.524 | 3719.6045 | 926.1194 | 3620.8883 | 891.524 | 1338 | 1278682.3551 | 320948.64 | 145585.8692 | 0 | 590188.888
804 | 1352.422 | 3865.9046 | 1404.9024 | 3763.3056 | 1352.422 | 1403.55 | 2032589.6376 | 486871.92 | 220850.5126 | 0 | 806652.1019
805 | 1341.667 | 3943.3433 | 1393.7301 | 3838.6892 | 1341.667 | 1484.65 | 2127858.908 | 483000.12 | 219094.2211 | 0 | 691428.0884
806 | 1194.461 | 3556.7802 | 1240.8118 | 3462.3852 | 1194.461 | 1494.45 | 1911344.4468 | 430005.96 | 195055.4813 | 0 | 603859.7585
807 | 1481.371 | 2684.767 | 1538.8552 | 2613.5147 | 1481.371 | 1508.55 | 2382070.9909 | 533293.56 | 241907.8843 | 0 | 728019.778
808 | 1646.336 | 712.5899 | 712.5899 | 693.6782 | 693.6782 | 1516.9 | 1117426.3083 | 249724.1461 | 113277.6474 | 1746221.7773 | 328026.8324
809 | 1713.488 | 713.1218 | 713.1218 | 694.1959 | 694.1959 | 1528 | 1123155.1399 | 249910.537 | 113362.1964 | 1868362.3529 | 320729.192
810 | 1434.101 | 121.9172 | 121.9172 | 118.6816 | 118.6816 | 1536.9 | 192855.0256 | 42725.3848 | 19380.7093 | 2411163.7152 | 53798.7901
811 | 1539.509 | 0 | 0 | 0 | 0 | 1585.95 | 0 | 0 | 0 | 5231251.582 | 0
812 | 1661.6 | 0 | 0 | 0 | 0 | 1559.35 | 0 | 0 | 0 | 5646116.8 | 0
813 | 1616 | 0 | 0 | 0 | 0 | 1539.25 | 0 | 0 | 0 | 5491168 | 0
814 | 1728.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1800.55 | 587467.1595 | 111351.8261 | 50510.4255 | 4823424.8863 | 61006.5693
815 | 1469.6 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1783.85 | 1130816.4714 | 215514.4963 | 97759.7701 | 2959483.4159 | 127960.8
816 | 1761.6 | 0 | 0 | 0 | 0 | 1771.1 | 0 | 0 | 0 | 3229012.8 | 0
817 | 1354.4 | 0 | 0 | 0 | 0 | 1598.25 | 0 | 0 | 0 | 1611736 | 0
818 | 1331.2 | 0 | 0 | 0 | 0 | 1752.1 | 0 | 0 | 0 | 1584128 | 0
819 | 1416.8 | 0 | 0 | 0 | 0 | 1747.8 | 0 | 0 | 0 | 1685992 | 0
820 | 1299.2 | 0 | 0 | 0 | 0 | 1746.6 | 0 | 0 | 0 | 1546048 | 0
821 | 1488 | 0 | 0 | 0 | 0 | 1747.3 | 0 | 0 | 0 | 1770720 | 0
822 | 1488.8 | 0 | 0 | 0 | 0 | 1748.75 | 0 | 0 | 0 | 1771672 | 0
823 | 1292.8 | 66.0711 | 66.0711 | 64.3176 | 64.3176 | 1750.75 | 119355.3385 | 23154.3387 | 10503.0653 | 2251808.2255 | 15692.0323
824 | 1289.506 | 1130.4377 | 1130.4377 | 1100.4365 | 1100.4365 | 1594.2 | 1864234.57 | 396157.1452 | 179701.2828 | 346564.367 | 437110.7164
825 | 1526.73 | 1585.9744 | 1585.9744 | 1543.8835 | 1526.73 | 1516.9 | 2464833.7087 | 549622.8 | 249315.009 | 0 | 737563.263
826 | 1083.978 | 2043.3435 | 1126.0415 | 1989.1143 | 1083.978 | 1466.35 | 1700672.976 | 390232.08 | 177013.6074 | 0 | 578464.8597
827 | 1402.913 | 2705.7965 | 1457.3527 | 2633.9862 | 1402.913 | 1465.5 | 2209957.1735 | 505048.68 | 229095.6929 | 0 | 749856.9985
828 | 1305.329 | 3529.7588 | 1355.982 | 3436.0809 | 1305.329 | 1467.95 | 2053872.679 | 469918.44 | 213160.2257 | 0 | 694500.2944
829 | 1517.919 | 3266.2608 | 1576.8215 | 3179.576 | 1517.919 | 1461.4 | 2375236.7524 | 546450.84 | 247876.1727 | 0 | 817551.1734
830 | 1335.878 | 3094.6128 | 1387.7164 | 3012.4835 | 1335.878 | 1467.95 | 2098153.9111 | 480916.08 | 218148.8774 | 0 | 710753.8899
831 | 1360.865 | 2423.0838 | 1413.673 | 2358.7764 | 1360.865 | 1460.4 | 2119221.7601 | 489911.4 | 222229.2545 | 0 | 734322.754
832 | 1604.627 | 2083.6616 | 1666.8941 | 2028.3623 | 1604.627 | 1490.55 | 2535586.5198 | 577665.72 | 262035.5891 | 0 | 817477.2252
833 | 1501.802 | 1195.817 | 1195.817 | 1164.0806 | 1164.0806 | 1508.4 | 1857383.453 | 419069.0301 | 190094.3684 | 619043.2544 | 560156.5696
834 | 1303.802 | 199.4204 | 199.4204 | 194.1279 | 194.1279 | 1588.3 | 326060.9644 | 69886.0361 | 31701.0825 | 2034032.6656 | 78231.6457
835 | 1407.738 | 0 | 0 | 0 | 0 | 1847.5 | 0 | 0 | 0 | 4783493.724 | 0
836 | 1397.6 | 0 | 0 | 0 | 0 | 1825.6 | 0 | 0 | 0 | 4749044.8 | 0
837 | 1207.2 | 0 | 0 | 0 | 0 | 1799.75 | 0 | 0 | 0 | 4102065.6 | 0
838 | 1357.6 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1793.35 | 585931.6203 | 111351.8261 | 50510.4255 | 3562087.2863 | 63208.8621
839 | 1300.8 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1657.4 | 1050025.2987 | 215514.4963 | 97759.7701 | 2385901.0159 | 202819.2
840 | 1248.8 | 0 | 0 | 0 | 0 | 1506.9 | 0 | 0 | 0 | 2289050.4 | 0
841 | 1178.4 | 0 | 0 | 0 | 0 | 1460.9 | 0 | 0 | 0 | 1402296 | 0
842 | 1225.6 | 0 | 0 | 0 | 0 | 1458.9 | 0 | 0 | 0 | 1458464 | 0
843 | 1224.8 | 0 | 0 | 0 | 0 | 1448.95 | 0 | 0 | 0 | 1457512 | 0
844 | 903.2 | 0 | 0 | 0 | 0 | 1447.7 | 0 | 0 | 0 | 1074808 | 0
845 | 1121.6 | 0 | 0 | 0 | 0 | 1449.6 | 0 | 0 | 0 | 1334704 | 0
846 | 1310.4 | 0 | 0 | 0 | 0 | 1462.65 | 0 | 0 | 0 | 1559376 | 0
847 | 1152 | 0 | 0 | 0 | 0 | 1476.95 | 0 | 0 | 0 | 2111616 | 0
848 | 933.17 | 230.7165 | 230.7165 | 224.5934 | 224.5934 | 1516.7 | 360389.4403 | 80853.6125 | 36676.097 | 1298820.9665 | 106250.1219
849 | 1215.698 | 1146.5704 | 1146.5704 | 1116.141 | 1116.141 | 1580.45 | 1875609.1007 | 401810.7603 | 182265.8254 | 182487.9795 | 458371.3811
850 | 1139.46 | 1183.6765 | 1183.6765 | 1152.2623 | 1139.46 | 1578.8 | 1916180.1279 | 410205.6 | 186073.818 | 0 | 479940.552
851 | 1551.141 | 1611.3326 | 1611.3326 | 1568.5687 | 1551.141 | 1527.95 | 2519398.3944 | 558410.76 | 253301.3253 | 0 | 732216.109
852 | 1338.153 | 2244.8924 | 1390.0797 | 2185.3142 | 1338.153 | 1483.7 | 2117059.0165 | 481735.08 | 218520.3849 | 0 | 690888.3939
853 | 1140.835 | 3873.8774 | 1185.1048 | 3771.0668 | 1140.835 | 1474.9 | 1796609.9473 | 410700.6 | 186298.3555 | 0 | 599052.4585
854 | 1315.264 | 2944.9709 | 1366.3025 | 2866.813 | 1315.264 | 1503.6 | 2114835.0243 | 473495.04 | 214782.6112 | 0 | 652897.0496
855 | 1361.037 | 2355.5874 | 1413.8517 | 2293.0714 | 1361.037 | 1540.7 | 2235340.7909 | 489973.32 | 222257.3421 | 0 | 625124.2941
856 | 1270.539 | 1653.3533 | 1319.8419 | 1609.4742 | 1270.539 | 1551.75 | 2088687.2569 | 457394.04 | 207479.0187 | 0 | 569519.1068
857 | 1377.713 | 1074.7453 | 1074.7453 | 1046.2222 | 1046.2222 | 1566.4 | 1729182.3339 | 376639.9777 | 170848.0788 | 607622.7093 | 444045.8576
858 | 1430.203 | 231.7573 | 231.7573 | 225.6066 | 225.6066 | 1580.65 | 376131.4638 | 81218.3853 | 36841.562 | 2208025.1537 | 92607.1572
859 | 1135.9 | 0 | 0 | 0 | 0 | 1584.45 | 0 | 0 | 0 | 3859788.2 | 0
860 | 1324 | 0 | 0 | 0 | 0 | 1547.1 | 0 | 0 | 0 | 4498952 | 0
861 | 1216.8 | 0 | 0 | 0 | 0 | 1512.65 | 0 | 0 | 0 | 4134686.4 | 0
862 | 1368.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1514.55 | 493902.9718 | 111351.8261 | 50510.4255 | 3600144.8863 | 148486.5333
863 | 1304 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1494.35 | 945010.3547 | 215514.4963 | 97759.7701 | 2396774.6159 | 299344.8
864 | 504 | 0 | 0 | 0 | 0 | 1475.75 | 0 | 0 | 0 | 923832 | 0
865 | 308.8 | 0 | 0 | 0 | 0 | 1459.95 | 0 | 0 | 0 | 367472 | 0
866 | 223.2 | 0 | 0 | 0 | 0 | 1414.9 | 0 | 0 | 0 | 265608 | 0
867 | 305.6 | 0 | 0 | 0 | 0 | 1390.7 | 0 | 0 | 0 | 363664 | 0
868 | 234.4 | 0 | 0 | 0 | 0 | 1407.5 | 0 | 0 | 0 | 278936 | 0
869 | 284.8 | 0 | 0 | 0 | 0 | 1396.6 | 0 | 0 | 0 | 338912 | 0
870 | 280.8 | 0 | 0 | 0 | 0 | 1454.75 | 0 | 0 | 0 | 334152 | 0
871 | 279.2 | 60.7015 | 60.7015 | 59.0905 | 59.0905 | 1469.05 | 91182.1246 | 21272.5913 | 9649.4838 | 403460.6558 | 30710.148
872 | 207.884 | 525.844 | 215.9509 | 511.8884 | 207.884 | 1492.95 | 325920.421 | 74838.24 | 33947.4572 | 0 | 105407.5822
873 | 1383.408 | 1920.0644 | 1437.0908 | 1869.1069 | 1383.408 | 1453.4 | 2115426.6848 | 498026.88 | 225910.5264 | 0 | 756170.8128
874 | 1305.53 | 3160.3765 | 1356.1908 | 3076.5018 | 1305.53 | 1358.75 | 1876427.6023 | 469990.8 | 213193.049 | 0 | 837171.1125
875 | 1615.041 | 3429.4695 | 1677.7123 | 3338.4532 | 1615.041 | 345.9 | 597487.4894 | 581414.76 | 263736.1953 | 0 | 2671439.3181
876 | 1779.002 | 3526.7484 | 1848.0357 | 3433.1504 | 1779.002 | 1228.95 | 2336997.5195 | 640440.72 | 290511.0266 | 0 | 1371699.4921
877 | 1624.258 | 3425.2405 | 1687.2869 | 3334.3365 | 1624.258 | 1307.1 | 2270348.9637 | 584732.88 | 265241.3314 | 0 | 1125448.3682
878 | 1539.01 | 3222.1957 | 1598.7309 | 3136.6804 | 1539.01 | 1228.6 | 2027673.4823 | 554043.6 | 251320.333 | 0 | 1187192.314
879 | 1787.689 | 2312.4625 | 1857.0598 | 2251.091 | 1787.689 | 1344.6 | 2558976.7377 | 643568.04 | 291929.6137 | 0 | 1171651.3706
880 | 1354.304 | 1795.3777 | 1406.8574 | 1747.7293 | 1354.304 | 859.2 | 1230057.8538 | 487549.44 | 221157.8432 | 0 | 1544990.0032
881 | 1620.241 | 741.7637 | 741.7637 | 722.0777 | 722.0777 | 1368.35 | 1038914.9358 | 259947.9791 | 117915.2916 | 1646333.2928 | 446452.115
882 | 1300.99 | 183.0384 | 183.0384 | 178.1807 | 178.1807 | 1393.6 | 260710.1613 | 64145.0503 | 29096.9075 | 2058109.4558 | 105762.8304
883 | 1394.069 | 0 | 0 | 0 | 0 | 1516.7 | 0 | 0 | 0 | 4737046.462 | 0
884 | 1272 | 0 | 0 | 0 | 0 | 1419.05 | 0 | 0 | 0 | 4322256 | 0
885 | 1471.2 | 0 | 0 | 0 | 0 | 1409.6 | 0 | 0 | 0 | 4999137.6 | 0
886 | 1444 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1535.45 | 496842.0144 | 111351.8261 | 50510.4255 | 3855674.4863 | 142093.7667
887 | 1357.6 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1515.25 | 951015.0179 | 215514.4963 | 97759.7701 | 2578907.4159 | 286972
888 | 576.8 | 0 | 0 | 0 | 0 | 1481.75 | 0 | 0 | 0 | 1057274.4 | 0
889 | 498.4 | 0 | 0 | 0 | 0 | 1459.95 | 0 | 0 | 0 | 593096 | 0
890 | 498.4 | 0 | 0 | 0 | 0 | 1451 | 0 | 0 | 0 | 593096 | 0
891 | 504 | 0 | 0 | 0 | 0 | 1454 | 0 | 0 | 0 | 599760 | 0
892 | 421.6 | 0 | 0 | 0 | 0 | 1445.8 | 0 | 0 | 0 | 501704 | 0
893 | 485.6 | 0 | 0 | 0 | 0 | 1470.5 | 0 | 0 | 0 | 577864 | 0
894 | 467.2 | 0 | 0 | 0 | 0 | 1454.75 | 0 | 0 | 0 | 555968 | 0
895 | 472 | 60.9498 | 60.9498 | 59.3322 | 59.3322 | 1469.05 | 92422.0699 | 21359.598 | 9688.951 | 756420.0467 | 30835.9832
896 | 385.522 | 521.3023 | 400.4821 | 507.4673 | 385.522 | 1641.85 | 672206.8115 | 138787.92 | 62955.7426 | 0 | 138074.7043
897 | 1044.814 | 1952.0294 | 1085.3577 | 1900.2236 | 1044.814 | 1556.45 | 1728106.6787 | 376133.04 | 170618.1262 | 0 | 463427.2497
898 | 1692.649 | 3279.4432 | 1758.3318 | 3192.4086 | 1692.649 | 1438.45 | 2601455.4613 | 609353.64 | 276409.5817 | 0 | 950507.046
899 | 1873.143 | 3870.5948 | 1945.8298 | 3767.8713 | 1873.143 | 1282 | 2568226.541 | 674331.48 | 305884.2519 | 0 | 1344916.674
900 | 1814.753 | 4197.7809 | 1885.174 | 4086.3741 | 1814.753 | 1281.9 | 2495452.3622 | 653311.08 | 296349.1649 | 0 | 1303174.1293
901 | 1605.764 | 4069.6662 | 1668.0753 | 3961.6594 | 1605.764 | 1317.1 | 2267043.3585 | 578075.04 | 262221.2612 | 0 | 1096576.2356
902 | 1656.929 | 3973.5809 | 1721.2257 | 3868.1242 | 1656.929 | 1306 | 2318809.3365 | 596494.44 | 270576.5057 | 0 | 1149908.726
903 | 1959.966 | 3414.7735 | 2036.022 | 3324.1473 | 1959.966 | 1344.6 | 2808061.2013 | 705587.76 | 320062.4478 | 0 | 1284561.7164
904 | 1925.128 | 2556.2087 | 1999.8321 | 2488.3683 | 1925.128 | 1513.45 | 3088053.0329 | 693046.08 | 314373.4024 | 0 | 936671.0284
905 | 1644.797 | 1399.8611 | 1399.8611 | 1362.7095 | 1362.7095 | 1569.45 | 2262437.547 | 490575.4294 | 222530.4656 | 517066.3397 | 574303.7562
906 | 1796.832 | 234.1653 | 234.1653 | 227.9507 | 227.9507 | 1582.25 | 381176.8872 | 82062.2411 | 37224.3444 | 2875759.4785 | 93211.722
907 | 1564.005 | 0 | 0 | 0 | 0 | 1615.45 | 0 | 0 | 0 | 5314488.99 | 0
908 | 1423.2 | 0 | 0 | 0 | 0 | 1464.6 | 0 | 0 | 0 | 4836033.6 | 0
909 | 1762.4 | 0 | 0 | 0 | 0 | 1459.95 | 0 | 0 | 0 | 5988635.2 | 0
910 | 1525.6 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1826.55 | 598573.8134 | 111351.8261 | 50510.4255 | 4132951.2863 | 53053.8453
911 | 1706.4 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1547.2 | 984096.9895 | 215514.4963 | 97759.7701 | 3764129.8159 | 268057.6
912 | 526.4 | 0 | 0 | 0 | 0 | 1481.75 | 0 | 0 | 0 | 964891.2 | 0
913 | 477.6 | 0 | 0 | 0 | 0 | 1459.95 | 0 | 0 | 0 | 568344 | 0
914 | 487.2 | 0 | 0 | 0 | 0 | 1332.75 | 0 | 0 | 0 | 579768 | 0
915 | 450.4 | 0 | 0 | 0 | 0 | 1165.95 | 0 | 0 | 0 | 535976 | 0
916 | 410.4 | 0 | 0 | 0 | 0 | 1159.7 | 0 | 0 | 0 | 488376 | 0
917 | 498.4 | 0 | 0 | 0 | 0 | 1166.6 | 0 | 0 | 0 | 593096 | 0
918 | 480.8 | 0 | 0 | 0 | 0 | 1192.2 | 0 | 0 | 0 | 572152 | 0
919 | 402.4 | 16.0506 | 16.0506 | 15.6246 | 15.6246 | 1124 | 18715.5003 | 5624.8555 | 2551.497 | 708959.3105 | 13397.544
920 | 183.582 | 551.4931 | 190.7059 | 536.8568 | 183.582 | 1211.85 | 236652.8297 | 66089.52 | 29978.9406 | 0 | 144690.1533
921 | 1361.436 | 1977.4895 | 1414.2662 | 1925.008 | 1361.436 | 1319.7 | 1919489.8113 | 490116.96 | 222322.4988 | 0 | 926184.9108
922 | 1498.899 | 3227.8375 | 1557.0634 | 3142.1724 | 1498.899 | 1364.45 | 2190659.4215 | 539603.64 | 244770.2067 | 0 | 952625.2595
923 | 1608.087 | 3743.657 | 1670.4884 | 3644.3024 | 1608.087 | 345.9 | 597638.1649 | 578911.32 | 262600.6071 | 0 | 2659936.7067
924 | 1399.808 | 4028.4339 | 1454.1272 | 3921.5215 | 1399.808 | 339.95 | 512008.6902 | 503930.88 | 228588.6464 | 0 | 2323751.2704
925 | 1724.006 | 4068.2347 | 1790.9056 | 3960.2659 | 1724.006 | 328.1 | 608433.9322 | 620642.16 | 281530.1798 | 0 | 2882365.6314
926 | 1255.265 | 3865.9638 | 1303.9752 | 3763.3632 | 1255.265 | 339.6 | 459634.8508 | 451895.4 | 204984.7745 | 0 | 2084242.006
927 | 1125.5 | 3392.247 | 1169.1747 | 3302.2186 | 1125.5 | 355.6 | 428469.9781 | 405180 | 183794.15 | 0 | 1850772.2
928 | 1614.058 | 2619.6007 | 1676.6911 | 2550.0779 | 1614.058 | 1350 | 2318071.0324 | 581060.88 | 263575.6714 | 0 | 1049137.7
929 | 1453.859 | 1498.347 | 1498.347 | 1458.5817 | 1453.859 | 1369.35 | 2113159.4476 | 523389.24 | 237415.1747 | 0 | 900396.6632
930 | 1370.109 | 228.9962 | 228.9962 | 222.9188 | 222.9188 | 1568.6 | 370762.8339 | 80250.7544 | 36402.6339 | 2102799.706 | 94132.7742
931 | 1452.169 | 0 | 0 | 0 | 0 | 1615.45 | 0 | 0 | 0 | 4934470.262 | 0
932 | 1032 | 0 | 0 | 0 | 0 | 1535.85 | 0 | 0 | 0 | 3506736 | 0
933 | 1212.8 | 0 | 0 | 0 | 0 | 1475.9 | 0 | 0 | 0 | 4121094.4 | 0
934 | 1396.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1776.55 | 585121.0411 | 111351.8261 | 50510.4255 | 3695288.8863 | 68347.5453
935 | 964 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1681.35 | 1071927.078 | 215514.4963 | 97759.7701 | 1241454.6159 | 188640.8
936 | 1384.8 | 0 | 0 | 0 | 0 | 1538.7 | 0 | 0 | 0 | 2538338.4 | 0
937 | 1120 | 0 | 0 | 0 | 0 | 1616.9 | 0 | 0 | 0 | 2052960 | 0
938 | 1568.8 | 0 | 0 | 0 | 0 | 1264.75 | 0 | 0 | 0 | 2875610.4 | 0
939 | 1411.2 | 0 | 0 | 0 | 0 | 261.95 | 0 | 0 | 0 | 2586729.6 | 0
940 | 1482.4 | 0 | 0 | 0 | 0 | 260.7 | 0 | 0 | 0 | 2717239.2 | 0
941 | 1182.4 | 0 | 0 | 0 | 0 | 262.6 | 0 | 0 | 0 | 2167339.2 | 0
942 | 1132 | 0 | 0 | 0 | 0 | 269.65 | 0 | 0 | 0 | 2074956 | 0
943 | 1137.6 | 35.0939 | 35.0939 | 34.1626 | 34.1626 | 283.95 | 10359.1872 | 12298.524 | 5578.7472 | 2022600.8151 | 57384.712
944 | 182.01 | 282.4531 | 189.0729 | 274.9569 | 182.01 | 1275.4 | 246690.6676 | 65523.6 | 29722.233 | 0 | 131884.446
945 | 481.147 | 1349.4344 | 499.8178 | 1313.6211 | 481.147 | 1369.7 | 702071.6758 | 173212.92 | 78571.3051 | 0 | 303266.9541
946 | 455.687 | 2558.3486 | 473.3698 | 2490.4514 | 455.687 | 1387.2 | 676353.9268 | 164047.32 | 74413.6871 | 0 | 279244.9936
947 | 498.735 | 3175.2563 | 518.0883 | 3090.9867 | 498.735 | 345.9 | 185173.1603 | 179544.6 | 81443.4255 | 0 | 824957.5635
948 | 415.99 | 3638.8073 | 432.1324 | 3542.2354 | 415.99 | 339.95 | 152330.1096 | 149756.4 | 67931.167 | 0 | 690564.1995
949 | 320.018 | 3708.1133 | 332.4362 | 3609.702 | 320.018 | 1168.15 | 402586.71 | 115206.48 | 52258.9394 | 0 | 266206.9733
950 | 335.666 | 3213.0231 | 348.6914 | 3127.7512 | 335.666 | 1275.7 | 460491.9998 | 120839.76 | 54814.2578 | 0 | 243122.8838
951 | 408.03 | 2239.7087 | 423.8635 | 2180.2681 | 408.03 | 1291.7 | 564949.4956 | 146890.8 | 66631.299 | 0 | 289007.649
952 | 329.489 | 2033.1923 | 342.2747 | 1979.2325 | 329.489 | 769.2 | 271156.0089 | 118616.04 | 53805.5537 | 0 | 405535.0612
953 | 413.609 | 1192.5167 | 429.659 | 1160.8679 | 413.609 | 384.35 | 169125.3097 | 148899.24 | 67542.3497 | 0 | 668247.3808
954 | 285.122 | 276.3844 | 276.3844 | 269.0493 | 269.0493 | 766.6 | 218544.3468 | 96857.7481 | 43935.7507 | 29461.2586 | 324825.7572
955 | 304.539 | 0 | 0 | 0 | 0 | 1459 | 0 | 0 | 0 | 558219.987 | 0
956 | 261.6 | 0 | 0 | 0 | 0 | 1414.05 | 0 | 0 | 0 | 479512.8 | 0
957 | 204 | 0 | 0 | 0 | 0 | 1487.65 | 0 | 0 | 0 | 373932 | 0
958 | 331.2 | 104.4539 | 104.4539 | 101.6817 | 101.6817 | 1536.65 | 166160.3738 | 36605.4284 | 16604.6291 | 420706.9603 | 46314.6126
959 | 296.8 | 308.3172 | 308.3172 | 300.1347 | 296.8 | 1806.35 | 571448.7102 | 106848 | 48467.44 | 0 | 57475.32
960 | 302.4 | 314.1346 | 314.1346 | 305.7976 | 302.4 | 1798.7 | 579566.4767 | 108864 | 49381.92 | 0 | 60873.12
961 | 324.8 | 0 | 0 | 0 | 0 | 897.55 | 0 | 0 | 0 | 386512 | 0
962 | 296.8 | 0 | 0 | 0 | 0 | 731.45 | 0 | 0 | 0 | 353192 | 0
963 | 296.8 | 0 | 0 | 0 | 0 | 255.75 | 0 | 0 | 0 | 353192 | 0
964 | 316 | 0 | 0 | 0 | 0 | 254.05 | 0 | 0 | 0 | 376040 | 0
965 | 227.2 | 0 | 0 | 0 | 0 | 254 | 0 | 0 | 0 | 270368 | 0
966 | 276 | 0 | 0 | 0 | 0 | 258.35 | 0 | 0 | 0 | 328440 | 0
967 | 256.8 | 266.7651 | 266.7651 | 259.6853 | 256.8 | 268.45 | 73776.1986 | 92448 | 41935.44 | 0 | 444662.04
968 | 246.146 | 519.392 | 255.6976 | 505.6076 | 246.146 | 288 | 75328.6422 | 88612.56 | 40195.6418 | 0 | 421401.952
969 | 460.316 | 1925.5233 | 478.1784 | 1874.4209 | 460.316 | 311.85 | 152964.653 | 165713.76 | 75169.6028 | 0 | 777082.4554
970 | 1172.832 | 3178.568 | 1218.3435 | 3094.2105 | 1172.832 | 316.9 | 398471.1422 | 422219.52 | 191523.4656 | 0 | 1973993.5392
971 | 1566.318 | 3658.4657 | 1627.0986 | 3561.372 | 1566.318 | 317.5 | 534163.7748 | 563874.48 | 255779.7294 | 0 | 2635330.035
972 | 1214.229 | 3937.1926 | 1261.3469 | 3832.7016 | 1214.229 | 314.55 | 411583.2856 | 437122.44 | 198283.5957 | 0 | 2046522.2681
973 | 1567.117 | 3903.3639 | 1627.9286 | 3799.7707 | 1567.117 | 305.65 | 517750.2449 | 564162.12 | 255910.2061 | 0 | 2655244.6889
974 | 1509.312 | 3400.6333 | 1567.8805 | 3310.3823 | 1509.312 | 312.4 | 509499.7492 | 543352.32 | 246470.6496 | 0 | 2547114.9312
975 | 1604.899 | 2821.1963 | 1667.1767 | 2746.3233 | 1604.899 | 322.5 | 560053.4721 | 577763.64 | 262080.0067 | 0 | 2692218.0725
976 | 1215.644 | 2121.3754 | 1262.8168 | 2065.0752 | 1215.644 | 334.85 | 440055.4538 | 437631.84 | 198514.6652 | 0 | 2024229.6066
977 | 1300.307 | 1055.4537 | 1055.4537 | 1027.4425 | 1027.4425 | 345.95 | 382338.7402 | 369879.3025 | 167781.3614 | 500160.6157 | 1663492.9715
978 | 1151.05 | 214.2462 | 214.2462 | 208.5602 | 208.5602 | 349.9 | 77977.4937 | 75081.6829 | 34057.8856 | 1727583.7481 | 336866.2649
979 | 1456.677 | 0 | 0 | 0 | 0 | 354.05 | 0 | 0 | 0 | 4949788.446 | 0
980 | 1494.4 | 0 | 0 | 0 | 0 | 327.45 | 0 | 0 | 0 | 5077971.2 | 0
981 | 1808.8 | 0 | 0 | 0 | 0 | 311.25 | 0 | 0 | 0 | 6146302.4 | 0
982 | 1650.4 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1423.35 | 471113.762 | 111351.8261 | 50510.4255 | 4557021.6863 | 176382.2421
983 | 1209.6 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1335.6 | 856598.3442 | 215514.4963 | 97759.7701 | 2076003.4159 | 393324.8
984 | 1028 | 0 | 0 | 0 | 0 | 1218.95 | 0 | 0 | 0 | 1884324 | 0
985 | 1335.2 | 0 | 0 | 0 | 0 | 652.6 | 0 | 0 | 0 | 1588888 | 0
986 | 1325.6 | 0 | 0 | 0 | 0 | 253.1 | 0 | 0 | 0 | 1577464 | 0
987 | 1358.4 | 0 | 0 | 0 | 0 | 248.8 | 0 | 0 | 0 | 1616496 | 0
988 | 1510.4 | 0 | 0 | 0 | 0 | 247.6 | 0 | 0 | 0 | 1797376 | 0
989 | 1220.8 | 0 | 0 | 0 | 0 | 248.3 | 0 | 0 | 0 | 1452752 | 0
990 | 1460.8 | 0 | 0 | 0 | 0 | 249.75 | 0 | 0 | 0 | 1738352 | 0
991 | 1494.4 | 48.2348 | 48.2348 | 46.9547 | 46.9547 | 251.8 | 12678.5057 | 16903.6902 | 7667.7017 | 2653167.244 | 80349.0202
992 | 1213.91 | 1068.5592 | 1068.5592 | 1040.2003 | 1040.2003 | 1310.35 | 1453315.9701 | 374472.0912 | 169864.7014 | 318409.9658 | 702199.5611
993 | 1285.355 | 1631.981 | 1335.2329 | 1588.6691 | 1285.355 | 1275.05 | 1754393.8288 | 462727.8 | 209898.4715 | 0 | 931818.1073
994 | 1854.487 | 2672.3491 | 1926.4499 | 2601.4264 | 1854.487 | 1278.8 | 2552075.168 | 667615.32 | 302837.7271 | 0 | 1337456.0244
995 | 1700.494 | 3285.7592 | 1766.4812 | 3198.5569 | 1700.494 | 1260.05 | 2305885.194 | 612177.84 | 277690.6702 | 0 | 1258280.5353
996 | 1593.166 | 3612.1236 | 1654.9884 | 3516.2598 | 1593.166 | 738.5 | 1263713.0229 | 573539.76 | 260164.0078 | 0 | 2009778.909
997 | 1302.813 | 2784.0985 | 1353.3683 | 2710.2101 | 1302.813 | 282.5 | 396993.9793 | 469012.68 | 212749.3629 | 0 | 2237581.3275
998 | 1470.149 | 2995.6002 | 1527.1978 | 2916.0986 | 1470.149 | 289.05 | 458182.0847 | 529253.64 | 240075.3317 | 0 | 2515351.4315
999 | 1044.668 | 2893.7257 | 1085.2061 | 2816.9278 | 1044.668 | 298.65 | 335031.5053 | 376080.48 | 170594.2844 | 0 | 1777345.9018
1000 | 1161.083 | 2164.3705 | 1206.1385 | 2106.9293 | 1161.083 | 308.5 | 384754.8802 | 417989.88 | 189604.8539 | 0 | 1963971.8945
1001 | 1434.037 | 1171.0373 | 1171.0373 | 1139.9586 | 1139.9586 | 320.4 | 390625.8691 | 410385.1065 | 186155.2441 | 539045.654 | 1874171.5824
1002 | 1519.101 | 158.6369 | 158.6369 | 154.4268 | 154.4268 | 833.75 | 136854.4403 | 55593.6389 | 25217.8923 | 2501447.8549 | 176290.35
1003 | 1470.4 | 0 | 0 | 0 | 0 | 1512.15 | 0 | 0 | 0 | 4996419.2 | 0
1004 | 1118.4 | 0 | 0 | 0 | 0 | 1743.45 | 0 | 0 | 0 | 3800323.2 | 0
1005 | 1686.4 | 0 | 0 | 0 | 0 | 1509.85 | 0 | 0 | 0 | 5730387.2 | 0
1006 | 1632 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1388.35 | 457096.4947 | 111351.8261 | 50510.4255 | 4494498.4863 | 187087.8321
1007 | 1343.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1266.9 | 808077.6169 | 215514.4963 | 97759.7701 | 2529976.2159 | 433995.2
1008 | 1206.4 | 0 | 0 | 0 | 0 | 956.05 | 0 | 0 | 0 | 2211331.2 | 0
1009 | 1653.6 | 0 | 0 | 0 | 0 | 1123.85 | 0 | 0 | 0 | 1967784 | 0
1010 | 1780 | 0 | 0 | 0 | 0 | 1064.9 | 0 | 0 | 0 | 2118200 | 0
1011 | 1225.6 | 0 | 0 | 0 | 0 | 1159.95 | 0 | 0 | 0 | 1458464 | 0
1012 | 1333.6 | 0 | 0 | 0 | 0 | 1158.7 | 0 | 0 | 0 | 1586984 | 0
1013 | 1466.4 | 0 | 0 | 0 | 0 | 1111.1 | 0 | 0 | 0 | 1745016 | 0
1014 | 1376 | 0 | 0 | 0 | 0 | 1118.15 | 0 | 0 | 0 | 1637440 | 0
1015 | 1212 | 31.1195 | 31.1195 | 30.2936 | 30.2936 | 1181.95 | 38169.2288 | 10905.6888 | 4946.9416 | 2166067.8679 | 24257.6367
1016 | 1119.408 | 910.4718 | 910.4718 | 886.3084 | 886.3084 | 1153.9 | 1084656.4094 | 319071.0319 | 144734.1653 | 427271.5265 | 734042.516
1017 | 1135.205 | 1321.6557 | 1179.2563 | 1286.5797 | 1135.205 | 1234.95 | 1494525.7472 | 408673.8 | 185378.9765 | 0 | 868488.5853
1018 | 1502.098 | 2289.6659 | 1560.3865 | 2228.8994 | 1502.098 | 1263.95 | 2040523.8838 | 540755.28 | 245292.6034 | 0 | 1105619.2329
1019 | 1740.14 | 2935.3838 | 1807.6657 | 2857.4803 | 1740.14 | 1144.9 | 2128988.1904 | 626450.4 | 284164.862 | 0 | 1487993.714
1020 | 1403.041 | 3269.3066 | 1457.4857 | 3182.541 | 1403.041 | 1138.95 | 1712487.2107 | 505094.76 | 229116.5953 | 0 | 1208088.453
1021 | 1200.195 | 3246.1298 | 1246.7683 | 3159.9793 | 1200.195 | 1174.15 | 1533180.5988 | 432070.2 | 195991.8435 | 0 | 991181.0407
1022 | 1044.046 | 3112.1655 | 1084.5599 | 3029.5704 | 1044.046 | 1138.6 | 1289013.7414 | 375856.56 | 170492.7118 | 0 | 899341.2244
1023 | 1298.188 | 2816.5903 | 1348.5639 | 2741.8395 | 1298.188 | 755.1 | 1060155.6081 | 467347.68 | 211994.1004 | 0 | 1616114.2412
1024 | 1559.024 | 2036.9528 | 1619.5215 | 1982.8931 | 1559.024 | 369.7 | 619964.2995 | 561248.64 | 254588.6192 | 0 | 2541676.8272
1025 | 1238.191 | 1080.7891 | 1080.7891 | 1052.1055 | 1052.1055 | 384.35 | 432167.1493 | 378757.9901 | 171808.8327 | 341094.6701 | 1663877.1525
1026 | 1380.315 | 194.7655 | 194.7655 | 189.5965 | 189.5965 | 1190.65 | 239257.1678 | 68254.7515 | 30961.1137 | 2182586.9518 | 150204.0291
1027 | 886.366 | 0 | 0 | 0 | 0 | 1274.4 | 0 | 0 | 0 | 3011871.668 | 0
1028 | 1113.6 | 0 | 0 | 0 | 0 | 1325.6 | 0 | 0 | 0 | 3784012.8 | 0
1029 | 1129.6 | 0 | 0 | 0 | 0 | 1262.6 | 0 | 0 | 0 | 3838380.8 | 0
1030 | 1440.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1312.55 | 432555.3767 | 111351.8261 | 50510.4255 | 3844800.8863 | 210273.0813
1031 | 1332.8 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1224.9 | 782159.0394 | 215514.4963 | 97759.7701 | 2494637.0159 | 458859.2
1032 | 138.4 | 0 | 0 | 0 | 0 | 1250.25 | 0 | 0 | 0 | 253687.2 | 0
1033 | 97.6 | 0 | 0 | 0 | 0 | 1336.45 | 0 | 0 | 0 | 116144 | 0
1034 | 94.4 | 0 | 0 | 0 | 0 | 1283.4 | 0 | 0 | 0 | 112336 | 0
1035 | 103.2 | 0 | 0 | 0 | 0 | 1278.95 | 0 | 0 | 0 | 122808 | 0
1036 | 92.8 | 0 | 0 | 0 | 0 | 1278.2 | 0 | 0 | 0 | 110432 | 0
1037 | 98.4 | 0 | 0 | 0 | 0 | 1311.6 | 0 | 0 | 0 | 117096 | 0
1038 | 89.6 | 0 | 0 | 0 | 0 | 1324.95 | 0 | 0 | 0 | 106624 | 0
1039 | 84.8 | 42.403 | 42.403 | 41.2776 | 41.2776 | 1332.95 | 58944.4386 | 14859.9429 | 6740.6352 | 79776.5238 | 26952.1552
1040 | 86.437 | 320.7943 | 89.7912 | 312.2806 | 86.437 | 1369.45 | 126526.4705 | 31117.32 | 14115.1621 | 0 | 54502.8503
1041 | 660.137 | 1583.4283 | 685.7545 | 1541.4049 | 660.137 | 1356.4 | 961807.9551 | 237649.32 | 107800.3721 | 0 | 424864.1732
1042 | 1046.053 | 2879.8046 | 1086.6448 | 2803.3762 | 1046.053 | 1314.4 | 1496533.4787 | 376579.08 | 170820.4549 | 0 | 717173.9368
1043 | 1011.485 | 3258.744 | 1050.7354 | 3172.2587 | 1011.485 | 1288.45 | 1394616.8017 | 364134.6 | 165175.5005 | 0 | 719722.1517
1044 | 1077.866 | 3573.1383 | 1119.6923 | 3478.3091 | 1077.866 | 1324.95 | 1531706.0714 | 388031.76 | 176015.5178 | 0 | 727613.4433
1045 | 1280.894 | 3440.8423 | 1330.5988 | 3349.5242 | 1280.894 | 1313.1 | 1831974.0539 | 461121.84 | 209169.9902 | 0 | 879846.0886
1046 | 1305.495 | 3363.5989 | 1356.1544 | 3274.3308 | 1305.495 | 1300.15 | 1846608.7595 | 469978.2 | 213187.3335 | 0 | 913650.6757
1047 | 1222.683 | 2783.1106 | 1270.1289 | 2709.2484 | 1222.683 | 823.7 | 1089807.5841 | 440165.88 | 199664.1339 | 0 | 1438242.0129
1048 | 1378.71 | 2300.9723 | 1432.2105 | 2239.9057 | 1378.71 | 837.8 | 1241933.9757 | 496335.6 | 225143.343 | 0 | 1602336.762
1049 | 1442.884 | 1297.7923 | 1297.7923 | 1263.3496 | 1263.3496 | 1426.35 | 1923365.8184 | 454805.8477 | 206304.9859 | 329086.5973 | 709389.9313
1050 | 1317.715 | 223.0407 | 223.0407 | 217.1213 | 217.1213 | 1627.65 | 375112.5056 | 78163.6858 | 35455.9164 | 2017388.1616 | 79134.8008
1051 | 1407.2 | 0 | 0 | 0 | 0 | 1540.45 | 0 | 0 | 0 | 4781665.6 | 0
1052 | 1616.8 | 0 | 0 | 0 | 0 | 1363.9 | 0 | 0 | 0 | 5493886.4 | 0
1053 | 1705.6 | 0 | 0 | 0 | 0 | 1363.15 | 0 | 0 | 0 | 5795628.8 | 0
1054 | 1624 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1476.55 | 485519.1105 | 111351.8261 | 50510.4255 | 4467314.4863 | 160109.7453
1055 | 1382.4 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1516.4 | 967568.6915 | 215514.4963 | 97759.7701 | 2663177.8159 | 286291.2
1056 | 136.8 | 0 | 0 | 0 | 0 | 1431.75 | 0 | 0 | 0 | 250754.4 | 0
1057 | 104.8 | 0 | 0 | 0 | 0 | 1507.9 | 0 | 0 | 0 | 124712 | 0
1058 | 96.8 | 0 | 0 | 0 | 0 | 1434.9 | 0 | 0 | 0 | 115192 | 0
1059 | 100 | 0 | 0 | 0 | 0 | 1430.95 | 0 | 0 | 0 | 119000 | 0
1060 | 98.4 | 0 | 0 | 0 | 0 | 1429.7 | 0 | 0 | 0 | 117096 | 0
1061 | 101.6 | 0 | 0 | 0 | 0 | 1431.6 | 0 | 0 | 0 | 120904 | 0
1062 | 95.2 | 0 | 0 | 0 | 0 | 1438.65 | 0 | 0 | 0 | 113288 | 0
1063 | 92.8 | 39.0736 | 39.0736 | 38.0366 | 38.0366 | 1440.75 | 58648.9938 | 13693.1795 | 6211.3784 | 100381.2944 | 20821.996
1064 | 85.97 | 344.5269 | 89.306 | 335.3833 | 85.97 | 1476.85 | 135623.8631 | 30949.2 | 14038.901 | 0 | 44975.2055
1065 | 932.616 | 1707.527 | 968.8059 | 1662.2102 | 932.616 | 1401 | 1403120.7268 | 335741.76 | 152296.1928 | 0 | 558636.984
1066 | 1383.414 | 3031.037 | 1437.097 | 2950.5949 | 1383.414 | 1331.9 | 1992938.8351 | 498029.04 | 225911.5062 | 0 | 924258.8934
1067 | 1261.111 | 3692.1157 | 1310.0481 | 3594.1289 | 1261.111 | 1330.9 | 1802713.6312 | 453999.96 | 205939.4263 | 0 | 843809.3701
1068 | 1457.305 | 3997.5918 | 1513.8554 | 3891.4979 | 1457.305 | 1325.45 | 2075040.225 | 524629.8 | 237977.9065 | 0 | 983025.0877
1069 | 1348.064 | 4015.1445 | 1400.3753 | 3908.5847 | 1348.064 | 1389.7 | 2027191.123 | 485303.04 | 220138.8512 | 0 | 822723.4592
1070 | 1417.335 | 3699.8454 | 1472.3343 | 3601.6535 | 1417.335 | 1325.1 | 2031980.5653 | 510240.6 | 231450.8055 | 0 | 956559.3915
1071 | 1553.989 | 3178.9638 | 1614.2912 | 3094.5958 | 1553.989 | 1340.6 | 2250569.1164 | 559436.04 | 253766.4037 | 0 | 1024700.3466
1072 | 1478.554 | 2378.0848 | 1535.9289 | 2314.9717 | 1478.554 | 1450 | 2298741.8435 | 532279.44 | 241447.8682 | 0 | 813204.7
1073 | 1282.839 | 1304.6162 | 1304.6162 | 1269.9924 | 1269.9924 | 1518.35 | 2049337.1523 | 457197.2577 | 207389.7561 | 23547.8497 | 598752.6012
1074 | 1716.587 | 219.1608 | 219.1608 | 213.3444 | 213.3444 | 1572.6 | 355069.1734 | 76803.9786 | 34839.1381 | 2755443.7133 | 89254.7968
1075 | 1229.933 | 0 | 0 | 0 | 0 | 1630.3 | 0 | 0 | 0 | 4179312.334 | 0
1076 | 828.8 | 0 | 0 | 0 | 0 | 1581.1 | 0 | 0 | 0 | 2816262.4 | 0
1077 | 1254.4 | 0 | 0 | 0 | 0 | 1555.65 | 0 | 0 | 0 | 4262451.2 | 0
1078 | 1271.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1712.05 | 561353.0247 | 111351.8261 | 50510.4255 | 3268500.0863 | 88076.4183
1079 | 1333.6 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1764.7 | 1122634.3385 | 215514.4963 | 97759.7701 | 2497355.4159 | 139297.6
1080 | 1302.4 | 0 | 0 | 0 | 0 | 1622.05 | 0 | 0 | 0 | 2387299.2 | 0
1081 | 1362.4 | 0 | 0 | 0 | 0 | 1384.4 | 0 | 0 | 0 | 1621256 | 0
1082 | 933.6 | 0 | 0 | 0 | 0 | 1499 | 0 | 0 | 0 | 1110984 | 0
1083 | 1361.6 | 0 | 0 | 0 | 0 | 1495.05 | 0 | 0 | 0 | 1620304 | 0
1084 | 1337.6 | 0 | 0 | 0 | 0 | 1493.75 | 0 | 0 | 0 | 1591744 | 0
1085 | 996 | 0 | 0 | 0 | 0 | 1494.45 | 0 | 0 | 0 | 1185240 | 0
1086 | 1271.2 | 0 | 0 | 0 | 0 | 1478.5 | 0 | 0 | 0 | 1512728 | 0
1087 | 1043.2 | 49.5531 | 49.5531 | 48.238 | 48.238 | 1492.8 | 76357.4547 | 17365.663 | 7877.2577 | 1823765.4325 | 23948.9696
1088 | 860.551 | 893.9445 | 893.9445 | 870.2197 | 860.551 | 1539.7 | 1406735.3796 | 309798.36 | 140527.9783 | 0 | 396111.6253
1089 | 1094.398 | 1628.5685 | 1136.8658 | 1585.3472 | 1094.398 | 1571.25 | 1828003.8626 | 393983.28 | 178715.1934 | 0 | 469223.1425
1090 | 1122.775 | 2867.1416 | 1166.344 | 2791.0492 | 1122.775 | 1471.2 | 1763163.2411 | 404199 | 183349.1575 | 0 | 593723.42
1091 | 1142.288 | 3672.1384 | 1186.6142 | 3574.6819 | 1142.288 | 1369.2 | 1669775.7408 | 411223.68 | 186535.6304 | 0 | 720555.2704
1092 | 987.833 | 3975.8164 | 1026.1656 | 3870.3004 | 987.833 | 1401.55 | 1477074.5218 | 355619.88 | 161313.1289 | 0 | 591168.6589
1093 | 1098.997 | 4011.4308 | 1141.6433 | 3904.9696 | 1098.997 | 1451.45 | 1703939.4028 | 395638.92 | 179466.2101 | 0 | 602854.8043
1094 | 1323.29 | 3765.125 | 1374.6399 | 3665.2006 | 1323.29 | 1359.95 | 1925548.9754 | 476384.4 | 216093.257 | 0 | 846971.7645
1095 | 1200.589 | 3230.2205 | 1247.1776 | 3144.4922 | 1200.589 | 1244.65 | 1592352.2412 | 432212.04 | 196056.1837 | 0 | 906864.9012
1096 | 1175.229 | 1988.3751 | 1220.8335 | 1935.6047 | 1175.229 | 1393 | 1740407.9777 | 423082.44 | 191914.8957 | 0 | 713364.003
1097 | 1183.22 | 1303.0549 | 1229.1346 | 1268.4725 | 1183.22 | 1445.95 | 1815356.3699 | 425959.2 | 193219.826 | 0 | 655563.041
1098 | 1286.45 | 207.6404 | 207.6404 | 202.1298 | 202.1298 | 1518.9 | 324629.4157 | 72766.7222 | 33007.7937 | 1987558.9559 | 95187.5594
1099 | 1205.541 | 0 | 0 | 0 | 0 | 1608.45 | 0 | 0 | 0 | 4096428.318 | 0
1100 | 1044 | 0 | 0 | 0 | 0 | 1574.1 | 0 | 0 | 0 | 3547512 | 0
1101 | 1465.6 | 0 | 0 | 0 | 0 | 1431.6 | 0 | 0 | 0 | 4980108.8 | 0
1102 | 1054.4 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1537.55 | 502961.9371 | 111351.8261 | 50510.4255 | 2531813.6863 | 141451.4313
1103 | 1262.4 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1494.35 | 946720.4496 | 215514.4963 | 97759.7701 | 2255417.8159 | 299344.8
1104 | 936 | 0 | 0 | 0 | 0 | 1351.3 | 0 | 0 | 0 | 1715688 | 0
1105 | 1169.6 | 0 | 0 | 0 | 0 | 1360.4 | 0 | 0 | 0 | 2143876.8 | 0
1106 | 1276 | 0 | 0 | 0 | 0 | 1247.95 | 0 | 0 | 0 | 2338908 | 0
1107 | 1006.4 | 0 | 0 | 0 | 0 | 1246.95 | 0 | 0 | 0 | 1844731.2 | 0
1108 | 1429.6 | 0 | 0 | 0 | 0 | 1245.7 | 0 | 0 | 0 | 2620456.8 | 0
1109 | 1362.4 | 0 | 0 | 0 | 0 | 1247.6 | 0 | 0 | 0 | 2497279.2 | 0
1110 | 1094.4 | 0 | 0 | 0 | 0 | 1254.65 | 0 | 0 | 0 | 2006035.2 | 0
1111 | 1244 | 62.2628 | 62.2628 | 60.6104 | 60.6104 | 1268.95 | 81529.1046 | 21819.7506 | 9897.6813 | 2169153.1031 | 43371.7344
1112 | 182.026 | 476.0894 | 189.0895 | 463.4543 | 182.026 | 1369.45 | 264185.3747 | 65529.36 | 29724.8458 | 0 | 114776.4943
1113 | 152.29 | 1863.6334 | 158.1996 | 1814.1736 | 152.29 | 1363.2 | 220502.0202 | 54824.4 | 24868.957 | 0 | 96978.272
1114 | 181.165 | 3139.4591 | 188.1951 | 3056.1396 | 181.165 | 1370.2 | 265328.5094 | 65219.4 | 29584.2445 | 0 | 114097.717
1115 | 170.605 | 3671.5889 | 177.2253 | 3574.1469 | 170.605 | 1287.9 | 234478.1776 | 61417.8 | 27859.7965 | 0 | 121487.8205
1116 | 185.42 | 3956.9392 | 192.6152 | 3851.9242 | 185.42 | 1324.95 | 262038.2763 | 66751.2 | 30279.086 | 0 | 125167.771
1117 | 195.463 | 3986.7456 | 203.0479 | 3880.9396 | 195.463 | 1313.1 | 272784.2699 | 70366.68 | 31919.1079 | 0 | 134263.5347
1118 | 197.058 | 3770.5891 | 204.7048 | 3670.5197 | 197.058 | 1318.7 | 276782.8142 | 70940.88 | 32179.5714 | 0 | 134255.6154
1119 | 129.537 | 2961.7788 | 134.5637 | 2883.1748 | 129.537 | 1266.65 | 174999.1795 | 46633.32 | 21153.3921 | 0 | 94995.9589
1120 | 177.796 | 2244.5465 | 184.6953 | 2184.9774 | 177.796 | 1115.75 | 210415.3647 | 64006.56 | 29034.0868 | 0 | 157216.113
1121 | 117.348 | 1369.2444 | 121.9017 | 1332.9054 | 117.348 | 1310.45 | 162422.1249 | 42245.28 | 19162.9284 | 0 | 80917.3134
1122 | 99.261 | 257.4781 | 103.1128 | 250.6448 | 99.261 | 1323.65 | 138783.1808 | 35733.96 | 16209.3213 | 0 | 67135.1773
1123 | 110.145 | 114.4191 | 114.4191 | 111.3825 | 110.145 | 1484.4 | 172213.4903 | 39652.2 | 17986.6785 | 0 | 56790.762
1124 | 108 | 112.1909 | 112.1909 | 109.2134 | 108 | 1450.6 | 165104.908 | 38880 | 17636.4 | 0 | 59335.2
1125 | 100 | 103.8805 | 103.8805 | 101.1235 | 100 | 1368.9 | 144028.0745 | 36000 | 16330 | 0 | 63110
1126 | 91.2 | 94.739 | 94.739 | 92.2247 | 91.2 | 1350.85 | 129431.5705 | 32832 | 14892.96 | 0 | 59202.48
1127 | 100 | 103.8805 | 103.8805 | 101.1235 | 100 | 1292.85 | 136326.2097 | 36000 | 16330 | 0 | 70715
1128 | 93.6 | 97.2321 | 97.2321 | 94.6516 | 93.6 | 1313.5 | 129840.0209 | 33696 | 15284.88 | 0 | 64256.4
1129 | 98.4 | 0 | 0 | 0 | 0 | 1472.55 | 0 | 0 | 0 | 117096 | 0
1130 | 90.4 | 0 | 0 | 0 | 0 | 1446.75 | 0 | 0 | 0 | 107576 | 0
1131 | 96.8 | 18.0014 | 18.0014 | 17.5237 | 17.5237 | 1380.05 | 25626.5628 | 6308.5316 | 2861.62 | 94338.7983 | 10743.1136
1132 | 91.2 | 94.739 | 94.739 | 92.2247 | 91.2 | 1441.05 | 139315.4374 | 32832 | 14892.96 | 0 | 50976.24
1133 | 96.8 | 100.5563 | 100.5563 | 97.8876 | 96.8 | 1441 | 147907.0133 | 34848 | 15807.44 | 0 | 54111.2
1134 | 89.6 | 93.0769 | 93.0769 | 90.6067 | 89.6 | 1445.35 | 137091.731 | 32256 | 14631.68 | 0 | 49696.64
1135 | 92.8 | 96.4011 | 96.4011 | 93.8426 | 92.8 | 1455.45 | 142722.2965 | 33408 | 15154.24 | 0 | 50534.24
1136 | 86.74 | 679.2412 | 90.1059 | 661.2145 | 86.74 | 1474.05 | 135058.0328 | 31226.4 | 14164.642 | 0 | 45620.903
1137 | 858.247 | 2162.1391 | 891.5511 | 2104.7571 | 858.247 | 1498.85 | 1361154.0265 | 308968.92 | 140151.7351 | 0 | 430110.4841
1138 | 1207.142 | 3404.0395 | 1253.9848 | 3313.6982 | 1207.142 | 1503.9 | 1932647.5302 | 434571.12 | 197126.2886 | 0 | 598863.1462
1139 | 1636.944 | 3940.5926 | 1700.4652 | 3836.0114 | 1636.944 | 1379.1 | 2410203.3032 | 589299.84 | 267312.9552 | 0 | 1016378.5296
1140 | 1392.639 | 4248.4289 | 1446.68 | 4135.6779 | 1392.639 | 1376.15 | 2043284.2514 | 501350.04 | 227417.9487 | 0 | 868797.8402
1141 | 1733.618 | 4269.5062 | 1800.8906 | 4156.1958 | 1733.618 | 1492.65 | 2747205.5991 | 624102.48 | 283099.8194 | 0 | 879551.0923
1142 | 1461.298 | 2893.2416 | 1518.0033 | 2816.4565 | 1461.298 | 1374 | 2141787.7862 | 526067.28 | 238629.9634 | 0 | 914772.548
1143 | 1523.695 | 1724.3806 | 1582.8216 | 1678.6164 | 1523.695 | 1384.1 | 2241874.1487 | 548530.2 | 248819.3935 | 0 | 938443.7505
1144 | 1550.416 | 2318.1759 | 1610.5795 | 2256.6528 | 1550.416 | 1426.9 | 2340589.004 | 558149.76 | 253182.9328 | 0 | 888543.4096
1145 | 1733.837 | 1472.6096 | 1472.6096 | 1433.5274 | 1433.5274 | 1493.3 | 2255814.7622 | 516069.8478 | 234095.0171 | 550467.5794 | 711002.9601
1146 | 1717.427 | 297.4036 | 297.4036 | 289.5106 | 289.5106 | 1607.4 | 491471.5181 | 104223.8297 | 47277.0872 | 2617370.6914 | 111257.3436
1147 | 1575.959 | 0 | 0 | 0 | 0 | 1622.05 | 0 | 0 | 0 | 5355108.682 | 0
1148 | 1707.2 | 0 | 0 | 0 | 0 | 1577.5 | 0 | 0 | 0 | 5801065.6 | 0
1149 | 1400 | 0 | 0 | 0 | 0 | 1521.3 | 0 | 0 | 0 | 4757200 | 0
1150 | 1287.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1550.55 | 503777.2262 | 111351.8261 | 50510.4255 | 3322868.0863 | 137475.0693
1151 | 1057.6 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1517.95 | 958210.9029 | 215514.4963 | 97759.7701 | 1559507.4159 | 285373.6
1152 | 1536.8 | 0 | 0 | 0 | 0 | 1503.05 | 0 | 0 | 0 | 2816954.4 | 0
1153 | 997.6 | 0 | 0 | 0 | 0 | 1639.6 | 0 | 0 | 0 | 1187144 | 0
1154 | 1274.4 | 0 | 0 | 0 | 0 | 1517.1 | 0 | 0 | 0 | 1516536 | 0
1155 | 1188.8 | 0 | 0 | 0 | 0 | 1512.8 | 0 | 0 | 0 | 1414672 | 0
1156 | 1111.2 | 0 | 0 | 0 | 0 | 1511.6 | 0 | 0 | 0 | 1322328 | 0
1157 | 1072.8 | 0 | 0 | 0 | 0 | 1481.4 | 0 | 0 | 0 | 1276632 | 0
1158 | 1068.8 | 0 | 0 | 0 | 0 | 1482.85 | 0 | 0 | 0 | 1271872 | 0
1159 | 1287.2 | 110.5153 | 110.5153 | 107.5823 | 107.5823 | 1483.65 | 169476.6424 | 38729.6296 | 17568.1903 | 2162239.236 | 54374.7531
1160 | 1071.05 | 1112.6118 | 1112.6118 | 1083.0837 | 1071.05 | 1494.95 | 1699214.5328 | 385578 | 174902.465 | 0 | 540933.8025
1161 | 1356.959 | 1856.8489 | 1409.6155 | 1807.5692 | 1356.959 | 1464.05 | 2116424.5954 | 488505.24 | 221591.4047 | 0 | 727262.176
1162 | 1375.012 | 3034.3518 | 1428.369 | 2953.8217 | 1375.012 | 1467.3 | 2151840.0342 | 495004.32 | 224539.4596 | 0 | 732468.8924
1163 | 1335.484 | 3910.2065 | 1387.3071 | 3806.4318 | 1335.484 | 1473.5 | 2100922.3773 | 480774.24 | 218084.5372 | 0 | 703132.326
1164 | 1194.744 | 3962.4511 | 1241.1057 | 3857.2898 | 1194.744 | 1475.95 | 1879385.5388 | 430107.84 | 195101.6952 | 0 | 626105.5932
1165 | 1239.472 | 2525.5681 | 1287.5694 | 2458.5409 | 1239.472 | 1469.4 | 1941981.6795 | 446209.92 | 202405.7776 | 0 | 657663.8432
1166 | 1494.782 | 2674.0205 | 1552.7866 | 2603.0535 | 1494.782 | 1413.25 | 2254031.3509 | 538121.52 | 244097.9006 | 0 | 877063.3385
1167 | 1663.536 | 2507.3464 | 1728.0891 | 2440.8028 | 1663.536 | 1328.9 | 2349319.8334 | 598872.96 | 271655.4288 | 0 | 1116399.0096
1168 | 1380.276 | 1847.9183 | 1433.8373 | 1798.8756 | 1380.276 | 1495.5 | 2182984.9054 | 496899.36 | 225399.0708 | 0 | 696349.242
1169 | 1448.549 | 1519.6145 | 1504.7596 | 1479.2847 | 1448.549 | 1568.95 | 2392952.0219 | 521477.64 | 236548.0517 | 0 | 624157.3827
1170 | 1689.979 | 300.8867 | 300.8867 | 292.9013 | 292.9013 | 1840.75 | 567375.1626 | 105444.4718 | 47830.784 | 2560843.4048 | 45657.7712
1171 | 1823.205 | 0 | 0 | 0 | 0 | 1855.35 | 0 | 0 | 0 | 6195250.59 | 0
1172 | 855.2 | 0 | 0 | 0 | 0 | 1828.45 | 0 | 0 | 0 | 2905969.6 | 0
1173 | 1082.4 | 0 | 0 | 0 | 0 | 1809.75 | 0 | 0 | 0 | 3677995.2 | 0
1174 | 1165.6 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1798.35 | 590371.7479 | 111351.8261 | 50510.4255 | 2909671.2863 | 61679.4921
1175 | 1396.8 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1781.9 | 1131994.5488 | 215514.4963 | 97759.7701 | 2712109.0159 | 129115.2
1176 | 754.4 | 0 | 0 | 0 | 0 | 1766.05 | 0 | 0 | 0 | 1382815.2 | 0
1177 | 602.4 | 0 | 0 | 0 | 0 | 1773.85 | 0 | 0 | 0 | 716856 | 0
1178 | 580.8 | 0 | 0 | 0 | 0 | 1532.9 | 0 | 0 | 0 | 691152 | 0
1179 | 700.8 | 0 | 0 | 0 | 0 | 1528.95 | 0 | 0 | 0 | 833952 | 0
1180 | 725.6 | 0 | 0 | 0 | 0 | 1524.7 | 0 | 0 | 0 | 863464 | 0
1181 | 505.6 | 0 | 0 | 0 | 0 | 1526.6 | 0 | 0 | 0 | 601664 | 0
1182 | 723.2 | 0 | 0 | 0 | 0 | 1535.15 | 0 | 0 | 0 | 860608 | 0
1183 | 676.8 | 96.4873 | 96.4873 | 93.9266 | 93.9266 | 1623.8 | 160757.6468 | 33813.5692 | 15338.2107 | 1068406.9769 | 34587.4518
1184 | 771.604 | 801.5459 | 801.5459 | 780.2733 | 771.604 | 1765.2 | 1431239.3129 | 277777.44 | 126002.9332 | 0 | 181172.6192
1185 | 658.296 | 1767.4473 | 683.841 | 1720.5402 | 658.296 | 1813.4 | 1256189.7097 | 236986.56 | 107499.7368 | 0 | 122838.0336
1186 | 829.986 | 3198.4964 | 862.1944 | 3113.6101 | 829.986 | 1595.45 | 1397114.0742 | 298794.96 | 135536.7138 | 0 | 335770.8363
1187 | 571.13 | 3814.1867 | 593.2926 | 3712.9602 | 571.13 | 1532.9 | 928285.0155 | 205606.8 | 93265.529 | 0 | 266774.823
1188 | 704.878 | 4092.5645 | 732.2306 | 3983.9501 | 704.878 | 1526.95 | 1135011.8059 | 253756.08 | 115106.5774 | 0 | 333442.5379
1189 | 802.622 | 4099.4373 | 833.7675 | 3990.6404 | 802.622 | 1515.1 | 1280103.4921 | 288943.92 | 131068.1726 | 0 | 389191.4078
1190 | 845.333 | 3832.319 | 878.1359 | 3730.6113 | 845.333 | 1557.6 | 1388290.3613 | 304319.88 | 138042.8789 | 0 | 373975.3192
1191 | 810.397 | 3333.0414 | 841.8443 | 3244.5843 | 810.397 | 1762.95 | 1503828.5445 | 291742.92 | 132337.8301 | 0 | 192104.6088
1192 | 948.631 | 2533.1732 | 985.4424 | 2465.9441 | 948.631 | 1793.7 | 1788698.485 | 341507.16 | 154911.4423 | 0 | 195702.5753
1193 | 863.605 | 1288.9562 | 897.117 | 1254.748 | 863.605 | 1888.35 | 1711838.1596 | 310897.8 | 141026.6965 | 0 | 96421.4982
1194 | 870.304 | 263.4565 | 263.4565 | 256.4645 | 256.4645 | 1898.6 | 512636.6608 | 92327.2111 | 41880.6488 | 1125167.8489 | 25455.456
1195 | 797.6 | 0 | 0 | 0 | 0 | 1902.4 | 0 | 0 | 0 | 2710244.8 | 0
1196 | 838.4 | 0 | 0 | 0 | 0 | 1853.95 | 0 | 0 | 0 | 2848883.2 | 0
1197 | 759.2 | 0 | 0 | 0 | 0 | 1735.1 | 0 | 0 | 0 | 2579761.6 | 0
1198 | 689.6 | 360.1266 | 360.1266 | 350.569 | 350.569 | 1836.55 | 675438.0876 | 126204.8522 | 57247.9232 | 1152027.2233 | 56663.8653
1199 | 551.2 | 572.5892 | 572.5892 | 557.393 | 551.2 | 1816.35 | 1052780.463 | 198432 | 90010.96 | 0 | 101227.88
1200 | 689.6 | 0 | 0 | 0 | 0 | 1798.7 | 0 | 0 | 0 | 1264036.8 | 0
1201 | 1026.4 | 0 | 0 | 0 | 0 | 1723.85 | 0 | 0 | 0 | 1221416 | 0
1202 | 1103.2 | 0 | 0 | 0 | 0 | 1759.85 | 0 | 0 | 0 | 1312808 | 0
1203 | 797.6 | 0 | 0 | 0 | 0 | 1755.9 | 0 | 0 | 0 | 949144 | 0
1204 | 818.4 | 0 | 0 | 0 | 0 | 1754.65 | 0 | 0 | 0 | 973896 | 0
1205 | 779.2 | 0 | 0 | 0 | 0 | 1642.05 | 0 | 0 | 0 | 927248 | 0
1206 | 741.6 | 0 | 0 | 0 | 0 | 1604.15 | 0 | 0 | 0 | 882504 | 0
1207 | 836.8 | 107.2566 | 107.2566 | 104.4101 | 104.4101 | 1772.85 | 194799.1592 | 37587.6212 | 17050.1626 | 1342470.7622 | 23214.9572
1208 | 625.816 | 650.1006 | 650.1006 | 632.8473 | 625.816 | 1806.85 | 1191408.1519 | 225293.76 | 102195.7528 | 0 | 120876.3604
1209 | 296.104 | 1920.6939 | 307.5942 | 1869.7197 | 296.104 | 1838.4 | 573917.473 | 106597.44 | 48353.7832 | 0 | 47850.4064
1210 | 281.168 | 3290.8805 | 292.0787 | 3203.5423 | 281.168 | 1840.85 | 547918.5652 | 101220.48 | 45914.7344 | 0 | 44747.8872
1211 | 221.19 | 3869.477 | 229.7732 | 3766.7832 | 221.19 | 1494.9 | 351192.5119 | 79628.4 | 36120.327 | 0 | 111723.069
1212 | 299.592 | 4181.8602 | 311.2176 | 4070.8759 | 299.592 | 1341.45 | 425716.1149 | 107853.12 | 48923.3736 | 0 | 197296.3116
1213 | 888.252 | 4210.017 | 922.7204 | 4098.2854 | 888.252 | 1452.4 | 1362308.0209 | 319770.72 | 145051.5516 | 0 | 486406.7952
1214 | 1121.586 | 3962.0366 | 1165.1089 | 3856.8863 | 1121.586 | 1565.1 | 1857939.246 | 403770.96 | 183154.9938 | 0 | 487777.7514
1215 | 839.555 | 3457.6554 | 872.1337 | 3365.8911 | 839.555 | 1622.6 | 1441298.9191 | 302239.8 | 137099.3315 | 0 | 316848.057
1216 | 1363.969 | 2630.0677 | 1416.8975 | 2560.2671 | 1363.969 | 1747.65 | 2519787.3784 | 491028.84 | 222736.1377 | 0 | 344197.5771
1217 | 1384.49 | 1481.4041 | 1438.2148 | 1442.0885 | 1384.49 | 1718.85 | 2508911.8595 | 498416.4 | 226087.217 | 0 | 389249.3635
1218 | 1247.034 | 283.3631 | 283.3631 | 275.8428 | 275.8428 | 1843.6 | 536304.2779 | 99303.4008 | 45045.126 | 1780193.5064 | 42229.2512
1219 | 1191.158 | 0 | 0 | 0 | 0 | 1907.4 | 0 | 0 | 0 | 4047554.884 | 0
1220 | 1089.6 | 0 | 0 | 0 | 0 | 1869.05 | 0 | 0 | 0 | 3702460.8 | 0
1221 | 1178.4 | 0 | 0 | 0 | 0 | 1735.1 | 0 | 0 | 0 | 4004203.2 | 0
1222 | 1048 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1836.55 | 598336.8156 | 111351.8261 | 50510.4255 | 2510066.4863 | 49995.1053
1223 | 1239.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1811.35 | 1145172.158 | 215514.4963 | 97759.7701 | 2176584.2159 | 111680.8
1224 | 1102.4 | 0 | 0 | 0 | 0 | 1783.65 | 0 | 0 | 0 | 2020699.2 | 0
1225 | 1004 | 0 | 0 | 0 | 0 | 1768.8 | 0 | 0 | 0 | 1194760 | 0
1226 | 894.4 | 0 | 0 | 0 | 0 | 1718.2 | 0 | 0 | 0 | 1064336 | 0
1227 | 741.6 | 0 | 0 | 0 | 0 | 1750.85 | 0 | 0 | 0 | 882504 | 0
1228 | 812 | 0 | 0 | 0 | 0 | 1603.55 | 0 | 0 | 0 | 966280 | 0
1229 | 906.4 | 0 | 0 | 0 | 0 | 1528.1 | 0 | 0 | 0 | 1078616 | 0
1230 | 1295.2 | 0 | 0 | 0 | 0 | 1535.15 | 0 | 0 | 0 | 1541288 | 0
1231 | 1083.2 | 111.6029 | 111.6029 | 108.6411 | 108.6411 | 1663.4 | 190544.5182 | 39110.7844 | 17741.0864 | 1786366.5225 | 35795.0538
1232 | 928.89 | 964.9353 | 964.9353 | 939.3265 | 928.89 | 1801.8 | 1763412.1445 | 334400.4 | 151687.737 | 0 | 184105.998
1233 | 1047.146 | 1860.7704 | 1087.7802 | 1811.3866 | 1047.146 | 1848.4 | 2040574.1951 | 376972.56 | 170998.9418 | 0 | 158747.3336
1234 | 1458.486 | 3223.5379 | 1515.0822 | 3137.9869 | 1458.486 | 1820.9 | 2807533.0747 | 525054.96 | 238170.7638 | 0 | 261214.8426
1235 | 1341.872 | 3979.5717 | 1393.943 | 3873.956 | 1341.872 | 1470.2 | 2095322.9932 | 483073.92 | 219127.6976 | 0 | 710923.7856
1236 | 1455.678 | 4278.8326 | 1512.1652 | 4165.2747 | 1455.678 | 1401.55 | 2164604.5902 | 524044.08 | 237712.2174 | 0 | 871150.4991
1237 | 1622.4 | 4303.097 | 1685.3568 | 4188.8952 | 1622.4 | 1306.1 | 2245923.0598 | 584064 | 264937.92 | 0 | 1125783.36
1238 | 1434.147 | 4038.2807 | 1489.7987 | 3931.107 | 1434.147 | 1362.9 | 2078657.9152 | 516292.92 | 234196.2051 | 0 | 913695.0537
1239 | 1627.379 | 3362.1144 | 1690.529 | 3272.8857 | 1627.379 | 1542.6 | 2663102.4026 | 585856.44 | 265750.9907 | 0 | 744363.1546
1240 | 1212.806 | 2652.3999 | 1259.8686 | 2582.0067 | 1212.806 | 1617.05 | 2076806.1631 | 436610.16 | 198051.2198 | 0 | 464444.0577
1241 | 1458.823 | 1498.4416 | 1498.4416 | 1458.6737 | 1458.6737 | 1767.35 | 2722626.1076 | 525122.5488 | 238201.4228 | 273.5816 | 332181.8577
1242 | 1503.121 | 289.1233 | 289.1233 | 281.4501 | 281.4501 | 1782.1 | 529579.5185 | 101322.029 | 45960.7981 | 2239322.7956 | 60030.7963
1243 | 1519.235 | 0 | 0 | 0 | 0 | 1897.4 | 0 | 0 | 0 | 5162360.53 | 0
1244 | 1223.2 | 0 | 0 | 0 | 0 | 1769.05 | 0 | 0 | 0 | 4156433.6 | 0
1245 | 1371.2 | 0 | 0 | 0 | 0 | 1735.1 | 0 | 0 | 0 | 4659337.6 | 0
1246 | 1432.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1836.55 | 597798.4369 | 111351.8261 | 50510.4255 | 3817616.8863 | 49995.1053
1247 | 1228 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1806.35 | 1141622.4026 | 215514.4963 | 97759.7701 | 2138526.6159 | 114640.8
1248 | 1250.4 | 0 | 0 | 0 | 0 | 1788.7 | 0 | 0 | 0 | 2291983.2 | 0
1249 | 1195.2 | 0 | 0 | 0 | 0 | 1773.85 | 0 | 0 | 0 | 1422288 | 0
1250 | 1082.4 | 0 | 0 | 0 | 0 | 1764.9 | 0 | 0 | 0 | 1288056 | 0
1251 | 1088.8 | 0 | 0 | 0 | 0 | 1760.95 | 0 | 0 | 0 | 1295672 | 0
1252 | 1428 | 0 | 0 | 0 | 0 | 1759.7 | 0 | 0 | 0 | 1699320 | 0
1253 | 942.4 | 0 | 0 | 0 | 0 | 1756.55 | 0 | 0 | 0 | 1121456 | 0
1254 | 957.6 | 0 | 0 | 0 | 0 | 1763.6 | 0 | 0 | 0 | 1139544 | 0
1255 | 1361.6 | 107.5402 | 107.5402 | 104.6861 | 104.6861 | 1661.9 | 183674.0636 | 37687.0054 | 17095.2444 | 2303923.1308 | 34645.7832
1256 | 1216.436 | 1201.7548 | 1201.7548 | 1169.8609 | 1169.8609 | 1571 | 1935987.3116 | 421149.9099 | 191038.2786 | 85372.23 | 491253.906
1257 | 1066.076 | 1802.399 | 1107.4448 | 1754.5643 | 1066.076 | 1587.1 | 1784561.4963 | 383787.36 | 174090.2108 | 0 | 440182.7804
1258 | 1100.807 | 2862.4836 | 1143.5235 | 2786.5149 | 1100.807 | 1539.9 | 1793854.1497 | 396290.52 | 179761.7831 | 0 | 506481.3007
1259 | 1411.611 | 3858.9384 | 1466.3882 | 3756.5243 | 1411.611 | 1342.45 | 2010091.3176 | 508179.96 | 230516.0763 | 0 | 928204.813
1260 | 1365.056 | 4098.3247 | 1418.0267 | 3989.5574 | 1365.056 | 1336.5 | 1929046.5475 | 491420.16 | 222913.6448 | 0 | 905714.656
1261 | 1239.767 | 4046.1279 | 1287.8758 | 3938.7458 | 1239.767 | 1307.2 | 1709459.7317 | 446316.12 | 202453.9511 | 0 | 858910.5776
1262 | 1146.147 | 3585.3504 | 1190.6229 | 3490.1972 | 1146.147 | 1336.65 | 1622272.6193 | 412612.92 | 187165.8051 | 0 | 760296.6124
1263 | 1181.115 | 2550.2116 | 1226.9479 | 2482.5304 | 1181.115 | 1370.1 | 1710716.6351 | 425201.4 | 192876.0795 | 0 | 743984.3385
1264 | 1267.883 | 1995.5252 | 1317.0829 | 1942.5651 | 1267.883 | 1408 | 1882221.2461 | 456437.88 | 207045.2939 | 0 | 750586.736
1265 | 1187.464 | 1420.4066 | 1233.5432 | 1382.7097 | 1187.464 | 1594.4 | 1994555.4286 | 427487.04 | 193912.8712 | 0 | 481635.3984
1266 | 1008.407 | 270.1869 | 270.1869 | 263.0163 | 263.0163 | 1641.1 | 455559.5656 | 94685.8571 | 42950.5568 | 1366301.2087 | 92399.8817
1267 | 1409.602 | 0 | 0 | 0 | 0 | 1664.55 | 0 | 0 | 0 | 4789827.596 | 0
1268 | 946.4 | 0 | 0 | 0 | 0 | 1633.55 | 0 | 0 | 0 | 3215867.2 | 0
1269 | 1150.4 | 0 | 0 | 0 | 0 | 1727.1 | 0 | 0 | 0 | 3909059.2 | 0
1270 | 1396 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1831.55 | 595289.2643 | 111351.8261 | 50510.4255 | 3692570.4863 | 51524.4753
1271 | 1171.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1806.35 | 1139785.3434 | 215514.4963 | 97759.7701 | 1945520.2159 | 114640.8
1272 | 1109.6 | 0 | 0 | 0 | 0 | 1793.7 | 0 | 0 | 0 | 2033896.8 | 0
1273 | 1380.8 | 0 | 0 | 0 | 0 | 1658.5 | 0 | 0 | 0 | 2531006.4 | 0
1274 | 1206.4 | 0 | 0 | 0 | 0 | 1762 | 0 | 0 | 0 | 2211331.2 | 0
1275 | 1380.8 | 0 | 0 | 0 | 0 | 1765.25 | 0 | 0 | 0 | 2531006.4 | 0
1276 | 1010.4 | 0 | 0 | 0 | 0 | 1764 | 0 | 0 | 0 | 1852063.2 | 0
1277 | 960 | 0 | 0 | 0 | 0 | 1756.55 | 0 | 0 | 0 | 1759680 | 0
1278 | 1000 | 0 | 0 | 0 | 0 | 1758.55 | 0 | 0 | 0 | 1833000 | 0
1279 | 1016 | 97.2082 | 97.2082 | 94.6284 | 94.6284 | 1785.1 | 178618.8022 | 34066.2162 | 15452.8142 | 1688874.1823 | 19905.5423
1280 | 231.095 | 545.3953 | 240.0626 | 530.9209 | 231.095 | 1801.8 | 439823.8207 | 83194.2 | 37737.8135 | 0 | 45803.029
1281 | 181.355 | 1932.9331 | 188.3924 | 1881.6341 | 181.355 | 1753.35 | 336052.8715 | 65287.8 | 29615.2715 | 0 | 44731.2108
1282 | 156.897 | 3230.1976 | 162.9853 | 3144.47 | 156.897 | 1611.55 | 268287.7104 | 56482.92 | 25621.2801 | 0 | 60946.6397
1283 | 202.713 | 3812.0872 | 210.5792 | 3710.9165 | 202.713 | 1560.75 | 337224.633 | 72976.68 | 33103.0329 | 0 | 89041.6853
1284 | 193.831 | 4133.0229 | 201.3526 | 4023.3347 | 193.831 | 1532.95 | 315743.0581 | 69779.16 | 31652.6023 | 0 | 90528.7686
1285 | 194.696 | 2858.9278 | 202.2511 | 2783.0534 | 194.696 | 1514.15 | 311329.2599 | 70090.56 | 31793.8568 | 0 | 94593.0516
1286 | 147.249 | 2876.2499 | 152.963 | 2799.9158 | 147.249 | 1525.65 | 237770.2693 | 53009.64 | 24045.7617 | 0 | 69847.5632
1287 | 149.362 | 3189.4443 | 155.158 | 3104.7982 | 149.362 | 1542.6 | 243846.2094 | 53770.32 | 24390.8146 | 0 | 68318.1788
1288 | 167.046 | 2226.9813 | 173.5282 | 2167.8784 | 167.046 | 1556.7 | 274577.6823 | 60136.56 | 27278.6118 | 0 | 74051.4918
1289 | 135.46 | 1462.9934 | 140.7165 | 1424.1663 | 135.46 | 1633.2 | 233328.5534 | 48765.6 | 22120.618 | 0 | 49686.728
1290 | 134.638 | 285.5757 | 139.8626 | 277.9967 | 134.638 | 1774.05 | 252449.584 | 48469.68 | 21986.3854 | 0 | 30421.4561
1291 | 106.102 | 110.2193 | 110.2193 | 107.2941 | 106.102 | 1894.5 | 212622.1317 | 38196.72 | 17326.4566 | 0 | 11193.761
1292 | 0 | 0 | 0 | 0 | 0 | 1861.15 | 0 | 0 | 0 | 0 | 0
1293 | 0 | 0 | 0 | 0 | 0 | 1841.7 | 0 | 0 | 0 | 0 | 0
1294 | 85.6 | 88.9217 | 88.9217 | 86.5618 | 85.6 | 1836.55 | 166056.3269 | 30816 | 13978.48 | 0 | 13991.32
1295 | 87.2 | 90.5838 | 90.5838 | 88.1797 | 87.2 | 1801.3 | 166400.068 | 31392 | 14239.76 | 0 | 17326.64
1296 | 90.4 | 93.9079 | 93.9079 | 91.4157 | 90.4 | 1667.65 | 159638.3283 | 32544 | 14762.32 | 0 | 30044.44
1297 | 84.8 | 88.0906 | 88.0906 | 85.7528 | 84.8 | 1492.35 | 134025.2533 | 30528 | 13847.84 | 0 | 43048.72
1298 | 87.2 | 90.5838 | 90.5838 | 88.1797 | 87.2 | 1515.45 | 139792.0541 | 31392 | 14239.76 | 0 | 42252.76
1299 | 80.8 | 83.9354 | 83.9354 | 81.7078 | 80.8 | 1470.15 | 125657.281 | 29088 | 13194.64 | 0 | 42811.88
1300 | 86.4 | 89.7527 | 89.7527 | 87.3707 | 86.4 | 1449.75 | 132523.3688 | 31104 | 14109.12 | 0 | 47541.6
1301 | 81.6 | 84.7665 | 84.7665 | 82.5168 | 81.6 | 1467.2 | 126817.7132 | 29376 | 13325.28 | 0 | 43476.48
1302 | 86.4 | 89.7527 | 89.7527 | 87.3707 | 86.4 | 1471.55 | 134766.6411 | 31104 | 14109.12 | 0 | 45658.08
1303 | 68.8 | 71.4698 | 71.4698 | 69.573 | 68.8 | 1508.35 | 109967.4523 | 24768 | 11235.04 | 0 | 33825.52
1304 | 94.436 | 615.1158 | 98.1006 | 598.7909 | 94.436 | 1502.4 | 150056.1924 | 33996.96 | 15421.3988 | 0 | 46991.3536
1305 | 767.602 | 2106.3782 | 797.3886 | 2050.476 | 767.602 | 1544.95 | 1255895.137 | 276336.72 | 125349.4066 | 0 | 349297.2901
1306 | 1311.495 | 3317.2214 | 1362.3872 | 3229.1842 | 1311.495 | 1525.75 | 2125553.7982 | 472138.2 | 214167.1335 | 0 | 621976.5038
1307 | 1454.312 | 3899.6564 | 1510.7462 | 3796.1616 | 1454.312 | 1503.55 | 2331778.5641 | 523552.32 | 237489.1496 | 0 | 721993.1924
1308 | 1278.237 | 4202.0327 | 1327.8387 | 4090.5131 | 1278.237 | 1437.9 | 1950150.7593 | 460165.32 | 208736.1021 | 0 | 718497.0177
1309 | 1477.846 | 4217.6937 | 1535.1934 | 4105.7585 | 1477.846 | 1491.7 | 2327185.7563 | 532024.56 | 241332.2518 | 0 | 751189.1218
1310 | 1606.507 | 3968.2996 | 1668.8471 | 3862.9831 | 1606.507 | 1436.7 | 2448713.8192 | 578342.52 | 262342.5931 | 0 | 904945.3931
1311 | 1514.242 | 3282.2231 | 1573.0018 | 3195.1147 | 1514.242 | 1513.85 | 2431951.4618 | 545127.12 | 247275.7186 | 0 | 736148.7483
1312 | 1656.625 | 2499.5107 | 1720.9099 | 2433.175 | 1656.625 | 1530.55 | 2684289.9498 | 596385 | 270526.8625 | 0 | 777702.6063
1313 | 1550.847 | 1439.131 | 1439.131 | 1400.9373 | 1400.9373 | 1474.6 | 2183993.1697 | 504337.4133 | 228773.0544 | 274784.5547 | 720482.0708
1314 | 1602.881 | 274.9186 | 274.9186 | 267.6224 | 267.6224 | 1545.6 | 438094.7586 | 96344.0809 | 43702.7456 | 2447528.9275 | 119035.0784
1315 | 1592.239 | 0 | 0 | 0 | 0 | 1670.1 | 0 | 0 | 0 | 5410428.122 | 0
1316 | 1521.6 | 0 | 0 | 0 | 0 | 1544.85 | 0 | 0 | 0 | 5170396.8 | 0
1317 | 1444 | 0 | 0 | 0 | 0 | 1523.35 | 0 | 0 | 0 | 4906712 | 0
1318 | 1625.6 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1537.65 | 501101.8897 | 111351.8261 | 50510.4255 | 4472751.2863 | 141420.8439
1319 | 1578.4 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1528.95 | 968768.0562 | 215514.4963 | 97759.7701 | 3329185.8159 | 278861.6
1320 | 1232.8 | 0 | 0 | 0 | 0 | 1501.85 | 0 | 0 | 0 | 2259722.4 | 0
1321 | 1146.4 | 0 | 0 | 0 | 0 | 1462.2 | 0 | 0 | 0 | 1364216 | 0
1322 | 1488 | 0 | 0 | 0 | 0 | 1485 | 0 | 0 | 0 | 1770720 | 0
1323 | 1347.2 | 0 | 0 | 0 | 0 | 1444.5 | 0 | 0 | 0 | 1603168 | 0
1324 | 1243.2 | 0 | 0 | 0 | 0 | 1443.3 | 0 | 0 | 0 | 1479408 | 0
1325 | 1531.2 | 0 | 0 | 0 | 0 | 1435.3 | 0 | 0 | 0 | 1822128 | 0
1326 | 1331.2 | 0 | 0 | 0 | 0 | 1445.45 | 0 | 0 | 0 | 1584128 | 0
1327 | 1144.8 | 159.6072 | 159.6072 | 155.3713 | 155.3713 | 1447.45 | 238075.8054 | 55933.6567 | 25372.1282 | 1813622.8645 | 84034.5667
1328 | 1010.871 | 1050.0976 | 1050.0976 | 1022.2286 | 1010.871 | 1453.2 | 1559394.7263 | 363913.56 | 165075.2343 | 0 | 552744.2628
1329 | 1203.916 | 1970.3093 | 1250.6337 | 1918.0183 | 1203.916 | 1410.05 | 1810546.5747 | 433409.76 | 196599.4828 | 0 | 710250.2442
1330 | 1503.542 | 3349.4348 | 1561.8866 | 3260.5426 | 1503.542 | 1350.6 | 2162159.6875 | 541275.12 | 245528.4086 | 0 | 976400.1748
1331 | 1515.135 | 3262.7953 | 1573.9294 | 3176.2025 | 1515.135 | 1454.5 | 2342096.6858 | 545448.6 | 247421.5455 | 0 | 826506.1425
1332 | 1556.164 | 460.4419 | 460.4419 | 448.222 | 448.222 | 1475.95 | 704415.4958 | 161359.9263 | 73194.6554 | 2030857.6541 | 224130.9445
1333 | 1211.064 | 1258.059 | 1258.059 | 1224.6708 | 1211.064 | 1326.7 | 1712435.9556 | 435983.04 | 197766.7512 | 0 | 815409.3912
1334 | 1410.099 | 1153.1948 | 1153.1948 | 1122.5896 | 1122.5896 | 1264 | 1513629.1597 | 404132.2737 | 183318.8897 | 527004.64 | 808748.448
1335 | 1317.507 | 786.8105 | 786.8105 | 765.9289 | 765.9289 | 1273.65 | 1038941.282 | 275734.4159 | 125076.1948 | 1011042.5965 | 544564.2064
1336 | 1520.142 | 465.2007 | 465.2007 | 452.8545 | 452.8545 | 1223.1 | 588137.3812 | 163027.6153 | 73951.1377 | 1956338.0115 | 344381.1244
1337 | 1602.996 | 135.0051 | 135.0051 | 131.4222 | 131.4222 | 1364.7 | 189998.6003 | 47311.9847 | 21461.242 | 2697394.8124 | 81726.2626
1338 | 1509.998 | 0 | 0 | 0 | 0 | 1465.4 | 0 | 0 | 0 | 2767826.334 | 0
1339 | 1268.157 | 0 | 0 | 0 | 0 | 1586.25 | 0 | 0 | 0 | 4309197.486 | 0
1340 | 1219.2 | 0 | 0 | 0 | 0 | 1582.6 | 0 | 0 | 0 | 4142841.6 | 0
1341 | 1537.6 | 0 | 0 | 0 | 0 | 1549.85 | 0 | 0 | 0 | 5224764.8 | 0
1342 | 1788 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1538.45 | 506139.8175 | 111351.8261 | 50510.4255 | 5024586.4863 | 141176.1447
1343 | 1920 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1468.6 | 933358.9724 | 215514.4963 | 97759.7701 | 4489942.6159 | 314588.8
1344 | 1416 | 0 | 0 | 0 | 0 | 1444.05 | 0 | 0 | 0 | 2595528 | 0
1345 | 1318.4 | 0 | 0 | 0 | 0 | 1413.5 | 0 | 0 | 0 | 1568896 | 0
1346 | 1386.4 | 0 | 0 | 0 | 0 | 1280.4 | 0 | 0 | 0 | 1649816 | 0
1347 | 1447.2 | 0 | 0 | 0 | 0 | 1362 | 0 | 0 | 0 | 1722168 | 0
1348 | 1560.8 | 0 | 0 | 0 | 0 | 1275.2 | 0 | 0 | 0 | 1857352 | 0
1349 | 1575.2 | 0 | 0 | 0 | 0 | 1276.6 | 0 | 0 | 0 | 1874488 | 0
1350 | 1132 | 0 | 0 | 0 | 0 | 1266.2 | 0 | 0 | 0 | 1347080 | 0
1351 | 1085.6 | 154.3913 | 154.3913 | 150.2939 | 150.2939 | 1384.45 | 219872.4468 | 54105.788 | 24542.9866 | 1714416.1628 | 90556.0227
1352 | 972.737 | 1010.4838 | 1010.4838 | 983.6661 | 972.737 | 1500.85 | 1541956.9933 | 350185.32 | 158847.9521 | 0 | 485541.6736
1353 | 1002.649 | 1855.6606 | 1041.5565 | 1806.4123 | 1002.649 | 1580.85 | 1676726.6498 | 360953.64 | 163732.5817 | 0 | 420260.3284
1354 | 1224.946 | 3302.0424 | 1272.4808 | 3214.408 | 1224.946 | 1560.1 | 2027729.6104 | 440980.56 | 200033.6818 | 0 | 538853.7454
1355 | 1629.851 | 4031.7394 | 1693.097 | 3924.7392 | 1629.851 | 1532.9 | 2651669.7385 | 586746.36 | 266154.6683 | 0 | 761303.4021
1356 | 1267.651 | 3542.1133 | 1316.8419 | 3448.1076 | 1267.651 | 1526.95 | 2047672.8597 | 456354.36 | 207007.4083 | 0 | 599662.3055
1357 | 1387.724 | 2708.8195 | 1441.5743 | 2636.9289 | 1387.724 | 1519.45 | 2225180.8412 | 499580.64 | 226615.3292 | 0 | 666870.7682
1358 | 1508.577 | 2321.8605 | 1567.117 | 2260.2396 | 1508.577 | 1530.95 | 2440401.5831 | 543087.72 | 246350.6241 | 0 | 707598.0419
1359 | 1492.205 | 1654.388 | 1550.1096 | 1610.4814 | 1492.205 | 1588.7 | 2507499.5328 | 537193.8 | 243677.0765 | 0 | 613743.9165
1360 | 1115.506 | 821.4255 | 821.4255 | 799.6253 | 799.6253 | 1567.05 | 1323177.6512 | 287865.1153 | 130578.8148 | 579009.2857 | 338874.2945
1361 | 1715.058 | 1370.4982 | 1370.4982 | 1334.1259 | 1334.1259 | 1608.75 | 2265553.0433 | 480285.3403 | 217862.7669 | 698248.4564 | 510935.3312
1362 | 1580.662 | 172.0146 | 172.0146 | 167.4495 | 167.4495 | 1623.65 | 287033.7828 | 60281.8073 | 27344.4976 | 2590418.5772 | 61686.3994
1363 | 1152.8 | 0 | 0 | 0 | 0 | 1643.3 | 0 | 0 | 0 | 3917214.4 | 0
1364 | 1612 | 0 | 0 | 0 | 0 | 1611.15 | 0 | 0 | 0 | 5477576 | 0
1365 | 1400.8 | 0 | 0 | 0 | 0 | 1593.3 | 0 | 0 | 0 | 4759918.4 | 0
1366 | 1607.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1591.55 | 520535.7395 | 111351.8261 | 50510.4255 | 4410228.0863 | 124934.2353
1367 | 1369.6 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1665.35 | 1059323.0407 | 215514.4963 | 97759.7701 | 2619683.4159 | 198112.8
1368 | 1172 | 0 | 0 | 0 | 0 | 1552.85 | 0 | 0 | 0 | 2148276 | 0
1369 | 1296.8 | 0 | 0 | 0 | 0 | 1411.4 | 0 | 0 | 0 | 1543192 | 0
1370 | 1394.4 | 0 | 0 | 0 | 0 | 1499 | 0 | 0 | 0 | 1659336 | 0
1371 | 1192 | 0 | 0 | 0 | 0 | 1472 | 0 | 0 | 0 | 1418480 | 0
1372 | 1368.8 | 0 | 0 | 0 | 0 | 1447.7 | 0 | 0 | 0 | 1628872 | 0
1373 | 1286.4 | 0 | 0 | 0 | 0 | 1448.65 | 0 | 0 | 0 | 1530816 | 0
1374 | 717.6 | 0 | 0 | 0 | 0 | 1456.65 | 0 | 0 | 0 | 853944 | 0
1375 | 961.6 | 160.4766 | 160.4766 | 156.2177 | 156.2177 | 1482.95 | 245569.4207 | 56238.3622 | 25510.346 | 1476265.8059 | 79063.6666
1376 | 858.742 | 892.0653 | 892.0653 | 868.3903 | 858.742 | 1539.75 | 1399441.3425 | 309147.12 | 140232.5686 | 0 | 395236.0055
1377 | 924.647 | 1929.53 | 960.5277 | 1878.3213 | 924.647 | 1598.5 | 1566117.6644 | 332872.92 | 150994.8551 | 0 | 371245.7705
1378 | 1261.322 | 3375.8173 | 1310.2673 | 3286.2249 | 1261.322 | 1606 | 2150033.7937 | 454075.92 | 205973.8826 | 0 | 496960.868
1379 | 921.625 | 3906.1552 | 957.3884 | 3802.4879 | 921.625 | 1605 | 1578782.0424 | 331785 | 150501.3625 | 0 | 364041.875
1380 | 1166.42 | 4160.6 | 1211.6826 | 4050.1799 | 1166.42 | 1584.85 | 1963962.7473 | 419911.2 | 190476.386 | 0 | 484239.263
1381 | 1425.732 | 4058.66 | 1481.0572 | 3950.9454 | 1425.732 | 1428.15 | 2154769.3213 | 513263.52 | 232822.0356 | 0 | 815304.8442
1382 | 1270.075 | 2682.0287 | 1319.3599 | 2610.8491 | 1270.075 | 1564.25 | 2108110.9048 | 457227 | 207403.2475 | 0 | 553435.1812
1383 | 1409.846 | 1697.7196 | 1464.5547 | 1652.6631 | 1409.846 | 1614.7 | 2415054.0471 | 507544.56 | 230227.8518 | 0 | 543213.6638
1384 | 1503.303 | 848.2038 | 848.2038 | 825.6929 | 825.6929 | 1584.55 | 1386002.7895 | 297249.4611 | 134835.6583 | 1242059.2263 | 335777.9072
1385 | 1426.651 | 647.1982 | 647.1982 | 630.0219 | 630.0219 | 1638.8 | 1092680.5127 | 226807.8927 | 102882.5802 | 1460221.096 | 222750.234
1386 | 1530.718 | 248.6722 | 248.6722 | 242.0726 | 242.0726 | 1640.7 | 420979.0411 | 87146.1261 | 39530.4511 | 2362087.0686 | 85136.8536
1387 | 1079.591 | 0 | 0 | 0 | 0 | 1644.5 | 0 | 0 | 0 | 3668450.218 | 0
1388 | 1292 | 0 | 0 | 0 | 0 | 1611.15 | 0 | 0 | 0 | 4390216 | 0
1389 | 1392.8 | 0 | 0 | 0 | 0 | 1590.5 | 0 | 0 | 0 | 4732734.4 | 0
1390 | 1493.6 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1593.05 | 521015.9234 | 111351.8261 | 50510.4255 | 4024215.2863 | 124475.4243
1391 | 1524 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1566.45 | 995107.3787 | 215514.4963 | 97759.7701 | 3144334.6159 | 256661.6
1392 | 1385.6 | 0 | 0 | 0 | 0 | 1497.6 | 0 | 0 | 0 | 2539804.8 | 0
1393 | 1531.2 | 0 | 0 | 0 | 0 | 1483.7 | 0 | 0 | 0 | 1822128 | 0
1394 | 1497.6 | 0 | 0 | 0 | 0 | 1451.95 | 0 | 0 | 0 | 1782144 | 0
1395 | 1485.6 | 0 | 0 | 0 | 0 | 1259 | 0 | 0 | 0 | 1767864 | 0
1396 | 1413.6 | 0 | 0 | 0 | 0 | 1159.7 | 0 | 0 | 0 | 1682184 | 0
1397 | 1488.8 | 0 | 0 | 0 | 0 | 1148.65 | 0 | 0 | 0 | 1771672 | 0
1398 | 1299.2 | 0 | 0 | 0 | 0 | 1227.25 | 0 | 0 | 0 | 1546048 | 0
1399 | 1104 | 58.8566 | 58.8566 | 57.2946 | 57.2946 | 1384.95 | 84292.4598 | 20626.0479 | 9356.2045 | 1918611.0397 | 34493.2341
1400 | 1358.071 | 1272.4382 | 1272.4382 | 1238.6684 | 1238.6684 | 1449.9 | 1908245.8311 | 445920.6073 | 202274.5422 | 218865.0506 | 666978.0967
1401 | 1671.657 | 1195.6092 | 1195.6092 | 1163.8784 | 1163.8784 | 1482.4 | 1831487.0377 | 418996.2211 | 190061.3414 | 930758.1883 | 589680.4584
1402 | 1400.192 | 2659.1012 | 1454.5261 | 2588.5301 | 1400.192 | 1343.45 | 1995122.4467 | 504069.12 | 228651.3536 | 0 | 919296.0576
1403 | 1499.733 | 3381.1827 | 1557.9298 | 3291.448 | 1499.733 | 1263.45 | 2015090.4532 | 539903.88 | 244906.3989 | 0 | 1104628.3411
1404 | 1335.797 | 3139.4819 | 1387.6323 | 3056.1618 | 1335.797 | 1338.95 | 1895935.0894 | 480886.92 | 218135.6501 | 0 | 883028.6068
1405 | 1593.236 | 2855.8997 | 1655.0611 | 2780.1057 | 1593.236 | 1307.2 | 2199614.3046 | 573564.96 | 260175.4388 | 0 | 1103793.9008
1406 | 1620.676 | 3160.5541 | 1683.5659 | 3076.6747 | 1620.676 | 1318.7 | 2266499.5076 | 583443.36 | 264656.3908 | 0 | 1104166.5588
1407 | 1525.559 | 2539.4839 | 1584.7579 | 2472.0874 | 1525.559 | 1313.2 | 2121863.9479 | 549201.24 | 249123.7847 | 0 | 1047753.9212
1408 | 1514.83 | 1378.79 | 1378.79 | 1342.1976 | 1342.1976 | 1366.25 | 1942006.2252 | 483191.1455 | 219180.8724 | 316435.1406 | 832624.5525
1409 | 1822.304 | 999.2003 | 999.2003 | 972.6821 | 972.6821 | 1527.35 | 1571576.2548 | 350165.5508 | 158838.9846 | 1557356.9691 | 450012.9009
1410 | 1605.867 | 273.9899 | 273.9899 | 266.7184 | 266.7184 | 1581.6 | 445714.9616 | 96018.6249 | 43555.1151 | 2454659.3791 | 109234.1984
1411 | 1954.45 | 0 | 0 | 0 | 0 | 1643.3 | 0 | 0 | 0 | 6641221.1 | 0
1412 | 1688.8 | 0 | 0 | 0 | 0 | 1611.15 | 0 | 0 | 0 | 5738542.4 | 0
1413 | 1488.8 | 0 | 0 | 0 | 0 | 1570.25 | 0 | 0 | 0 | 5058942.4 | 0
1414 | 1700 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1593.05 | 521134.3353 | 111351.8261 | 50510.4255 | 4725562.4863 | 124475.4243
1415 | 1531.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1568.05 | 996068.7853 | 215514.4963 | 97759.7701 | 3168800.2159 | 255714.4
1416 | 1661.6 | 0 | 0 | 0 | 0 | 1535.8 | 0 | 0 | 0 | 3045712.8 | 0
1417 | 677.6 | 0 | 0 | 0 | 0 | 1518.9 | 0 | 0 | 0 | 806344 | 0
1418 | 501.6 | 0 | 0 | 0 | 0 | 1520.9 | 0 | 0 | 0 | 596904 | 0
1419 | 592.8 | 0 | 0 | 0 | 0 | 1493.85 | 0 | 0 | 0 | 705432 | 0
1420 | 738.4 | 0 | 0 | 0 | 0 | 1469.55 | 0 | 0 | 0 | 878696 | 0
1421 | 784.8 | 0 | 0 | 0 | 0 | 1493.3 | 0 | 0 | 0 | 933912 | 0
1422 | 656.8 | 0 | 0 | 0 | 0 | 1511.1 | 0 | 0 | 0 | 781592 | 0
1423 | 596 | 150.7773 | 150.7773 | 146.7758 | 146.7758 | 1541 | 240507.4233 | 52839.2763 | 23968.4828 | 823428.0183 | 65944.989
1424 | 458.959 | 592.5124 | 476.7688 | 576.7875 | 458.959 | 1562.85 | 759530.3938 | 165225.24 | 74948.0047 | 0 | 200633.9268
1425 | 545.507 | 1973.6864 | 566.6753 | 1921.3059 | 545.507 | 1596.45 | 923153.0576 | 196382.52 | 89081.2931 | 0 | 220139.3499
1426 | 657.357 | 3049.1579 | 682.8656 | 2968.2349 | 657.357 | 1555.95 | 1085188.9891 | 236648.52 | 107346.3981 | 0 | 291899.3759
1427 | 784.747 | 3754.9883 | 815.1989 | 3655.333 | 784.747 | 1316.9 | 1102327.0799 | 282508.92 | 128149.1851 | 0 | 536060.6757
1428 | 756.627 | 3917.7347 | 785.9877 | 3813.7602 | 756.627 | 1353.95 | 1089047.1359 | 272385.72 | 123557.1891 | 0 | 488818.8734
1429 | 915.603 | 3361.0922 | 951.1327 | 3271.8907 | 915.603 | 1342.1 | 1301124.9911 | 329617.08 | 149517.9699 | 0 | 602375.2137
1430 | 833.363 | 2981.0289 | 865.7014 | 2901.914 | 833.363 | 1439.1 | 1273133.2866 | 300010.68 | 136088.1779 | 0 | 467433.3067
1431 | 642.919 | 2223.2915 | 667.8673 | 2164.2865 | 642.919 | 1540.6 | 1051079.2601 | 231450.84 | 104988.6727 | 0 | 295356.9886
1432 | 667.766 | 1966.34 | 693.6785 | 1914.1544 | 667.766 | 1555.75 | 1101021.7071 | 240395.76 | 109046.1878 | 0 | 296655.0455
1433 | 671.56 | 1134.7664 | 697.6197 | 1104.6503 | 671.56 | 1602.75 | 1138936.2884 | 241761.6 | 109665.748 | 0 | 266777.21
1434 | 759.475 | 214.5308 | 214.5308 | 208.8373 | 208.8373 | 1626.5 | 359153.4912 | 75181.4311 | 34103.1325 | 1009318.8882 | 76350.4965
1435 | 768.029 | 0 | 0 | 0 | 0 | 1642.45 | 0 | 0 | 0 | 2609762.542 | 0
1436 | 534.4 | 0 | 0 | 0 | 0 | 1611.15 | 0 | 0 | 0 | 1815891.2 | 0
1437 | 708.8 | 0 | 0 | 0 | 0 | 1588.45 | 0 | 0 | 0 | 2408502.4 | 0
1438 | 805.6 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1589.85 | 519236.2238 | 111351.8261 | 50510.4255 | 1686391.2863 | 125454.2211
1439 | 713.6 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1564.4 | 993296.4712 | 215514.4963 | 97759.7701 | 390595.4159 | 257875.2
1440 | 728.8 | 0 | 0 | 0 | 0 | 1544.7 | 0 | 0 | 0 | 1335890.4 | 0
1441 | 1704 | 0 | 0 | 0 | 0 | 1379.75 | 0 | 0 | 0 | 3123432 | 0
1442 | 1666.4 | 0 | 0 | 0 | 0 | 1464.25 | 0 | 0 | 0 | 3054511.2 | 0
1443 | 1551.2 | 0 | 0 | 0 | 0 | 1368.25 | 0 | 0 | 0 | 2843349.6 | 0
1444 | 1624 | 0 | 0 | 0 | 0 | 1227.35 | 0 | 0 | 0 | 2976792 | 0
1445 | 1580.8 | 0 | 0 | 0 | 0 | 1367.25 | 0 | 0 | 0 | 2897606.4 | 0
1446 | 1460 | 0 | 0 | 0 | 0 | 1373.85 | 0 | 0 | 0 | 2676180 | 0
1447 | 1464 | 78.7092 | 78.7092 | 76.6203 | 76.6203 | 1569.25 | 127376.0778 | 27583.3072 | 12512.0946 | 2543066.9941 | 32306.25
1448 | 110.259 | 200.7511 | 114.5376 | 195.4233 | 110.259 | 1496.4 | 174568.2798 | 39693.24 | 18005.2947 | 0 | 55526.4324
1449 | 89.69 | 1569.5768 | 93.1704 | 1527.9211 | 89.69 | 1562 | 148519.7361 | 32288.4 | 14646.377 | 0 | 39284.22
1450 | 0 | 2642.0202 | 0 | 2571.9024 | 0 | 1396.3 | 0 | 0 | 0 | 0 | 0
1451 | 0 | 3424.7149 | 0 | 3333.8248 | 0 | 346.75 | 0 | 0 | 0 | 0 | 0
1452 | 0 | 3384.1797 | 0 | 3294.3654 | 0 | 337.7 | 0 | 0 | 0 | 0 | 0
1453 | 0 | 2609.2448 | 0 | 2539.9969 | 0 | 760.6 | 0 | 0 | 0 | 0 | 0
1454 | 87.814 | 2740.5176 | 91.2216 | 2667.7857 | 87.814 | 1218.9 | 113724.6497 | 31613.04 | 14340.0262 | 0 | 68591.5154
1455 | 71.433 | 2066.085 | 74.2049 | 2011.2522 | 71.433 | 1240.35 | 93856.5416 | 25715.88 | 11665.0089 | 0 | 54264.0785
1456 | 76.614 | 2442.1687 | 79.587 | 2377.3548 | 76.614 | 1375.2 | 111384.587 | 27581.04 | 12511.0662 | 0 | 47868.4272
1457 | 71.47 | 1369.0854 | 74.2434 | 1332.7507 | 71.47 | 1579.55 | 118966.8599 | 25729.2 | 11671.051 | 0 | 30049.5615
1458 | 83.419 | 270.5889 | 86.6561 | 263.4076 | 83.419 | 1412.4 | 124027.9648 | 30030.84 | 13622.3227 | 0 | 49017.0044
1459 | 77.625 | 80.6372 | 80.6372 | 78.4972 | 77.625 | 1409.9 | 115198.8463 | 27945 | 12676.1625 | 0 | 45806.5125
1460 | 86.4 | 89.7527 | 89.7527 | 87.3707 | 86.4 | 1422.85 | 129532.6352 | 31104 | 14109.12 | 0 | 49865.76
1461 | 79.2 | 82.2733 | 82.2733 | 80.0898 | 79.2 | 1614.45 | 134793.7741 | 28512 | 12933.36 | 0 | 30535.56
1462 | 86.4 | 89.7527 | 89.7527 | 87.3707 | 86.4 | 1726.3 | 157378.324 | 31104 | 14109.12 | 0 | 23647.68
1463 | 79.2 | 82.2733 | 82.2733 | 80.0898 | 79.2 | 1701.05 | 142550.2097 | 28512 | 12933.36 | 0 | 23676.84
1464 | 84 | 87.2596 | 87.2596 | 84.9438 | 84 | 1487.7 | 132248.4243 | 30240 | 13717.2 | 0 | 43033.2
1465 | 75.2 | 7.4971 | 7.4971 | 7.2981 | 7.2981 | 1422.25 | 10973.802 | 2627.311 | 1191.7775 | 80803.2775 | 3785.9958
1466 | 81.6 | 84.7665 | 84.7665 | 82.5168 | 81.6 | 1464.7 | 126460.8119 | 29376 | 13325.28 | 0 | 43680.48
1467 | 76 | 78.9492 | 78.9492 | 76.8539 | 76 | 1461.15 | 117706.0016 | 27360 | 12410.8 | 0 | 40952.6
1468 | 80 | 83.1044 | 83.1044 | 80.8988 | 80 | 1459.25 | 123832.3993 | 28800 | 13064 | 0 | 43260
1469 | 76.8 | 79.7802 | 79.7802 | 77.6629 | 76.8 | 1458.9 | 118753.1435 | 27648 | 12541.44 | 0 | 41556.48
1470 | 81.6 | 84.7665 | 84.7665 | 82.5168 | 81.6 | 1462.3 | 126348.5076 | 29376 | 13325.28 | 0 | 43876.32
1471 | 67.2 | 69.8077 | 69.8077 | 67.955 | 67.2 | 1469.9 | 104846.0568 | 24192 | 10973.76 | 0 | 35622.72
1472 | 79.057 | 82.1248 | 82.1248 | 79.9452 | 79.057 | 1490.1 | 124911.9001 | 28460.52 | 12910.0081 | 0 | 40311.1643
1473 | 544.574 | 813.5109 | 565.7061 | 791.9207 | 544.574 | 1531.45 | 884655.2349 | 196046.64 | 88928.9342 | 0 | 255160.1477
1474 | 1505.096 | 1990.8537 | 1563.5009 | 1938.0175 | 1505.096 | 1542.2 | 2464355.8312 | 541834.56 | 245782.1768 | 0 | 689032.9488
1475 | 1673.221 | 3027.879 | 1738.1499 | 2947.5207 | 1673.221 | 1450.45 | 2577336.4145 | 602359.56 | 273236.9893 | 0 | 919518.6006
1476 | 1557.38 | 3973.4157 | 1617.8137 | 3867.9634 | 1557.38 | 1495.5 | 2471166.8835 | 560656.8 | 254320.154 | 0 | 785698.21
1477 | 1552.097 | 4027.0617 | 1612.3257 | 3920.1856 | 1552.097 | 1396.35 | 2298103.2342 | 558754.92 | 253457.4401 | 0 | 936923.3541
1478 | 1601.467 | 3753.9942 | 1663.6115 | 3654.3652 | 1601.467 | 1419.05 | 2414229.9348 | 576528.12 | 261519.5611 | 0 | 930372.2536
1479 | 1699.22 | 3229.9016 | 1765.1578 | 3144.1818 | 1699.22 | 1324.65 | 2383227.7665 | 611719.2 | 277482.626 | 0 | 1147568.227
1480 | 1209.033 | 1810.8611 | 1255.9492 | 1762.8018 | 1209.033 | 1563.25 | 1998733.5084 | 435251.88 | 197435.0889 | 0 | 528045.1628
1481 | 1602.265 | 1352.3659 | 1352.3659 | 1316.4748 | 1316.4748 | 1563.2 | 2173578.4908 | 473930.939 | 214980.3399 | 523853.3803 | 562872.2736
1482 | 1255.783 | 258.0453 | 258.0453 | 251.1969 | 251.1969 | 1548.4 | 409611.8711 | 90430.902 | 41020.4619 | 1841406.2299 | 111040.7628
1483 | 1313.251 | 0 | 0 | 0 | 0 | 1543.05 | 0 | 0 | 0 | 4462426.898 | 0
1484 | 1345.6 | 0 | 0 | 0 | 0 | 1525.2 | 0 | 0 | 0 | 4572348.8 | 0
1485 | 1182.4 | 0 | 0 | 0 | 0 | 1430.9 | 0 | 0 | 0 | 4017795.2 | 0
1486 | 1305.6 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1512.9 | 492557.4812 | 111351.8261 | 50510.4255 | 3385391.2863 | 148991.2254
1487 | 1395.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1497.15 | 946364.1967 | 215514.4963 | 97759.7701 | 2706672.2159 | 297687.2
1488 | 1414.4 | 0 | 0 | 0 | 0 | 1432.95 | 0 | 0 | 0 | 2592595.2 | 0
1489 | 1534.4 | 0 | 0 | 0 | 0 | 860.2 | 0 | 0 | 0 | 1825936 | 0
1490 | 1493.6 | 0 | 0 | 0 | 0 | 1367.55 | 0 | 0 | 0 | 1777384 | 0
1491 | 1685.6 | 0 | 0 | 0 | 0 | 1363.3 | 0 | 0 | 0 | 2005864 | 0
1492 | 1434.4 | 0 | 0 | 0 | 0 | 1274.6 | 0 | 0 | 0 | 1706936 | 0
1493 | 1459.2 | 0 | 0 | 0 | 0 | 1058.8 | 0 | 0 | 0 | 1736448 | 0
1494 | 1717.6 | 0 | 0 | 0 | 0 | 1307.6 | 0 | 0 | 0 | 2043944 | 0
1495 | 1190.4 | 113.4011 | 113.4011 | 110.3915 | 110.3915 | 1355.75 | 158545.0539 | 39740.9459 | 18026.9346 | 1979655.5504 | 69615.078
1496 | 1580.043 | 1051.823 | 1051.823 | 1023.9082 | 1023.9082 | 1453.9 | 1579981.4985 | 368606.9661 | 167204.2154 | 1019395.0167 | 547328.1789
1497 | 1502.036 | 1560.3221 | 1560.3221 | 1518.912 | 1502.036 | 1302.25 | 2079732.8093 | 540732.96 | 245282.4788 | 0 | 1048045.619
1498 | 1441.807 | 2001.4339 | 1497.756 | 1948.317 | 1441.807 | 1245.55 | 1912350.8052 | 519050.52 | 235447.0831 | 0 | 1087771.2911
1499 | 1867.076 | 3572.6178 | 1939.5285 | 3477.8025 | 1867.076 | 1315.8 | 2612384.1234 | 672147.36 | 304893.5108 | 0 | 1277453.3992
1500 | 1969.563 | 4015.908 | 2045.9914 | 3909.328 | 1969.563 | 1282.35 | 2691434.3665 | 709042.68 | 321629.6379 | 0 | 1413456.8869
1501 | 1991.36 | 2537.3782 | 2068.6342 | 2470.0376 | 1991.36 | 724.25 | 1536185.2776 | 716889.6 | 325189.088 | 0 | 2540477.52
1502 | 1801.825 | 1728.6615 | 1728.6615 | 1682.7837 | 1682.7837 | 282 | 504707.7251 | 605802.1478 | 274798.5854 | 218202.6222 | 2840195.882
1503 | 1593.282 | 2435.5276 | 1655.1089 | 2370.89 | 1593.282 | 295.55 | 501047.3963 | 573581.52 | 260182.9506 | 0 | 2715669.5049
1504 | 1359.178 | 2414.7795 | 1411.9206 | 2350.6926 | 1359.178 | 301.3 | 434691.2474 | 489304.08 | 221953.7674 | 0 | 2308835.6686
1505 | 1889.839 | 1378.0919 | 1378.0919 | 1341.5181 | 1341.5181 | 310.05 | 438828.6367 | 482946.5075 | 219069.9019 | 1005072.2532 | 2219142.6329
1506 | 1338.014 | 267.325 | 267.325 | 260.2303 | 260.2303 | 1368 | 375518.752 | 93682.9138 | 42495.6106 | 1975577.4927 | 160986.2
1507 | 1353.885 | 0 | 0 | 0 | 0 | 1517 | 0 | 0 | 0 | 4600501.23 | 0
1508 | 1158.4 | 0 | 0 | 0 | 0 | 1503.75 | 0 | 0 | 0 | 3936243.2 | 0
1509 | 1659.2 | 0 | 0 | 0 | 0 | 1487.05 | 0 | 0 | 0 | 5637961.6 | 0
1510 | 1568 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1480.15 | 484027.9266 | 111351.8261 | 50510.4255 | 4277026.4863 | 159008.5989
1511 | 1603.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1467.85 | 930708.0126 | 215514.4963 | 97759.7701 | 3413456.2159 | 315032.8
1512 | 1517.6 | 0 | 0 | 0 | 0 | 633.75 | 0 | 0 | 0 | 2781760.8 | 0
1513 | 1664 | 0 | 0 | 0 | 0 | 1476.7 | 0 | 0 | 0 | 1980160 | 0
1514 | 1617.6 | 0 | 0 | 0 | 0 | 1065.4 | 0 | 0 | 0 | 1924944 | 0
1515 | 1648 | 0 | 0 | 0 | 0 | 911.7 | 0 | 0 | 0 | 1961120 | 0
1516 | 1176.8 | 0 | 0 | 0 | 0 | 260.85 | 0 | 0 | 0 | 1400392 | 0
1517 | 1515.2 | 0 | 0 | 0 | 0 | 510.7 | 0 | 0 | 0 | 1803088 | 0
1518 | 1512.8 | 0 | 0 | 0 | 0 | 1235.05 | 0 | 0 | 0 | 1800232 | 0
1519 | 1321.6 | 119.581 | 119.581 | 116.4074 | 116.4074 | 1535.9 | 189196.3341 | 41906.6482 | 19009.3212 | 2209118.1164 | 52881.8745
1520 | 1341.317 | 1145.3882 | 1145.3882 | 1114.9902 | 1114.9902 | 1673.3 | 1971308.1247 | 401396.4774 | 182077.9021 | 414856.9971 | 356561.6868
1521 | 1629.663 | 1692.9017 | 1692.9017 | 1647.973 | 1629.663 | 1790.65 | 3085752.22 | 586678.68 | 266123.9679 | 0 | 341169.949
1522 | 1448.199 | 2151.8092 | 1504.396 | 2094.7014 | 1448.199 | 1748.25 | 2686727.4281 | 521351.64 | 236490.8967 | 0 | 364584.0982
1523 | 1859.743 | 3764.2191 | 1931.9099 | 3664.3188 | 1859.743 | 1540.15 | 3039232.3307 | 669507.48 | 303696.0319 | 0 | 855202.8185
1524 | 1762.66 | 3972.1203 | 1831.0596 | 3866.7024 | 1762.66 | 1531.1 | 2857381.9557 | 634557.6 | 287842.378 | 0 | 826511.274
1525 | 1573.75 | 2980.1418 | 1634.819 | 2901.0504 | 1573.75 | 1517.5 | 2525475.143 | 566550 | 256993.375 | 0 | 759334.375
1526 | 1726.047 | 2844.1903 | 1793.0258 | 2768.707 | 1726.047 | 1541.65 | 2813407.8539 | 621376.92 | 281863.4751 | 0 | 791133.6424
1527 | 1828.904 | 2244.5932 | 1899.8742 | 2185.0229 | 1828.904 | 1716.35 | 3315623.4033 | 658405.44 | 298660.0232 | 0 | 518768.6196
1528 | 1697.557 | 2134.1257 | 1763.4303 | 2077.4871 | 1697.557 | 1775.2 | 3173683.5126 | 611120.52 | 277211.0581 | 0 | 381610.8136
1529 | 1829.581 | 1405.7875 | 1405.7875 | 1368.4786 | 1368.4786 | 1890.7 | 2719990.0486 | 492652.3047 | 223472.5593 | 845200.6547 | 146410.7383
1530 | 1704.422 | 284.9244 | 284.9244 | 277.3627 | 277.3627 | 1886.35 | 549504.0322 | 99850.56 | 45293.3235 | 2615799.7578 | 30855.5204
1531 | 1675.433 | 0 | 0 | 0 | 0 | 1883.85 | 0 | 0 | 0 | 5693121.334 | 0
1532 | 1698.4 | 0 | 0 | 0 | 0 | 1865.55 | 0 | 0 | 0 | 5771163.2 | 0
1533 | 1537.6 | 0 | 0 | 0 | 0 | 1850.4 | 0 | 0 | 0 | 5224764.8 | 0
1534 | 1532 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1836.3 | 597255.4342 | 111351.8261 | 50510.4255 | 4154698.4863 | 50071.5738
1535 | 1324 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1816.05 | 1144685.51 | 215514.4963 | 97759.7701 | 2464734.6159 | 108898.4
1536 | 382.4 | 0 | 0 | 0 | 0 | 1798.85 | 0 | 0 | 0 | 700939.2 | 0
1537 | 394.4 | 0 | 0 | 0 | 0 | 1783.2 | 0 | 0 | 0 | 469336 | 0
1538 | 378.4 | 0 | 0 | 0 | 0 | 1770.4 | 0 | 0 | 0 | 450296 | 0
1539 | 357.6 | 0 | 0 | 0 | 0 | 1690.2 | 0 | 0 | 0 | 425544 | 0
1540 | 367.2 | 0 | 0 | 0 | 0 | 1633.85 | 0 | 0 | 0 | 436968 | 0
1541 | 380 | 0 | 0 | 0 | 0 | 1667.2 | 0 | 0 | 0 | 452200 | 0
1542 | 397.6 | 0 | 0 | 0 | 0 | 1673.05 | 0 | 0 | 0 | 473144 | 0
1543 | 354.4 | 150.8895 | 150.8895 | 146.885 | 146.885 | 1685.7 | 261074.5913 | 52878.5931 | 23986.3174 | 380375.0301 | 45189.4254
1544 | 442.969 | 616.7124 | 460.1583 | 600.3452 | 442.969 | 1726.8 | 807100.99 | 159468.84 | 72336.8377 | 0 | 121019.1308
1545 | 1680.912 | 1746.1394 | 1746.1394 | 1699.7978 | 1680.912 | 1838.15 | 3258321.7137 | 605128.32 | 274492.9296 | 0 | 272055.6072
1546 | 1829.403 | 1900.3925 | 1900.3925 | 1849.9571 | 1829.403 | 1848.25 | 3566972.7433 | 658585.08 | 298741.5099 | 0 | 277611.9052
1547 | 1851.263 | 1923.1008 | 1923.1008 | 1872.0627 | 1851.263 | 1748.25 | 3417598.7434 | 666454.68 | 302311.2479 | 0 | 466055.4603
1548 | 1924.839 | 2633.5518 | 1999.5309 | 2563.6588 | 1924.839 | 1611.5 | 3272903.3097 | 692942.04 | 314326.2087 | 0 | 747799.9515
1549 | 1677.954 | 1852.7789 | 1743.0666 | 1803.6072 | 1677.954 | 1517.5 | 2681882.3048 | 604063.44 | 274009.8882 | 0 | 809612.805
1550 | 1718.738 | 738.5642 | 738.5642 | 718.9631 | 718.9631 | 1653.55 | 1255438.1689 | 258826.7212 | 117406.6766 | 1832587.365 | 235141.5046
1551 | 1907.596 | 1981.6198 | 1981.6198 | 1929.0287 | 1907.596 | 1773.35 | 3569739.477 | 686734.56 | 311510.4268 | 0 | 430148.3824
1552 | 1688.519 | 1754.0416 | 1754.0416 | 1707.4902 | 1688.519 | 1876.2 | 3336204.8036 | 607866.84 | 275735.1527 | 0 | 209038.6522
1553 | 2091.005 | 1317.5088 | 1317.5088 | 1282.5428 | 1282.5428 | 1890.7 | 2551965.8667 | 461715.4172 | 209439.2434 | 1481911.1657 | 137216.6409
1554 | 1608.296 | 230.8889 | 230.8889 | 224.7612 | 224.7612 | 1886.35 | 445731.7518 | 80914.0439 | 36703.5094 | 2536019.2278 | 25003.6819
1555 | 1773.255 | 0 | 0 | 0 | 0 | 1883.85 | 0 | 0 | 0 | 6025520.49 | 0
1556 | 1601.6 | 0 | 0 | 0 | 0 | 1865.55 | 0 | 0 | 0 | 5442236.8 | 0
1557 | 1201.6 | 0 | 0 | 0 | 0 | 1850.4 | 0 | 0 | 0 | 4083036.8 | 0
1558 | 1380.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1836.3 | 597591.8453 | 111351.8261 | 50510.4255 | 3640920.8863 | 50071.5738
1559 | 1320.8 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1816.05 | 1145771.1952 | 215514.4963 | 97759.7701 | 2453861.0159 | 108898.4
1560 | 361.6 | 0 | 0 | 0 | 0 | 1798.85 | 0 | 0 | 0 | 662812.8 | 0
1561 | 110.4 | 0 | 0 | 0 | 0 | 1783.2 | 0 | 0 | 0 | 131376 | 0
1562 | 116.8 | 0 | 0 | 0 | 0 | 1709 | 0 | 0 | 0 | 138992 | 0
1563 | 111.2 | 0 | 0 | 0 | 0 | 1668.7 | 0 | 0 | 0 | 132328 | 0
1564 | 113.6 | 0 | 0 | 0 | 0 | 1659.85 | 0 | 0 | 0 | 135184 | 0
1565 | 110.4 | 0 | 0 | 0 | 0 | 1635.2 | 0 | 0 | 0 | 131376 | 0
1566 | 114.4 | 0 | 0 | 0 | 0 | 1667.05 | 0 | 0 | 0 | 136136 | 0
1567 | 98.4 | 102.2184 | 102.2184 | 99.5056 | 98.4 | 1773.8 | 183722.4334 | 35424 | 16068.72 | 0 | 22258.08
1568 | 220.236 | 556.8451 | 228.7822 | 542.0667 | 220.236 | 1788.4 | 415386.4062 | 79284.96 | 35964.5388 | 0 | 46601.9376
1569 | 1212.985 | 1882.4326 | 1260.0546 | 1832.4739 | 1212.985 | 1847.15 | 2362391.0438 | 436674.6 | 198080.4505 | 0 | 185404.7573
1570 | 1238.812 | 3080.2181 | 1286.8838 | 2998.4708 | 1238.812 | 1857.25 | 2427312.8114 | 445972.32 | 202297.9996 | 0 | 176840.413
1571 | 1664.717 | 3219.4637 | 1729.3159 | 3134.0209 | 1664.717 | 1799.25 | 3163564.0306 | 599298.12 | 271848.2861 | 0 | 334191.9377
1572 | 1556.917 | 3434.4017 | 1617.3328 | 3343.2546 | 1556.917 | 1711.7 | 2819736.3846 | 560490.12 | 254244.5461 | 0 | 448859.1711
1573 | 1408.483 | 3378.8932 | 1463.1388 | 3289.2192 | 1408.483 | 1555.95 | 2309830.2886 | 507053.88 | 230005.2739 | 0 | 625436.8761
1574 | 1587.586 | 3007.9194 | 1649.1919 | 2928.0909 | 1587.586 | 1578.35 | 2650432.1926 | 571530.96 | 259252.7938 | 0 | 669405.6369
1575 | 1726.378 | 2651.4234 | 1793.3697 | 2581.0561 | 1726.378 | 1716.35 | 3131888.8056 | 621496.08 | 281917.5274 | 0 | 489687.1197
1576 | 1711.478 | 2000.7359 | 1777.8915 | 1947.6374 | 1711.478 | 1753.7 | 3167070.5381 | 616132.08 | 279484.3574 | 0 | 421537.0314
1577 | 1544.327 | 1009.1417 | 1009.1417 | 982.3596 | 982.3596 | 1890.7 | 1953878.2523 | 353649.4591 | 160419.3241 | 1030086.2282 | 105100.5847
1578 | 1402.659 | 204.388 | 204.388 | 198.9636 | 198.9636 | 1886.35 | 394517.0136 | 71626.8981 | 32490.7568 | 2206373.6575 | 22133.9058
1579 | 1439.865 | 0 | 0 | 0 | 0 | 1883.85 | 0 | 0 | 0 | 4892661.27 | 0
1580 | 1459.2 | 0 | 0 | 0 | 0 | 1865.55 | 0 | 0 | 0 | 4958361.6 | 0
1581 | 1510.4 | 0 | 0 | 0 | 0 | 1850.4 | 0 | 0 | 0 | 5132339.2 | 0
1582 | 1384 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1836.3 | 595915.3325 | 111351.8261 | 50510.4255 | 3651794.4863 | 50071.5738
1583 | 1400 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1816.05 | 1143457.2564 | 215514.4963 | 97759.7701 | 2722982.6159 | 108898.4
1584 | 472 | 0 | 0 | 0 | 0 | 1798.85 | 0 | 0 | 0 | 865176 | 0
1585 | 416.8 | 0 | 0 | 0 | 0 | 1661.85 | 0 | 0 | 0 | 495992 | 0
1586 | 390.4 | 0 | 0 | 0 | 0 | 1760.4 | 0 | 0 | 0 | 464576 | 0
1587 | 431.2 | 0 | 0 | 0 | 0 | 1668.7 | 0 | 0 | 0 | 513128 | 0
1588 | 381.6 | 0 | 0 | 0 | 0 | 1663.35 | 0 | 0 | 0 | 454104 | 0
1589 | 384 | 0 | 0 | 0 | 0 | 1660.2 | 0 | 0 | 0 | 456960 | 0
1590 | 484.8 | 0 | 0 | 0 | 0 | 1662.55 | 0 | 0 | 0 | 576912 | 0
1591 | 424 | 130.1674 | 130.1674 | 126.7129 | 126.7129 | 1685.7 | 224718.8108 | 45616.6283 | 20692.2094 | 544927.3342 | 38983.2576
1592 | 433.137 | 531.9179 | 449.9448 | 517.8011 | 433.137 | 1705.3 | 779140.08 | 155929.32 | 70731.2721 | 0 | 127645.4739
1593 | 1644.823 | 1795.4151 | 1708.6499 | 1747.7657 | 1644.823 | 1847.15 | 3205339.2993 | 592136.28 | 268599.5959 | 0 | 251411.1955
1594 | 1786.904 | 2962.9433 | 1856.2444 | 2884.3084 | 1786.904 | 1805.75 | 3412697.008 | 643285.44 | 291801.4232 | 0 | 347106.102
1595 | 1792.2 | 3400.5917 | 1861.7459 | 3310.3419 | 1792.2 | 1718.25 | 3265244.9072 | 645192 | 292666.26 | 0 | 504952.35
1596 | 1606.691 | 3694.2868 | 1669.0382 | 3596.2424 | 1606.691 | 1611.5 | 2745784.8534 | 578408.76 | 262372.6403 | 0 | 624199.4535
1597 | 1894.24 | 3731.7814 | 1967.7455 | 3632.742 | 1894.24 | 1517.5 | 3046860.4851 | 681926.4 | 309329.392 | 0 | 913970.8
1598 | 1829.242 | 3334.6152 | 1900.2253 | 3246.1163 | 1829.242 | 1541.9 | 2995254.1788 | 658527.12 | 298715.2186 | 0 | 837975.7602
1599 | 1903.518 | 3046.6917 | 1977.3835 | 2965.8342 | 1903.518 | 1716.35 | 3464934.0142 | 685266.48 | 310844.4894 | 0 | 539932.8807
1600 | 1476.616 | 2281.13 | 1533.9157 | 2220.5901 | 1476.616 | 1776.2 | 2774103.1115 | 531581.76 | 241131.3928 | 0 | 330466.6608
1601 | 1535.769 | 1247.6232 | 1247.6232 | 1214.512 | 1214.512 | 1886.2 | 2418195.2534 | 437224.3062 | 198329.8033 | 588864.1514 | 135287.8298
1602 | 1485.795 | 217.1621 | 217.1621 | 211.3988 | 211.3988 | 1886.35 | 420727.7279 | 76103.5565 | 34521.4188 | 2335968.2932 | 23517.2536
1603 | 1357.077 | 0 | 0 | 0 | 0 | 1883.85 | 0 | 0 | 0 | 4611347.646 | 0
1604 | 1589.6 | 0 | 0 | 0 | 0 | 1865.55 | 0 | 0 | 0 | 5401460.8 | 0
1605 | 1525.6 | 0 | 0 | 0 | 0 | 1798.9 | 0 | 0 | 0 | 5183988.8 | 0
1606 | 1258.4 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1836.3 | 600101.3033 | 111351.8261 | 50510.4255 | 3225005.6863 | 50071.5738
1607 | 1140 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1796.6 | 1136148.8683 | 215514.4963 | 97759.7701 | 1839502.6159 | 120412.8
1608 | 1290.4 | 0 | 0 | 0 | 0 | 1667.35 | 0 | 0 | 0 | 2365303.2 | 0
1609 | 1470.4 | 0 | 0 | 0 | 0 | 1504.05 | 0 | 0 | 0 | 2695243.2 | 0
1610 | 904.8 | 0 | 0 | 0 | 0 | 1532.45 | 0 | 0 | 0 | 1658498.4 | 0
1611 | 1167.2 | 0 | 0 | 0 | 0 | 1495 | 0 | 0 | 0 | 2139477.6 | 0
1612 | 1140.8 | 0 | 0 | 0 | 0 | 1454.25 | 0 | 0 | 0 | 2091086.4 | 0
1613 | 1201.6 | 0 | 0 | 0 | 0 | 1454.6 | 0 | 0 | 0 | 2202532.8 | 0
1614 | 1211.2 | 0 | 0 | 0 | 0 | 1533.1 | 0 | 0 | 0 | 2220129.6 | 0
1615 | 1014.4 | 122.7628 | 122.7628 | 119.5048 | 119.5048 | 1587.35 | 200870.0682 | 43021.7173 | 19515.129 | 1640342.9562 | 48270.5591
1616 | 337.397 | 511.201 | 350.4896 | 497.634 | 337.397 | 1648.3 | 589461.2632 | 121462.92 | 55096.9301 | 0 | 118662.5249
1617 | 274.291 | 1785.8518 | 284.9348 | 1738.4563 | 274.291 | 1734.65 | 505385.6312 | 98744.76 | 44791.7203 | 0 | 72783.1168
1618 | 264.437 | 3010.0666 | 274.6984 | 2930.1811 | 264.437 | 1655.8 | 465971.8187 | 95197.32 | 43182.5621 | 0 | 91019.2154
1619 | 281.379 | 3521.7455 | 292.2978 | 3428.2803 | 281.379 | 1540.15 | 459916.2867 | 101296.44 | 45949.1907 | 0 | 129392.1331
1620 | 297.305 | 3801.0583 | 308.8418 | 3700.1802 | 297.305 | 1531.1 | 482547.7612 | 107029.8 | 48549.9065 | 0 | 139406.3145
1621 | 288.999 | 3546.04 | 300.2135 | 3451.93 | 288.999 | 1517.5 | 465207.8587 | 104039.64 | 47193.5367 | 0 | 139442.0175
1622 | 276.252 | 2765.0261 | 286.9719 | 2691.6438 | 276.252 | 1539.3 | 451671.6345 | 99450.72 | 45111.9516 | 0 | 127269.2964
1623 | 267.096 | 1337.3209 | 277.4606 | 1301.8291 | 267.096 | 1560.75 | 442367.1557 | 96154.56 | 43616.7768 | 0 | 117321.918
1624 | 204.599 | 1298.7023 | 212.5384 | 1264.2354 | 204.599 | 1608.55 | 348955.9378 | 73655.64 | 33411.0167 | 0 | 80090.2786
1625 | 286.349 | 925.9906 | 297.4607 | 901.4153 | 286.349 | 1759.2 | 533733.3267 | 103085.64 | 46760.7917 | 0 | 68952.8392
1626 | 229.93 | 179.5553 | 179.5553 | 174.79 | 174.79 | 1754.85 | 324813.4057 | 62924.4082 | 28543.2107 | 101071.5783 | 41943.2038
1627 | 205.13 | 0 | 0 | 0 | 0 | 1752.35 | 0 | 0 | 0 | 376003.29 | 0
1628 | 299.2 | 0 | 0 | 0 | 0 | 1718.55 | 0 | 0 | 0 | 548433.6 | 0
1629 | 287.2 | 218.8492 | 218.8492 | 213.041 | 213.041 | 1677.45 | 377427.456 | 76694.7652 | 34789.5976 | 135933.4207 | 67952.8987
1630 | 292 | 303.331 | 303.331 | 295.2807 | 292 | 1733.3 | 534785.3217 | 105120 | 47683.6 | 0 | 77876.4
1631 | 230.4 | 239.3406 | 239.3406 | 232.9886 | 230.4 | 1709.55 | 415878.2285 | 82944 | 37624.32 | 0 | 66919.68
1632 | 164.8 | 171.195 | 171.195 | 166.6516 | 164.8 | 1597.4 | 277655.585 | 59328 | 26911.84 | 0 | 66348.48
1633 | 195.2 | 0 | 0 | 0 | 0 | 1505.35 | 0 | 0 | 0 | 232288 | 0
1634 | 238.4 | 0 | 0 | 0 | 0 | 1536.4 | 0 | 0 | 0 | 283696 | 0
1635 | 187.2 | 0 | 0 | 0 | 0 | 1466.35 | 0 | 0 | 0 | 222768 | 0
1636 | 148.8 | 0 | 0 | 0 | 0 | 1459.25 | 0 | 0 | 0 | 177072 | 0
1637 | 132.8 | 0 | 0 | 0 | 0 | 1458.9 | 0 | 0 | 0 | 158032 | 0
1638 | 192.8 | 0 | 0 | 0 | 0 | 1462.3 | 0 | 0 | 0 | 229432 | 0
1639 | 120 | 124.6566 | 124.6566 | 121.3483 | 120 | 1469.9 | 186237.3321 | 43200 | 19596 | 0 | 63612
1640 | 191.45 | 543.4143 | 198.8792 | 528.9924 | 191.45 | 1528.8 | 309927.5723 | 68922 | 31263.785 | 0 | 90211.24
1641 | 866.164 | 1828.3317 | 899.7763 | 1779.8088 | 866.164 | 1684.95 | 1550234.6983 | 311819.04 | 141444.5812 | 0 | 272884.9682
1642 | 1455.515 | 3037.034 | 1511.9959 | 2956.4328 | 1455.515 | 1612.4 | 2494418.5972 | 523985.4 | 237685.5995 | 0 | 564157.614
1643 | 1743.462 | 3556.881 | 1811.1166 | 3462.4833 | 1743.462 | 1536.15 | 2839336.8279 | 627646.32 | 284707.3446 | 0 | 808704.8487
1644 | 1648.641 | 3809.4798 | 1712.6161 | 3708.3783 | 1648.641 | 1442.5 | 2521308.4694 | 593510.76 | 269223.0753 | 0 | 919117.3575
1645 | 1680.833 | 3813.8085 | 1746.0573 | 3712.5921 | 1680.833 | 1428.05 | 2541929.9041 | 605099.88 | 274480.0289 | 0 | 961352.4343
1646 | 1635.438 | 3581.0571 | 1698.9008 | 3486.0178 | 1635.438 | 1429.3 | 2476783.5205 | 588757.68 | 267067.0254 | 0 | 933344.4666
1647 | 1660.537 | 3074.8953 | 1724.9737 | 2993.2893 | 1660.537 | 1555.55 | 2738356.3656 | 597793.32 | 271165.6921 | 0 | 738025.6697
1648 | 1717.571 | 2319.3404 | 1784.2209 | 2257.7864 | 1717.571 | 1565.85 | 2837888.2256 | 618325.56 | 280479.3443 | 0 | 745683.4497
1649 | 1588.152 | 1273.2786 | 1273.2786 | 1239.4864 | 1239.4864 | 1676.9 | 2192729.0984 | 446215.1195 | 202408.1362 | 639103.9656 | 392006.5677
1650 | 1863.569 | 224.868 | 224.868 | 218.9001 | 218.9001 | 1652.55 | 381423.9103 | 78804.0405 | 35746.3884 | 3014678.0708 | 74448.1115
1651 | 1540.524 | 0 | 0 | 0 | 0 | 1615.4 | 0 | 0 | 0 | 5234700.552 | 0
1652 | 1230.4 | 0 | 0 | 0 | 0 | 1561.65 | 0 | 0 | 0 | 4180899.2 | 0
1653 | 1436 | 0 | 0 | 0 | 0 | 1518.7 | 0 | 0 | 0 | 4879528 | 0
1654 | 1564.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1581.1 | 514688.7431 | 111351.8261 | 50510.4255 | 4266152.8863 | 128130.6186
1655 | 1647.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1567.95 | 989515.8213 | 215514.4963 | 97759.7701 | 3562968.2159 | 255773.6
1656 | 1421.6 | 0 | 0 | 0 | 0 | 1552.5 | 0 | 0 | 0 | 2605792.8 | 0
1657 | 1376.8 | 0 | 0 | 0 | 0 | 1534.7 | 0 | 0 | 0 | 1638392 | 0
1658 | 1502.4 | 0 | 0 | 0 | 0 | 1534.85 | 0 | 0 | 0 | 1787856 | 0
1659 | 1624 | 0 | 0 | 0 | 0 | 1457.7 | 0 | 0 | 0 | 1932560 | 0
1660 | 1292.8 | 0 | 0 | 0 | 0 | 1289.6 | 0 | 0 | 0 | 1538432 | 0
1661 | 1245.6 | 0 | 0 | 0 | 0 | 1453.2 | 0 | 0 | 0 | 1482264 | 0
1662 | 1281.6 | 0 | 0 | 0 | 0 | 1452 | 0 | 0 | 0 | 1525104 | 0
1663 | 1044.8 | 85.7409 | 85.7409 | 83.4654 | 83.4654 | 1450.15 | 127588.5313 | 30047.5262 | 13629.8917 | 1762126.4126 | 44922.745
1664 | 1268.07 | 1109.8039 | 1109.8039 | 1080.3503 | 1080.3503 | 1453.9 | 1660190.704 | 388926.1242 | 176421.2113 | 344090.1276 | 577499.1117
1665 | 1664.469 | 1729.0583 | 1729.0583 | 1683.17 | 1664.469 | 1467.65 | 2584302.8274 | 599208.84 | 271807.7877 | 0 | 886080.0721
1666 | 1354.034 | 2462.5604 | 1406.5769 | 2397.2054 | 1354.034 | 1475.95 | 2122103.9815 | 487452.24 | 221113.7522 | 0 | 709581.5177
1667 | 1675.929 | 1740.963 | 1740.963 | 1694.7588 | 1675.929 | 1482.2 | 2643340.1896 | 603334.44 | 273679.2057 | 0 | 867796.0362
1668 | 1404.339 | 3406.5483 | 1458.834 | 3316.1403 | 1404.339 | 1476.75 | 2206472.9633 | 505562.04 | 229328.5587 | 0 | 734820.3818
1669 | 1405.495 | 4051.6107 | 1460.0349 | 3944.0831 | 1405.495 | 1361 | 2028506.831 | 505978.2 | 229517.3335 | 0 | 898111.305
1670 | 1385.337 | 3486.4334 | 1439.0947 | 3393.9053 | 1385.337 | 1221.05 | 1796403.1757 | 498721.32 | 226225.5321 | 0 | 1079108.2562
1671 | 1426.323 | 3325.3885 | 1481.6711 | 3237.1345 | 1426.323 | 1084.6 | 1642900.2223 | 513476.28 | 232918.5459 | 0 | 1305656.0742
1672 | 1546.268 | 2503.4613 | 1606.2705 | 2437.0208 | 1546.268 | 1231.3 | 2015951.8613 | 556656.48 | 252505.5644 | 0 | 1188616.2116
1673 | 1512.557 | 1409.176 | 1409.176 | 1371.7773 | 1371.7773 | 1503.45 | 2178484.0446 | 493839.8187 | 224011.2289 | 258049.2373 | 666747.478
1674 | 1715.266 | 278.7799 | 278.7799 | 271.3812 | 271.3812 | 1517.8 | 432885.9995 | 97697.2353 | 44316.5515 | 2646640.8216 | 128092.0902
1675 | 1546.02 | 0 | 0 | 0 | 0 | 1631.25 | 0 | 0 | 0 | 5253375.96 | 0
1676 | 1220 | 0 | 0 | 0 | 0 | 1605.9 | 0 | 0 | 0 | 4145560 | 0
1677 | 1550.4 | 0 | 0 | 0 | 0 | 1559.95 | 0 | 0 | 0 | 5268259.2 | 0
1678 | 1778.4 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1553.05 | 506718.4075 | 111351.8261 | 50510.4255 | 4991965.6863 | 136710.3843
1679 | 1676.8 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1540.75 | 971860.734 | 215514.4963 | 97759.7701 | 3663549.0159 | 271876
1680 | 1480.8 | 0 | 0 | 0 | 0 | 1480.5 | 0 | 0 | 0 | 2714306.4 | 0
1681 | 1334.4 | 0 | 0 | 0 | 0 | 1504.05 | 0 | 0 | 0 | 1587936 | 0
1682 | 1472 | 0 | 0 | 0 | 0 | 1280.9 | 0 | 0 | 0 | 1751680 | 0
1683 | 1444.8 | 0 | 0 | 0 | 0 | 1277.7 | 0 | 0 | 0 | 1719312 | 0
1684 | 230.4 | 0 | 0 | 0 | 0 | 1199.9 | 0 | 0 | 0 | 274176 | 0
1685 | 354.4 | 0 | 0 | 0 | 0 | 1195.25 | 0 | 0 | 0 | 421736 | 0
1686 | 880.8 | 0 | 0 | 0 | 0 | 1156.05 | 0 | 0 | 0 | 1048152 | 0
1687 | 1391.249 | 188.4205 | 188.4205 | 183.4199 | 183.4199 | 1383.4 | 267586.8985 | 66031.1661 | 29952.4706 | 2213950.7294 | 110704.364
1688 | 1367.166 | 1291.5937 | 1291.5937 | 1257.3155 | 1257.3155 | 1606.95 | 2132583.0503 | 452633.5927 | 205319.6269 | 201355.902 | 483734.1029
1689 | 1114.978 | 1847.7116 | 1158.2444 | 1798.6744 | 1114.978 | 1738.15 | 2047808.7377 | 401392.08 | 182075.9074 | 0 | 291956.9893
1690 | 991.078 | 2927.2302 | 1029.5365 | 2849.5431 | 991.078 | 1697.25 | 1778350.4047 | 356788.08 | 161843.0374 | 0 | 300048.8645
1691 | 1722.516 | 3930.8756 | 1789.3578 | 3826.5523 | 1722.516 | 1540.15 | 2804027.9633 | 620105.76 | 281286.8628 | 0 | 792098.9826
1692 | 1259.699 | 4212.8789 | 1308.5813 | 4101.0714 | 1259.699 | 1531.1 | 2039593.1679 | 453491.64 | 205708.8467 | 0 | 590672.8611
1693 | 1018.275 | 4219.4088 | 1057.7889 | 4107.428 | 1018.275 | 1517.5 | 1633890.7867 | 366579 | 166284.3075 | 0 | 491317.6875
1694 | 905.101 | 3847.4648 | 940.2232 | 3745.3552 | 905.101 | 1575.75 | 1507100.0264 | 325836.36 | 147802.9933 | 0 | 383989.0993
1695 | 1153.41 | 3443.2368 | 1198.1678 | 3351.8551 | 1153.41 | 1706.85 | 2075917.2481 | 415227.6 | 188351.853 | 0 | 338122.1415
1696 | 1638.025 | 2617.146 | 1701.5881 | 2547.6884 | 1638.025 | 1753.7 | 3031490.0054 | 589689 | 267489.4825 | 0 | 403445.5575
1697 | 1603.774 | 1485.8513 | 1485.8513 | 1446.4176 | 1446.4176 | 1783.2 | 2720615.3866 | 520710.3263 | 236199.9897 | 288434.3306 | 306949.9928
1698 | 1509.175 | 297.7931 | 297.7931 | 289.8899 | 289.8899 | 1751.35 | 534734.2351 | 104360.3465 | 47339.0127 | 2234949.6774 | 70556.4267
1699 | 994.822 | 0 | 0 | 0 | 0 | 1774.85 | 0 | 0 | 0 | 3380405.156 | 0
1700 | 1233.6 | 0 | 0 | 0 | 0 | 1762.55 | 0 | 0 | 0 | 4191772.8 | 0
1701 | 1465.6 | 0 | 0 | 0 | 0 | 1764.4 | 0 | 0 | 0 | 4980108.8 | 0
1702 | 1463.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1836.3 | 598813.0455 | 111351.8261 | 50510.4255 | 3920916.0863 | 50071.5738
1703 | 1261.6 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1806 | 1140186.9137 | 215514.4963 | 97759.7701 | 2252699.4159 | 114848
1704 | 1423.2 | 0 | 0 | 0 | 0 | 1667.35 | 0 | 0 | 0 | 2608725.6 | 0
1705 | 1556.8 | 0 | 0 | 0 | 0 | 1623.2 | 0 | 0 | 0 | 1852592 | 0
1706 | 1232.8 | 0 | 0 | 0 | 0 | 1580.4 | 0 | 0 | 0 | 1467032 | 0
1707 | 1564 | 0 | 0 | 0 | 0 | 1534.7 | 0 | 0 | 0 | 1861160 | 0
1708 | 1275.2 | 0 | 0 | 0 | 0 | 1532.85 | 0 | 0 | 0 | 1517488 | 0
1709 | 1312.8 | 0 | 0 | 0 | 0 | 1533.2 | 0 | 0 | 0 | 1562232 | 0
1710 | 1168 | 0 | 0 | 0 | 0 | 1539.05 | 0 | 0 | 0 | 1389920 | 0
1711 | 1272.8 | 206.9195 | 206.9195 | 201.428 | 201.428 | 1651.2 | 350443.4631 | 72514.0752 | 32893.1902 | 1963824.9005 | 68771.8496
1712 | 922.415 | 958.2091 | 958.2091 | 932.7787 | 922.415 | 1648.3 | 1605032.6176 | 332069.4 | 150630.3695 | 0 | 324413.3555
1713 | 1110.192 | 1901.3576 | 1153.2727 | 1850.8966 | 1110.192 | 1740.65 | 2042222.63 | 399669.12 | 181294.3536 | 0 | 287928.2952
1714 | 1567.16 | 3296.3892 | 1627.9732 | 3208.9049 | 1567.16 | 1719.75 | 2853083.7097 | 564177.6 | 255917.228 | 0 | 439196.59
1715 | 1212.443 | 3827.7888 | 1259.4915 | 3726.2013 | 1212.443 | 1579.45 | 2026709.8578 | 436479.48 | 197991.9419 | 0 | 509892.9036
1716 | 1091.61 | 4087.5679 | 1133.9697 | 3979.086 | 1091.61 | 1531.1 | 1766444.0677 | 392979.6 | 178259.913 | 0 | 511855.929
1717 | 971.536 | 4108.1954 | 1009.2362 | 3999.1662 | 971.536 | 1590.4 | 1631767.9344 | 349752.96 | 158651.8288 | 0 | 397941.1456
1718 | 1055.456 | 3401.402 | 1096.4127 | 3311.1307 | 1055.456 | 1578.6 | 1759744.091 | 379964.16 | 172355.9648 | 0 | 444769.1584
1719 | 957.674 | 3347.407 | 994.8363 | 3258.5687 | 957.674 | 1639.35 | 1656678.8231 | 344762.64 | 156388.1642 | 0 | 345385.1281
1720 | 997.558 | 2529.394 | 1036.268 | 2462.2653 | 997.558 | 1645.35 | 1731032.8588 | 359120.88 | 162901.2214 | 0 | 353783.9447
1721 | 1166.299 | 1421.6604 | 1211.5569 | 1383.9303 | 1166.299 | 1692.2 | 2079344.8033 | 419867.64 | 190456.6267 | 0 | 358986.8322
1722 | 1040.947 | 282.4822 | 282.4822 | 274.9853 | 274.9853 | 1726.35 | 499966.3078 | 98994.6908 | 44905.0917 | 1404007.8836 | 73657.8232
1723 | 1287.915 | 0 | 0 | 0 | 0 | 1780.85 | 0 | 0 | 0 | 4376335.17 | 0
1724 | 1227.2 | 0 | 0 | 0 | 0 | 1865.45 | 0 | 0 | 0 | 4170025.6 | 0
1725 | 1147.2 | 0 | 0 | 0 | 0 | 1820.4 | 0 | 0 | 0 | 3898185.6 | 0
1726 | 1378.4 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1836.3 | 599102.5898 | 111351.8261 | 50510.4255 | 3632765.6863 | 50071.5738
1727 | 1175.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1806.6 | 1140629.8088 | 215514.4963 | 97759.7701 | 1959112.2159 | 114492.8
1728 | 160.8 | 0 | 0 | 0 | 0 | 1691.35 | 0 | 0 | 0 | 294746.4 | 0
1729 | 104.8 | 0 | 0 | 0 | 0 | 1768.25 | 0 | 0 | 0 | 124712 | 0
1730 | 106.4 | 0 | 0 | 0 | 0 | 1667.9 | 0 | 0 | 0 | 126616 | 0
1731 | 102.4 | 0 | 0 | 0 | 0 | 1611.7 | 0 | 0 | 0 | 121856 | 0
1732 | 108 | 0 | 0 | 0 | 0 | 1559 | 0 | 0 | 0 | 128520 | 0
1733 | 101.6 | 0 | 0 | 0 | 0 | 1527.5 | 0 | 0 | 0 | 120904 | 0
1734 | 104 | 0 | 0 | 0 | 0 | 1574.7 | 0 | 0 | 0 | 123760 | 0
1735 | 86.785 | 90.1527 | 90.1527 | 87.7601 | 86.785 | 1722.3 | 157630.2288 | 31242.6 | 14171.9905 | 0 | 24100.1945
1736 | 102.491 | 772.6765 | 106.4681 | 752.1701 | 102.491 | 1741.9 | 188514.8622 | 36896.76 | 16736.7803 | 0 | 26452.9271
1737 | 1053.719 | 2281.3804 | 1094.6083 | 2220.8338 | 1053.719 | 1837.15 | 2046129.1877 | 379338.84 | 172072.3127 | 0 | 171598.1391
1738 | 1351.25 | 3442.9885 | 1403.6849 | 3351.6135 | 1351.25 | 1754.25 | 2510353.1984 | 486450 | 220659.125 | 0 | 332069.6875
1739 | 1014.359 | 4003.0746 | 1053.7209 | 3896.8352 | 1014.359 | 1613.05 | 1731675.2307 | 365169.24 | 165644.8247 | 0 | 392506.215
1740 | 1130.671 | 2479.3205 | 1174.5464 | 2413.5207 | 1130.671 | 1645.35 | 1969508.1355 | 407041.56 | 184638.5743 | 0 | 400992.4702
1741 | 1327.615 | 2993.7678 | 1379.1328 | 2914.3148 | 1327.615 | 1673.1 | 2351998.651 | 477941.4 | 216799.5295 | 0 | 433997.3435
1742 | 1312.509 | 4036.6062 | 1363.4406 | 3929.4769 | 1312.509 | 1782.5 | 2480676.9519 | 472503.24 | 214332.7197 | 0 | 285470.7075
1743 | 1182.509 | 3501.5438 | 1228.396 | 3408.6148 | 1182.509 | 1773.35 | 2216686.8874 | 425703.24 | 193103.7197 | 0 | 268015.6649
1744 | 1270.68 | 2659.8575 | 1319.9884 | 2589.2663 | 1270.68 | 1782.2 | 2390060.0577 | 457444.8 | 207502.044 | 0 | 276754.104
1745 | 1403.753 | 1508.8213 | 1458.2253 | 1468.778 | 1403.753 | 1809.2 | 2676190.1049 | 505351.08 | 229232.8649 | 0 | 267836.0724
1746 | 1739.825 | 301.029 | 301.029 | 293.0398 | 293.0398 | 1856.3 | 572340.2605 | 105494.3459 | 47853.4075 | 2651957.1804 | 41219.0517
1747 | 1588.775 | 0 | 0 | 0 | 0 | 1883.35 | 0 | 0 | 0 | 5398657.45 | 0
1748 | 1500.8 | 0 | 0 | 0 | 0 | 1865.55 | 0 | 0 | 0 | 5099718.4 | 0
1749 | 1536 | 0 | 0 | 0 | 0 | 1850.4 | 0 | 0 | 0 | 5219328 | 0
1750 | 1589.6 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1836.3 | 597449.5357 | 111351.8261 | 50510.4255 | 4350423.2863 | 50071.5738
1751 | 1916 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1816.05 | 1146398.2162 | 215514.4963 | 97759.7701 | 4476350.6159 | 108898.4
1752 | 192 | 0 | 0 | 0 | 0 | 1798.85 | 0 | 0 | 0 | 351936 | 0
1753 | 107.2 | 0 | 0 | 0 | 0 | 1783.05 | 0 | 0 | 0 | 127568 | 0
1754 | 116 | 0 | 0 | 0 | 0 | 1765.4 | 0 | 0 | 0 | 138040 | 0
1755 | 110.4 | 0 | 0 | 0 | 0 | 1690.2 | 0 | 0 | 0 | 131376 | 0
1756 | 110.4 | 0 | 0 | 0 | 0 | 1666.85 | 0 | 0 | 0 | 131376 | 0
1757 | 108 | 0 | 0 | 0 | 0 | 1667.2 | 0 | 0 | 0 | 128520 | 0
1758 | 110.4 | 0 | 0 | 0 | 0 | 1673.05 | 0 | 0 | 0 | 131376 | 0
1759 | 103.221 | 107.2265 | 107.2265 | 104.3807 | 103.221 | 1783.65 | 194162.1436 | 37159.56 | 16855.9893 | 0 | 22331.8633
1760 | 126.773 | 830.6397 | 131.6924 | 808.595 | 126.773 | 1726.8 | 231153.158 | 45638.28 | 20702.0309 | 0 | 34634.3836
1761 | 999.966 | 2319.4256 | 1038.7694 | 2257.8693 | 999.966 | 1832.7 | 1934852.8187 | 359987.76 | 163294.4478 | 0 | 167294.3118
1762 | 1972.895 | 3525.2525 | 2049.4527 | 3431.6942 | 1972.895 | 1796.3 | 3750582.1136 | 710242.2 | 322173.7535 | 0 | 401878.7115
1763 | 1497.263 | 4074.3023 | 1555.3639 | 3966.1726 | 1497.263 | 1686.25 | 2668672.8375 | 539014.68 | 244503.0479 | 0 | 469766.2663
1764 | 1447.357 | 4114.6474 | 1503.5213 | 4005.4469 | 1447.357 | 1667.7 | 2545173.8163 | 521048.52 | 236353.3981 | 0 | 480956.7311
1765 | 1492.397 | 4350.1081 | 1550.3091 | 4234.6586 | 1492.397 | 1673.1 | 2631286.8641 | 537262.92 | 243708.4301 | 0 | 487864.5793
1766 | 1665.983 | 4015.3221 | 1730.6311 | 3908.7577 | 1665.983 | 1624.9 | 2858014.4876 | 599753.88 | 272055.0239 | 0 | 624910.2233
1767 | 1335.156 | 3382.6838 | 1386.9664 | 3292.9092 | 1335.156 | 1716.35 | 2416460.0696 | 480656.16 | 218030.9748 | 0 | 378716.9994
1768 | 1587.901 | 2544.2738 | 1649.5191 | 2476.7502 | 1587.901 | 1747.7 | 2920624.9363 | 571644.36 | 259304.2333 | 0 | 400627.4223
1769 | 1409.122 | 1388.643 | 1388.643 | 1351.7892 | 1351.7892 | 1781.7 | 2532001.1284 | 486644.1101 | 220747.1755 | 105091.0323 | 288853.2502
1770 | 1956.792 | 264.5628 | 264.5628 | 257.5414 | 257.5414 | 1804.85 | 489127.8044 | 92714.9188 | 42056.5173 | 3114726.2747 | 49196.1441
1771 | 1705.486 | 0 | 0 | 0 | 0 | 1868.9 | 0 | 0 | 0 | 5795241.428 | 0
1772 | 1647.2 | 0 | 0 | 0 | 0 | 1814 | 0 | 0 | 0 | 5597185.6 | 0
1773 | 1580.8 | 0 | 0 | 0 | 0 | 1789.45 | 0 | 0 | 0 | 5371558.4 | 0
1774 | 1783.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1836.25 | 598244.0091 | 111351.8261 | 50510.4255 | 5008276.0863 | 50086.8675
1775 | 1466.4 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1816 | 1146881.4314 | 215514.4963 | 97759.7701 | 2948609.8159 | 108928
1776 | 1642.4 | 0 | 0 | 0 | 0 | 1798.85 | 0 | 0 | 0 | 3010519.2 | 0
1777 | 1504 | 0 | 0 | 0 | 0 | 1778.15 | 0 | 0 | 0 | 2756832 | 0
1778 | 1396 | 0 | 0 | 0 | 0 | 1755.5 | 0 | 0 | 0 | 2558868 | 0
1779 | 1258.4 | 0 | 0 | 0 | 0 | 1668.7 | 0 | 0 | 0 | 2306647.2 | 0
1780 | 1348.8 | 0 | 0 | 0 | 0 | 1666.85 | 0 | 0 | 0 | 2472350.4 | 0
1781 | 1135.2 | 0 | 0 | 0 | 0 | 1667.2 | 0 | 0 | 0 | 2080821.6 | 0
1782 | 1196.8 | 0 | 0 | 0 | 0 | 1673.05 | 0 | 0 | 0 | 2193734.4 | 0
1783 | 1208.997 | 200.5319 | 200.5319 | 195.2099 | 195.2099 | 1783.65 | 366892.0133 | 70275.564 | 31877.7767 | 1858271.7544 | 41340.3743
1784 | 230.659 | 701.3656 | 239.6097 | 682.7518 | 230.659 | 1741.9 | 423726.3689 | 83037.24 | 37666.6147 | 0 | 59533.0879
1785 | 288.152 | 1964.4546 | 299.3337 | 1912.319 | 288.152 | 1838.15 | 560205.9718 | 103734.72 | 47055.2216 | 0 | 46637.4012
1786 | 332.224 | 3313.0174 | 345.1159 | 3225.0917 | 332.224 | 1749.75 | 615201.8946 | 119600.64 | 54252.1792 | 0 | 83139.056
1787 | 287.755 | 3885.6814 | 298.9213 | 3782.5575 | 287.755 | 1695.75 | 515177.2212 | 103591.8 | 46990.3915 | 0 | 87549.4587
1788 | 233.034 | 4187.7564 | 242.0768 | 4076.6157 | 233.034 | 1642.25 | 404026.7812 | 83892.24 | 38054.4522 | 0 | 83367.9135
1789 | 257.376 | 4189.7499 | 267.3634 | 4078.5562 | 257.376 | 1638.15 | 445022.4743 | 92655.36 | 42029.5008 | 0 | 93131.5056
1790 | 254.785 | 3891.6368 | 264.6719 | 3788.3549 | 254.785 | 1625 | 437648.0476 | 91722.6 | 41606.3905 | 0 | 95544.375
1791 | 276.33 | 3334.8219 | 287.0529 | 3246.3175 | 276.33 | 1744.85 | 509984.4516 | 99478.8 | 45124.689 | 0 | 70505.5995
1792 | 204.693 | 2473.4357 | 212.6361 | 2407.792 | 204.693 | 1828.7 | 393975.7451 | 73689.48 | 33426.3669 | 0 | 35063.9109
1793 | 301.357 | 1266.4598 | 313.0511 | 1232.8487 | 301.357 | 1885.7 | 597201.1858 | 108488.52 | 49211.5981 | 0 | 34445.1051
1794 | 228.211 | 249.3994 | 237.0667 | 242.7804 | 228.211 | 1886.25 | 452289.7892 | 82155.96 | 37266.8563 | 0 | 25959.0012
1795 | 216.305 | 0 | 0 | 0 | 0 | 1883.85 | 0 | 0 | 0 | 396487.065 | 0
1796 | 242.4 | 0 | 0 | 0 | 0 | 1865.55 | 0 | 0 | 0 | 444319.2 | 0
1797 | 200.8 | 44.33 | 44.33 | 43.1535 | 43.1535 | 1850.35 | 83894.635 | 15535.246 | 7046.9602 | 288966.1059 | 6386.1641
1798 | 296 | 307.4862 | 307.4862 | 299.3257 | 296 | 1836.3 | 571472.3542 | 106560 | 48336.8 | 0 | 48455.2
1799 | 268 | 278.3997 | 278.3997 | 271.0111 | 268 | 1816.05 | 513126.2169 | 96480 | 43764.4 | 0 | 49298.6
1800 | 291.2 | 302.4999 | 302.4999 | 294.4718 | 291.2 | 1798.8 | 552656.2184 | 104832 | 47552.96 | 0 | 58589.44
1801 | 237.6 | 0 | 0 | 0 | 0 | 1769.65 | 0 | 0 | 0 | 282744 | 0
1802 | 191.2 | 0 | 0 | 0 | 0 | 1769.35 | 0 | 0 | 0 | 227528 | 0
1803 | 243.2 | 0 | 0 | 0 | 0 | 1752.4 | 0 | 0 | 0 | 289408 | 0
1804 | 204 | 0 | 0 | 0 | 0 | 1671.85 | 0 | 0 | 0 | 242760 | 0
1805 | 236 | 0 | 0 | 0 | 0 | 1708.1 | 0 | 0 | 0 | 280840 | 0
1806 | 293.6 | 0 | 0 | 0 | 0 | 1748.1 | 0 | 0 | 0 | 349384 | 0
1807 | 169.6 | 176.1813 | 176.1813 | 171.5055 | 169.6 | 1784.9 | 319329.1436 | 61056 | 27695.68 | 0 | 36480.96
1808 | 205.306 | 758.128 | 213.2728 | 738.0077 | 205.306 | 1791.75 | 388151.2891 | 73910.16 | 33526.4698 | 0 | 42754.9745
1809 | 1200.592 | 2178.1481 | 1247.1807 | 2120.3413 | 1200.592 | 1835.45 | 2330188.514 | 432213.12 | 196056.6736 | 0 | 197557.4136
1810 | 1832.064 | 2787.6824 | 1903.1568 | 2713.6988 | 1832.064 | 1724.2 | 3347456.5524 | 659543.04 | 299176.0512 | 0 | 505283.2512
1811 | 1718.381 | 3940.1376 | 1785.0623 | 3835.5685 | 1718.381 | 1621.85 | 2949230.8695 | 618617.16 | 280611.6173 | 0 | 649805.7752
1812 | 1345.557 | 4219.0421 | 1397.771 | 4107.071 | 1345.557 | 1664.3 | 2367722.13 | 484400.52 | 219729.4581 | 0 | 451703.4849
1813 | 1408.003 | 4165.981 | 1462.6402 | 4055.4181 | 1408.003 | 1659.85 | 2473762.6795 | 506881.08 | 229926.8899 | 0 | 478932.2205
1814 | 1247.32 | 3271.0808 | 1295.7219 | 3184.2681 | 1247.32 | 1632.1 | 2154103.1652 | 449035.2 | 203687.356 | 0 | 458889.028
1815 | 1222.285 | 2833.5747 | 1269.7155 | 2758.3732 | 1222.285 | 1651.2 | 2129992.6908 | 440022.6 | 199599.1405 | 0 | 426333.008
1816 | 1327.605 | 2369.3911 | 1379.1224 | 2306.5087 | 1327.605 | 1683.9 | 2357404.3524 | 477937.8 | 216797.8965 | 0 | 419655.9405
1817 | 1517.328 | 1382.4216 | 1382.4216 | 1345.7329 | 1345.7329 | 1817.85 | 2575377.5813 | 484463.846 | 219758.1835 | 314533.8081 | 239940.0019
1818 | 1493.831 | 265.9704 | 265.9704 | 258.9117 | 258.9117 | 1803.05 | 491684.3231 | 93208.1994 | 42280.2749 | 2263607.141 | 49914.0233
1819 | 1418.435 | 0 | 0 | 0 | 0 | 1839.75 | 0 | 0 | 0 | 4819842.13 | 0
1820 | 1030.4 | 0 | 0 | 0 | 0 | 1779.85 | 0 | 0 | 0 | 3501299.2 | 0
1821 | 1524 | 0 | 0 | 0 | 0 | 1742.25 | 0 | 0 | 0 | 5178552 | 0
1822 | 1386.4 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1823.8 | 594077.9596 | 111351.8261 | 50510.4255 | 3659949.6863 | 53894.9988
1823 | 1324 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1810.65 | 1142086.1084 | 215514.4963 | 97759.7701 | 2464734.6159 | 112095.2
1824 | 1220 | 0 | 0 | 0 | 0 | 1795.75 | 0 | 0 | 0 | 2236260 | 0
1825 | 1348.8 | 0 | 0 | 0 | 0 | 1720.9 | 0 | 0 | 0 | 1605072 | 0
1826 | 1544.8 | 0 | 0 | 0 | 0 | 1757.65 | 0 | 0 | 0 | 1838312 | 0
1827 | 1356 | 0 | 0 | 0 | 0 | 1706.9 | 0 | 0 | 0 | 1613640 | 0
1828 | 1223.2 | 0 | 0 | 0 | 0 | 1667.6 | 0 | 0 | 0 | 1455608 | 0
1829 | 995.2 | 0 | 0 | 0 | 0 | 1665.8 | 0 | 0 | 0 | 1184288 | 0
1830 | 1268 | 0 | 0 | 0 | 0 | 1636.1 | 0 | 0 | 0 | 1508920 | 0
1831 | 1071.282 | 206.6702 | 206.6702 | 201.1853 | 201.1853 | 1658.25 | 352517.4992 | 72426.7044 | 32853.5579 | 1594887.2692 | 67300.8275
1832 | 1080.559 | 1122.4898 | 1122.4898 | 1092.6996 | 1080.559 | 1666.5 | 1903499.0808 | 389001.24 | 176455.2847 | 0 | 360366.4265
1833 | 1433.37 | 1793.0248 | 1488.9916 | 1745.4389 | 1433.37 | 1651.75 | 2509869.0954 | 516013.2 | 234069.321 | 0 | 499171.1025
1834 | 1536.183 | 2979.6213 | 1595.7942 | 2900.5438 | 1536.183 | 1565.2 | 2551295.4779 | 553025.88 | 250858.6839 | 0 | 667932.3684
1835 | 1523.623 | 3761.2388 | 1582.7468 | 3661.4176 | 1523.623 | 1555.1 | 2516238.3336 | 548504.28 | 248807.6359 | 0 | 677859.8727
1836 | 1417.562 | 3965.7867 | 1472.5701 | 3860.5369 | 1417.562 | 1549.65 | 2333774.1407 | 510322.32 | 231487.8746 | 0 | 638399.0467
1837 | 1857.995 | 4016.0254 | 1930.094 | 3909.4423 | 1857.995 | 1395.95 | 2754375.316 | 668878.2 | 303410.5835 | 0 | 1122321.8798
1838 | 1821.112 | 2745.2015 | 1891.7798 | 2672.3454 | 1821.112 | 731.5 | 1414658.4157 | 655600.32 | 297387.5896 | 0 | 2310080.572
1839 | 2055.08 | 2911.7874 | 2134.8269 | 2834.5101 | 2055.08 | 1416.75 | 3082765.5213 | 739828.8 | 335594.564 | 0 | 1198625.41
1840 | 1685.353 | 2353.5005 | 1750.7527 | 2291.0398 | 1685.353 | 1350.3 | 2403769.8486 | 606727.08 | 275218.1449 | 0 | 1094973.8441
1841 | 1935.979 | 1320.0694 | 1320.0694 | 1285.0355 | 1285.0355 | 1576.35 | 2136144.1699 | 462612.7875 | 209846.3006 | 1193179.3971 | 532889.4235
1842 | 1652.92 | 247.5129 | 247.5129 | 240.944 | 240.944 | 1588.1 | 402446.1436 | 86739.8522 | 39346.1607 | 2588151.9461 | 97145.3793
1843 | 1211.742 | 0 | 0 | 0 | 0 | 1767.15 | 0 | 0 | 0 | 4117499.316 | 0
1844 | 1214.4 | 0 | 0 | 0 | 0 | 1811.25 | 0 | 0 | 0 | 4126531.2 | 0
1845 | 1048 | 0 | 0 | 0 | 0 | 1792.65 | 0 | 0 | 0 | 3561104 | 0
1846 | 1320.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1776.85 | 579486.498 | 111351.8261 | 50510.4255 | 3437040.8863 | 68255.7831
1847 | 1692 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1769 | 1116890.5829 | 215514.4963 | 97759.7701 | 3715198.6159 | 136752
1848 | 1456.8 | 0 | 0 | 0 | 0 | 1704.35 | 0 | 0 | 0 | 2670314.4 | 0
1849 | 1660.8 | 0 | 0 | 0 | 0 | 1680.2 | 0 | 0 | 0 | 1976352 | 0
1850 | 1558.4 | 0 | 0 | 0 | 0 | 1639.4 | 0 | 0 | 0 | 1854496 | 0
1851 | 1351.2 | 0 | 0 | 0 | 0 | 1570.35 | 0 | 0 | 0 | 1607928 | 0
1852 | 954.4 | 0 | 0 | 0 | 0 | 1527.15 | 0 | 0 | 0 | 1135736 | 0
1853 | 1149.6 | 0 | 0 | 0 | 0 | 1491.05 | 0 | 0 | 0 | 1368024 | 0
1854 | 950.4 | 0 | 0 | 0 | 0 | 1533.35 | 0 | 0 | 0 | 1130976 | 0
1855 | 1003.501 | 157.2948 | 157.2948 | 153.1203 | 153.1203 | 1657.2 | 267891.3668 | 55123.2931 | 25004.5382 | 1558747.899 | 51379.2068
1856 | 1142.233 | 1186.5571 | 1186.5571 | 1155.0665 | 1142.233 | 1705.3 | 2058137.6208 | 411203.88 | 186526.6489 | 0 | 336616.0651
1857 | 1496.27 | 1741.3131 | 1554.3324 | 1695.0996 | 1496.27 | 1786.2 | 2818476.4883 | 538657.2 | 244340.891 | 0 | 319902.526
1858 | 1685.004 | 2746.1074 | 1750.3912 | 2673.2272 | 1685.004 | 1725.75 | 3069760.075 | 606601.44 | 275161.1532 | 0 | 462112.347
1859 | 1751.14 | 4048.9316 | 1819.0925 | 3941.4752 | 1751.14 | 1613.05 | 2980502.079 | 630410.4 | 285961.162 | 0 | 677603.623
1860 | 1623.245 | 4344.2233 | 1686.2346 | 4228.93 | 1623.245 | 1667.7 | 2853565.2947 | 584368.2 | 265075.9085 | 0 | 539404.3135
1861 | 1835.131 | 4362.6984 | 1906.3428 | 4246.9148 | 1835.131 | 1590.4 | 3080817.8998 | 660647.16 | 299676.8923 | 0 | 751669.6576
1862 | 1759.08 | 3721.3019 | 1827.3407 | 3622.5406 | 1759.08 | 1685.4 | 3126620.4496 | 633268.8 | 287257.764 | 0 | 553406.568
1863 | 1738.997 | 3521.9886 | 1806.4783 | 3428.5169 | 1738.997 | 1706.85 | 3124110.6465 | 626038.92 | 283978.2101 | 0 | 509786.9706
1864 | 1558.583 | 2662.3465 | 1619.0634 | 2591.6892 | 1558.583 | 1747.7 | 2863479.4216 | 561089.88 | 254516.6039 | 0 | 393230.4909
1865 | 1589.517 | 1491.8483 | 1491.8483 | 1452.2554 | 1452.2554 | 1829.75 | 2790950.2813 | 522811.9567 | 237153.3126 | 251600.4482 | 242016.3337
1866 | 1636.574 | 294.5707 | 294.5707 | 286.753 | 286.753 | 1871.9 | 563537.6503 | 103231.0797 | 46826.7647 | 2474221.8947 | 35956.0047
1867 | 1446.081 | 0 | 0 | 0 | 0 | 1883.75 | 0 | 0 | 0 | 4913783.238 | 0
1868 | 1508 | 0 | 0 | 0 | 0 | 1860.45 | 0 | 0 | 0 | 5124184 | 0
1869 | 1304 | 0 | 0 | 0 | 0 | 1840.95 | 0 | 0 | 0 | 4430992 | 0
1870 | 1274.4 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1836.3 | 596991.827 | 111351.8261 | 50510.4255 | 3279373.6863 | 50071.5738
1871 | 1512.8 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1816.05 | 1145855.1107 | 215514.4963 | 97759.7701 | 3106277.0159 | 108898.4
1872 | 1444 | 0 | 0 | 0 | 0 | 1793.75 | 0 | 0 | 0 | 2646852 | 0
1873 | 1532 | 0 | 0 | 0 | 0 | 1638.25 | 0 | 0 | 0 | 1823080 | 0
1874 | 1208.8 | 0 | 0 | 0 | 0 | 1709 | 0 | 0 | 0 | 1438472 | 0
1875 | 1256.8 | 0 | 0 | 0 | 0 | 1665.2 | 0 | 0 | 0 | 1495592 | 0
1876 | 1124 | 0 | 0 | 0 | 0 | 1654.85 | 0 | 0 | 0 | 1337560 | 0
1877 | 1070.4 | 0 | 0 | 0 | 0 | 1610.2 | 0 | 0 | 0 | 1273776 | 0
1878 | 1064 | 0 | 0 | 0 | 0 | 1638.55 | 0 | 0 | 0 | 1266160 | 0
1879 | 1158.633 | 250.381 | 250.381 | 243.7361 | 243.7361 | 1685.7 | 434569.381 | 87744.9797 | 39802.0978 | 1677006.1005 | 74985.694
1880 | 1337.607 | 1294.6811 | 1294.6811 | 1260.3209 | 1260.3209 | 1693.3 | 2255259.7773 | 453715.5337 | 205810.4074 | 141665.372 | 378363.8287
1881 | 1602.436 | 1664.6181 | 1664.6181 | 1620.4401 | 1602.436 | 1734.65 | 2931974.4191 | 576876.96 | 261677.7988 | 0 | 425206.3926
1882 | 1659.929 | 2502.8266 | 1724.3421 | 2436.4029 | 1659.929 | 1687.75 | 2959334.9247 | 597574.44 | 271066.4057 | 0 | 518312.8302
1883 | 0 | 3498.1958 | 0 | 3405.3556 | 0 | 1625.85 | 0 | 0 | 0 | 0 | 0
1884 | 1537.528 | 4458.6061 | 1597.1914 | 4340.2771 | 1537.528 | 1573.95 | 2558338.5988 | 553510.08 | 251078.3224 | 0 | 655063.8044
1885 | 1283.8 | 4404.5342 | 1333.6175 | 4287.6403 | 1283.8 | 1517.5 | 2059853.1361 | 462168 | 209644.54 | 0 | 619433.5
1886 | 1608.326 | 3969.5482 | 1670.7367 | 3864.1986 | 1608.326 | 1539.3 | 2620002.3475 | 578997.36 | 262639.6358 | 0 | 740955.7882
1887 | 1597.92 | 3135.9936 | 1659.9269 | 3052.7661 | 1597.92 | 1560.75 | 2627620.5648 | 575251.2 | 260940.336 | 0 | 701886.36
1888 | 1735.168 | 2725.9639 | 1802.5008 | 2653.6183 | 1735.168 | 1612.45 | 2940443.2822 | 624660.48 | 283352.9344 | 0 | 672464.3584
1889 | 1535.971 | 1535.529 | 1535.529 | 1494.7769 | 1494.7769 | 1759.2 | 2764512.7754 | 538119.6747 | 244097.0635 | 75508.8328 | 352328.2056
1890 | 1401.399 | 295.5171 | 295.5171 | 287.6742 | 287.6742 | 1777.35 | 537887.0952 | 103562.7244 | 46977.2025 | 2041457.4951 | 62695.7909
1891 | 1316.835 | 0 | 0 | 0 | 0 | 1777.35 | 0 | 0 | 0 | 4474605.33 | 0
1892 | 1148 | 0 | 0 | 0 | 0 | 1758.05 | 0 | 0 | 0 | 3900904 | 0
1893 | 1382.4 | 0 | 0 | 0 | 0 | 1718.9 | 0 | 0 | 0 | 4697395.2 | 0
1894 | 1640.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1821.85 | 593983.0194 | 111351.8261 | 50510.4255 | 4524400.8863 | 54491.4531
1895 | 1377.6 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1797.15 | 1137183.6369 | 215514.4963 | 97759.7701 | 2646867.4159 | 120087.2
1896 | 1239.2 | 0 | 0 | 0 | 0 | 1713.85 | 0 | 0 | 0 | 2271453.6 | 0
1897 | 950.4 | 0 | 0 | 0 | 0 | 1472.8 | 0 | 0 | 0 | 1130976 | 0
1898 | 1244.8 | 0 | 0 | 0 | 0 | 1459.8 | 0 | 0 | 0 | 1481312 | 0
1899 | 963.2 | 0 | 0 | 0 | 0 | 1366.4 | 0 | 0 | 0 | 1146208 | 0
1900 | 860.8 | 0 | 0 | 0 | 0 | 1149.85 | 0 | 0 | 0 | 1024352 | 0
1901 | 976.8 | 0 | 0 | 0 | 0 | 1150.2 | 0 | 0 | 0 | 1162392 | 0
1902 | 1053.6 | 0 | 0 | 0 | 0 | 1162.55 | 0 | 0 | 0 | 1253784 | 0
1903 | 880.938 | 269.3413 | 269.3413 | 262.1931 | 262.1931 | 1473.1 | 408112.4296 | 94389.5246 | 42816.1372 | 1134159.3577 | 135227.3043
1904 | 756.271 | 842.078 | 785.6179 | 819.7297 | 756.271 | 1330.8 | 1061679.152 | 272257.56 | 123499.0543 | 0 | 506096.5532
1905 | 1395.164 | 2225.0263 | 1449.304 | 2165.9753 | 1395.164 | 1536.95 | 2262494.3537 | 502259.04 | 227830.2812 | 0 | 646030.6902
1906 | 1631.193 | 3514.7377 | 1694.491 | 3421.4585 | 1631.193 | 1614.55 | 2777730.4247 | 587229.48 | 266373.8169 | 0 | 628743.3418
1907 | 1633.019 | 4088.1704 | 1696.3879 | 3979.6726 | 1633.019 | 1540.15 | 2657008.4993 | 587886.84 | 266672.0027 | 0 | 750943.7871
1908 | 1231.998 | 4367.5715 | 1279.8054 | 4251.6585 | 1231.998 | 1531.1 | 1993988.0007 | 443519.28 | 201185.2734 | 0 | 577683.8622
1909 | 1467.239 | 4374.4619 | 1524.1748 | 4258.366 | 1467.239 | 1517.5 | 2356475.3723 | 528206.04 | 239600.1287 | 0 | 707942.8175
1910 | 1286.247 | 3791.0037 | 1336.1595 | 3690.3925 | 1286.247 | 1539.3 | 2092836.3657 | 463048.92 | 210044.1351 | 0 | 592573.9929
1911 | 1439.505 | 3535.6852 | 1495.3646 | 3441.85 | 1439.505 | 1560.75 | 2372674.9754 | 518221.8 | 235071.1665 | 0 | 632302.5713
1912 | 1449.081 | 2686.1922 | 1505.3122 | 2614.9021 | 1449.081 | 1569.6 | 2400791.8988 | 521669.16 | 236634.9273 | 0 | 623684.4624
1913 | 1125.488 | 1508.2063 | 1169.1623 | 1468.1794 | 1125.488 | 1652.9 | 1963626.9922 | 405175.68 | 183792.1904 | 0 | 390656.8848
1914 | 1313.406 | 290.3355 | 290.3355 | 282.6302 | 282.6302 | 1675.5 | 499478.2648 | 101746.8692 | 46153.5104 | 1889412.0557 | 89773.574
1915 | 1105.904 | 0 | 0 | 0 | 0 | 1688.9 | 0 | 0 | 0 | 3757861.792 | 0
1916 | 1031.2 | 0 | 0 | 0 | 0 | 1728.05 | 0 | 0 | 0 | 3504017.6 | 0
1917 | 1051.2 | 0 | 0 | 0 | 0 | 1655.45 | 0 | 0 | 0 | 3571977.6 | 0
1918 | 1335.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1775.35 | 579253.8225 | 111351.8261 | 50510.4255 | 3485972.0863 | 68714.5941
1919 | 1077.6 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1707.05 | 1080105.8962 | 215514.4963 | 97759.7701 | 1627467.4159 | 173426.4
1920 | 1121.6 | 0 | 0 | 0 | 0 | 1603.9 | 0 | 0 | 0 | 2055892.8 | 0
1921 | 1212 | 0 | 0 | 0 | 0 | 1604.35 | 0 | 0 | 0 | 1442280 | 0
1922 | 1262.4 | 0 | 0 | 0 | 0 | 1498.85 | 0 | 0 | 0 | 1502256 | 0
1923 | 1207.2 | 0 | 0 | 0 | 0 | 1456.1 | 0 | 0 | 0 | 1436568 | 0
1924 | 970.4 | 0 | 0 | 0 | 0 | 1324.55 | 0 | 0 | 0 | 1154776 | 0
1925 | 967.2 | 0 | 0 | 0 | 0 | 1195.2 | 0 | 0 | 0 | 1150968 | 0
1926 | 1076.8 | 0 | 0 | 0 | 0 | 1330.75 | 0 | 0 | 0 | 1281392 | 0
1927 | 691.327 | 268.9216 | 268.9216 | 261.7846 | 261.7846 | 1501.05 | 414538.5489 | 94242.4506 | 42749.4227 | 787351.2469 | 127854.4407
1928 | 897.95 | 932.7947 | 932.7947 | 908.0389 | 897.95 | 1495.3 | 1416012.3025 | 323262 | 146635.235 | 0 | 453195.365
1929 | 500.197 | 2092.7033 | 519.607 | 2037.1641 | 500.197 | 1645.8 | 868186.3639 | 180070.92 | 81682.1701 | 0 | 177169.7774
1930 | 375.337 | 3416.3286 | 389.9019 | 3325.6611 | 375.337 | 1609.8 | 637519.0753 | 135121.32 | 61292.5321 | 0 | 146456.4974
1931 | 375.588 | 3889.7265 | 390.1626 | 3786.4952 | 375.588 | 1542.75 | 611998.6001 | 135211.68 | 61333.5204 | 0 | 171737.613
1932 | 389.912 | 4127.593 | 405.0424 | 4018.049 | 389.912 | 1536.3 | 632126.5778 | 140368.32 | 63672.6296 | 0 | 180802.1944
1933 | 750.082 | 3295.0326 | 779.1887 | 3207.5842 | 750.082 | 1520.1 | 1203638.119 | 270029.52 | 122488.3906 | 0 | 359964.3518
1934 | 1316.533 | 3839.948 | 1367.6207 | 3738.0379 | 1316.533 | 1539.3 | 2140737.4523 | 473951.88 | 214989.8389 | 0 | 606526.7531
1935 | 1499.779 | 3289.3368 | 1557.9775 | 3202.0396 | 1499.779 | 1560.75 | 2469547.3735 | 539920.44 | 244913.9107 | 0 | 658777.9257
1936 | 1507.149 | 2465.2031 | 1565.6335 | 2399.778 | 1507.149 | 1606.05 | 2550967.778 | 542573.64 | 246117.4317 | 0 | 593741.3486
1937 | 1397.369 | 1362.9108 | 1362.9108 | 1326.7399 | 1326.7399 | 1721.2 | 2402493.2613 | 477626.3574 | 216656.6227 | 129463.174 | 362070.59
1938 | 997.74 | 258.8972 | 258.8972 | 252.0262 | 252.0262 | 1754.85 | 465649.6089 | 90729.4187 | 41155.8724 | 1366893.4634 | 60477.2793
1939 | 884.928 | 0 | 0 | 0 | 0 | 1780.85 | 0 | 0 | 0 | 3006985.344 | 0
1940 | 686.4 | 0 | 0 | 0 | 0 | 1804.6 | 0 | 0 | 0 | 2332387.2 | 0
1941 | 1051.2 | 0 | 0 | 0 | 0 | 1747.4 | 0 | 0 | 0 | 3571977.6 | 0
1942 | 1072.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1836.25 | 599110.1937 | 111351.8261 | 50510.4255 | 2594336.8863 | 50086.8675
1943 | 1167.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1764.05 | 1116797.1458 | 215514.4963 | 97759.7701 | 1931928.2159 | 139682.4
1944 | 1155.2 | 0 | 0 | 0 | 0 | 1695.85 | 0 | 0 | 0 | 2117481.6 | 0
1945 | 943.2 | 0 | 0 | 0 | 0 | 1656.7 | 0 | 0 | 0 | 1728885.6 | 0
1946 | 1432.8 | 0 | 0 | 0 | 0 | 1615.4 | 0 | 0 | 0 | 2626322.4 | 0
1947 | 1044 | 0 | 0 | 0 | 0 | 1611.7 | 0 | 0 | 0 | 1913652 | 0
1948 | 1157.6 | 0 | 0 | 0 | 0 | 1482.2 | 0 | 0 | 0 | 2121880.8 | 0
1949 | 960.8 | 0 | 0 | 0 | 0 | 1457.2 | 0 | 0 | 0 | 1761146.4 | 0
1950 | 852.8 | 0 | 0 | 0 | 0 | 1463.05 | 0 | 0 | 0 | 1563182.4 | 0
1951 | 1154.806 | 264.5212 | 264.5212 | 257.501 | 257.501 | 1576.25 | 428889.1872 | 92700.357 | 42049.9119 | 1644760.0804 | 106807.8825
1952 | 248.715 | 761.7711 | 258.3663 | 741.5541 | 248.715 | 1543.4 | 405336.8546 | 89537.4 | 40615.1595 | 0 | 113563.269
1953 | 294.906 | 2081.4281 | 306.3498 | 2026.1882 | 294.906 | 1559.5 | 485875.168 | 106166.16 | 48158.1498 | 0 | 129906.093
1954 | 233.76 | 3302.9981 | 242.831 | 3215.3384 | 233.76 | 1541.65 | 380790.4803 | 84153.6 | 38173.008 | 0 | 107143.896
1955 | 233.438 | 3770.8083 | 242.4965 | 3670.7331 | 233.438 | 1280.75 | 315757.7298 | 84037.68 | 38120.4254 | 0 | 167900.2815
1956 | 273.494 | 4051.031 | 284.1069 | 3943.5189 | 273.494 | 1335.7 | 386217.7016 | 98457.84 | 44661.5702 | 0 | 181682.0642
1957 | 185.868 | 4039.2853 | 193.0806 | 3932.0848 | 185.868 | 1264.6 | 248484.4973 | 66912.48 | 30352.2444 | 0 | 136687.3272
1958 | 251.672 | 3748.743 | 261.4381 | 3649.2534 | 251.672 | 812.9 | 216218.6507 | 90601.92 | 41098.0376 | 0 | 298759.8312
1959 | 290.153 | 3218.8425 | 301.4123 | 3133.4161 | 290.153 | 1140.35 | 349437.5347 | 104455.08 | 47381.9849 | 0 | 249430.0265
1960 | 251.848 | 2404.1183 | 261.6209 | 2340.3143 | 251.848 | 1310.2 | 348364.8073 | 90665.28 | 41126.7784 | 0 | 173724.7504
1961 | 267.282 | 1333.7671 | 277.6538 | 1298.3697 | 267.282 | 1678 | 472418.0217 | 96221.52 | 43647.1506 | 0 | 86064.804
1962 | 269.159 | 251.4572 | 251.4572 | 244.7837 | 244.7837 | 1759.85 | 453018.4462 | 88122.1301 | 39973.1773 | 44679.9346 | 57541.3809
1963 | 186.389 | 0 | 0 | 0 | 0 | 1822.9 | 0 | 0 | 0 | 341651.037 | 0
1964 | 352 | 0 | 0 | 0 | 0 | 1856.1 | 0 | 0 | 0 | 645216 | 0
1965 | 209.6 | 96.6857 | 96.6857 | 94.1197 | 94.1197 | 1798.9 | 178270.4083 | 33883.1017 | 15369.7514 | 211675.3404 | 18717.1814
1966 | 269.6 | 280.0618 | 280.0618 | 272.6291 | 269.6 | 1836.3 | 521633.9565 | 97056 | 44025.68 | 0 | 44133.52
1967 | 288.8 | 300.0068 | 300.0068 | 292.0448 | 288.8 | 1816.05 | 554423.4142 | 103968 | 47161.04 | 0 | 53124.76
1968 | 246.4 | 255.9615 | 255.9615 | 249.1684 | 246.4 | 1779.95 | 463960.8413 | 88704 | 40237.12 | 0 | 54220.32
1969 | 255.2 | 0 | 0 | 0 | 0 | 1682.05 | 0 | 0 | 0 | 303688 | 0
1970 | 220 | 0 | 0 | 0 | 0 | 1677.3 | 0 | 0 | 0 | 261800 | 0
1971 | 287.2 | 0 | 0 | 0 | 0 | 1670.25 | 0 | 0 | 0 | 341768 | 0
1972 | 292.8 | 0 | 0 | 0 | 0 | 1664.85 | 0 | 0 | 0 | 348432 | 0
1973 | 234.4 | 0 | 0 | 0 | 0 | 1639.5 | 0 | 0 | 0 | 278936 | 0
1974 | 231.2 | 0 | 0 | 0 | 0 | 1642.9 | 0 | 0 | 0 | 275128 | 0
1975 | 217.414 | 225.8507 | 225.8507 | 219.8567 | 217.414 | 1682.5 | 385955.0671 | 78269.04 | 35503.7062 | 0 | 69028.945
1976 | 235.207 | 697.279 | 244.3341 | 678.7736 | 235.207 | 1702.7 | 422782.1584 | 84674.52 | 38409.3031 | 0 | 69927.0411
1977 | 822.233 | 2017.6975 | 854.1395 | 1964.1489 | 822.233 | 1826.05 | 1582473.778 | 296003.88 | 134270.6489 | 0 | 143027.4304
1978 | 1224.436 | 1886.5006 | 1271.9499 | 1836.4339 | 1224.436 | 1746.7 | 2259660.6064 | 440796.96 | 199950.3988 | 0 | 310149.6388
1979 | 1183.914 | 3806.8122 | 1229.8555 | 3705.7815 | 1183.914 | 1672.75 | 2093771.1514 | 426209.04 | 193333.1562 | 0 | 387435.8565
1980 | 1080.396 | 4119.1309 | 1122.3205 | 4009.8114 | 1080.396 | 1683.3 | 1921755.9114 | 388942.56 | 176428.6668 | 0 | 342161.4132
1981 | 1034.163 | 4132.8514 | 1074.2934 | 4023.1678 | 1034.163 | 1669.35 | 1823898.8251 | 372298.68 | 168878.8179 | 0 | 341945.996
1982 | 1287.314 | 3856.3185 | 1337.2679 | 3753.9739 | 1287.314 | 1692.05 | 2304811.5968 | 463433.04 | 210218.3762 | 0 | 396428.3463
1983 | 930.64 | 3316.4174 | 966.7533 | 3228.4015 | 930.64 | 1736.15 | 1704350.7699 | 335030.4 | 151973.512 | 0 | 245549.364
1984 | 1303.577 | 2477.9004 | 1354.162 | 2412.1383 | 1303.577 | 1775.85 | 2437962.8441 | 469287.72 | 212874.1241 | 0 | 292196.7845
1985 | 1377.861 | 1367.494 | 1367.494 | 1331.2015 | 1331.2015 | 1874.3 | 2621017.9644 | 479232.5228 | 217385.1972 | 85526.9508 | 163792.3794
1986 | 1489.129 | 254.3555 | 254.3555 | 247.605 | 247.605 | 1854.55 | 482177.0786 | 89137.815 | 40433.9033 | 2275713.4158 | 35252.2802
1987 | 1582.537 | 0 | 0 | 0 | 0 | 1849.15 | 0 | 0 | 0 | 5377460.726 | 0
1988 | 1236.8 | 0 | 0 | 0 | 0 | 1789.25 | 0 | 0 | 0 | 4202646.4 | 0
1989 | 1488.8 | 0 | 0 | 0 | 0 | 1780.2 | 0 | 0 | 0 | 5058942.4 | 0
1990 | 1436.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1823.8 | 592959.1007 | 111351.8261 | 50510.4255 | 3831208.8863 | 53894.9988
1991 | 1529.6 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1810.65 | 1143150.4589 | 215514.4963 | 97759.7701 | 3163363.4159 | 112095.2
1992 | 1294.4 | 0 | 0 | 0 | 0 | 1786.3 | 0 | 0 | 0 | 2372635.2 | 0
1993 | 1304 | 0 | 0 | 0 | 0 | 1713 | 0 | 0 | 0 | 1551760 | 0
1994 | 1234.4 | 0 | 0 | 0 | 0 | 1763.1 | 0 | 0 | 0 | 1468936 | 0
1995 | 1701.6 | 0 | 0 | 0 | 0 | 1712.35 | 0 | 0 | 0 | 2024904 | 0
1996 | 1300 | 0 | 0 | 0 | 0 | 1667.6 | 0 | 0 | 0 | 1547000 | 0
1997 | 1364.8 | 0 | 0 | 0 | 0 | 1665.8 | 0 | 0 | 0 | 1624112 | 0
1998 | 1507.2 | 0 | 0 | 0 | 0 | 1664.6 | 0 | 0 | 0 | 1793568 | 0
1999 | 1696 | 258.9501 | 258.9501 | 252.0777 | 252.0777 | 1741.4 | 463508.2199 | 90747.9849 | 41164.2943 | 2646709.51 | 63808.5156
2000 | 1387.644 | 1359.3155 | 1359.3155 | 1323.24 | 1323.24 | 1663 | 2326139.6008 | 476366.3985 | 216085.0913 | 118052.5398 | 436498.913
2001 | 1583.009 | 1870.4864 | 1644.4373 | 1820.8447 | 1583.009 | 1529.45 | 2568260.6744 | 569883.24 | 258505.3697 | 0 | 744884.8849
2002 | 2116.262 | 2886.2878 | 2198.383 | 2809.6873 | 2116.262 | 1503.9 | 3382057.6616 | 761854.32 | 345585.5846 | 0 | 1049877.5782
2003 | 2008.054 | 3828.0557 | 2085.976 | 3726.4612 | 2008.054 | 1562.6 | 3336577.3471 | 722899.44 | 327915.2182 | 0 | 878322.8196
2004 | 1681.412 | 4116.3095 | 1746.6588 | 4007.0649 | 1681.412 | 1549.65 | 2775776.7927 | 605308.32 | 274574.5796 | 0 | 757223.8942
2005 | 1625.792 | 2816.2828 | 1688.8804 | 2741.5402 | 1625.792 | 1468.15 | 2544543.7733 | 585285.12 | 265491.8336 | 0 | 864677.4752
2006 | 1544.619 | 3740.6112 | 1604.5576 | 3641.3375 | 1544.619 | 1475.4 | 2422039.5455 | 556062.84 | 252236.2827 | 0 | 810307.1274
2007 | 1606.752 | 3280.0229 | 1669.1016 | 3192.9729 | 1606.752 | 1550.75 | 2651601.3276 | 578430.72 | 262382.6016 | 0 | 721833.336
2008 | 1395.182 | 2446.7166 | 1449.3217 | 2381.782 | 1395.182 | 1583.95 | 2342100.902 | 502265.52 | 227833.2206 | 0 | 580465.4711
2009 | 1443.602 | 1355.7669 | 1355.7669 | 1319.7856 | 1319.7856 | 1709.05 | 2379666.2332 | 475122.8216 | 215520.991 | 226955.4328 | 375868.7036
2010 | 1556.4 | 256.2711 | 256.2711 | 249.4698 | 249.4698 | 1821.35 | 478736.1933 | 89809.1135 | 40738.4118 | 2395603.1304 | 43625.0795
2011 | 1556.11 | 0 | 0 | 0 | 0 | 1832.6 | 0 | 0 | 0 | 5287661.78 | 0
2012 | 1073.6 | 0 | 0 | 0 | 0 | 1816.75 | 0 | 0 | 0 | 3648092.8 | 0
2013 | 1459.2 | 0 | 0 | 0 | 0 | 1802.65 | 0 | 0 | 0 | 4958361.6 | 0
2014 | 1785.6 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1795.75 | 587117.5691 | 111351.8261 | 50510.4255 | 5016431.2863 | 62474.7645
2015 | 1840 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1731.9 | 1096761.5415 | 215514.4963 | 97759.7701 | 4218102.6159 | 158715.2
2016 | 1543.2 | 0 | 0 | 0 | 0 | 1667.75 | 0 | 0 | 0 | 2828685.6 | 0
2017 | 1344.8 | 0 | 0 | 0 | 0 | 1698.75 | 0 | 0 | 0 | 1600312 | 0
2018 | 1585.6 | 0 | 0 | 0 | 0 | 1615.4 | 0 | 0 | 0 | 1886864 | 0
2019 | 1395.2 | 0 | 0 | 0 | 0 | 1560.85 | 0 | 0 | 0 | 1660288 | 0
2020 | 1634.4 | 0 | 0 | 0 | 0 | 1504.95 | 0 | 0 | 0 | 1944936 | 0
2021 | 1428 | 0 | 0 | 0 | 0 | 1482.55 | 0 | 0 | 0 | 1699320 | 0
2022 | 1732.8 | 0 | 0 | 0 | 0 | 1541.05 | 0 | 0 | 0 | 2062032 | 0
2023 | 1353.618 | 259.8726 | 259.8726 | 252.9757 | 252.9757 | 1682.2 | 448989.3646 | 91071.2567 | 41310.9339 | 2017477.3121 | 78695.225
2024 | 1535.856 | 1337.5099 | 1337.5099 | 1302.0132 | 1302.0132 | 1698.3 | 2334032.4643 | 468724.735 | 212618.7478 | 428633.9391 | 384507.9007
2025 | 1275.614 | 1799.3708 | 1325.1139 | 1751.6165 | 1275.614 | 1740.65 | 2341470.4508 | 459221.04 | 208307.7662 | 0 | 330830.4909
2026 | 1988.333 | 2839.8335 | 2065.4898 | 2764.4659 | 1988.333 | 1754.25 | 3689667.9411 | 715799.88 | 324694.7789 | 0 | 488632.8347
2027 | 1904.751 | 3878.7681 | 1978.6644 | 3775.8277 | 1904.751 | 1643.3 | 3314116.3093 | 685710.36 | 311045.8383 | 0 | 679424.6817
2028 | 1672.28 | 4134.7203 | 1737.1724 | 4024.987 | 1672.28 | 1559.05 | 2755232.7301 | 602020.8 | 273083.324 | 0 | 737391.866
2029 | 1859.284 | 2753.8714 | 1931.433 | 2680.7851 | 1859.284 | 1517.5 | 2977015.0534 | 669342.24 | 303621.0772 | 0 | 897104.53
2030 | 1626.32 | 2284.9154 | 1689.4289 | 2224.275 | 1626.32 | 1619.7 | 2785145.656 | 585475.2 | 265578.056 | 0 | 618489.496
2031 | 1494.969 | 3316.299 | 1552.9809 | 3228.2862 | 1494.969 | 1763.85 | 2785655.7878 | 538188.84 | 244128.4377 | 0 | 353036.9293
2032 | 1162.25 | 2472.8207 | 1207.3508 | 2407.1934 | 1162.25 | 1772.7 | 2174235.6436 | 418410 | 189795.425 | 0 | 264179.425
2033 | 1264.538 | 1355.7908 | 1313.6081 | 1319.8089 | 1264.538 | 1839.2 | 2447892.6704 | 455233.68 | 206499.0554 | 0 | 203337.7104
2034 | 1476.872 | 261.6178 | 261.6178 | 254.6746 | 254.6746 | 1886.35 | 505571.3396 | 91682.8519 | 41588.3603 | 2240287.8552 | 28331.4676
2035 | 1536.546 | 0 | 0 | 0 | 0 | 1883.85 | 0 | 0 | 0 | 5221183.308 | 0
2036 | 1277.6 | 0 | 0 | 0 | 0 | 1865.55 | 0 | 0 | 0 | 4341284.8 | 0
2037 | 1460.8 | 0 | 0 | 0 | 0 | 1850.4 | 0 | 0 | 0 | 4963798.4 | 0
2038 | 1661.6 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1836.3 | 598631.8301 | 111351.8261 | 50510.4255 | 4595079.2863 | 50071.5738
2039 | 1407.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1816.05 | 1148506.6319 | 215514.4963 | 97759.7701 | 2747448.2159 | 108898.4
2040 | 1428 | 0 | 0 | 0 | 0 | 1798.85 | 0 | 0 | 0 | 2617524 | 0
2041 | 1554.4 | 0 | 0 | 0 | 0 | 1726.7 | 0 | 0 | 0 | 1849736 | 0
2042 | 1313.6 | 0 | 0 | 0 | 0 | 1672.4 | 0 | 0 | 0 | 1563184 | 0
2043 | 1546.4 | 0 | 0 | 0 | 0 | 1668.7 | 0 | 0 | 0 | 1840216 | 0
2044 | 1344.8 | 0 | 0 | 0 | 0 | 1659.85 | 0 | 0 | 0 | 1600312 | 0
2045 | 1362.4 | 0 | 0 | 0 | 0 | 1659.2 | 0 | 0 | 0 | 1621256 | 0
2046 | 1128.8 | 0 | 0 | 0 | 0 | 1668.55 | 0 | 0 | 0 | 1343272 | 0
2047 | 1486.419 | 269.3766 | 269.3766 | 262.2275 | 262.2275 | 1685.7 | 466854.8882 | 94401.9022 | 42821.7517 | 2243943.0085 | 80674.8383
2048 | 1323.308 | 825.1153 | 825.1153 | 803.2172 | 803.2172 | 1670.8 | 1417384.3324 | 289158.2023 | 131165.3734 | 953326.3839 | 258825.5992
2049 | 1226.957 | 1473.2724 | 1274.5688 | 1434.1725 | 1226.957 | 1732.15 | 2241654.4219 | 441704.52 | 200362.0781 | 0 | 328640.4324
2050 | 1796.019 | 2805.7212 | 1865.7131 | 2731.2589 | 1796.019 | 1655.9 | 3139243.2989 | 646566.84 | 293289.9027 | 0 | 618010.1379
2051 | 1668.541 | 3638.7783 | 1733.2883 | 3542.2071 | 1668.541 | 1540.15 | 2715279.7734 | 600674.76 | 272472.7453 | 0 | 767278.5789
2052 | 1931.97 | 3883.4521 | 2006.9396 | 3780.3874 | 1931.97 | 1531.1 | 3120715.4048 | 695509.2 | 315490.701 | 0 | 905900.733
2053 | 1668.96 | 3139.429 | 1733.7236 | 3056.1102 | 1668.96 | 1517.5 | 2673308.6175 | 600825.6 | 272541.168 | 0 | 805273.2
2054 | 1763.69 | 2453.955 | 1832.1295 | 2388.8283 | 1763.69 | 1567.25 | 2925121.5428 | 634928.4 | 288010.577 | 0 | 763236.8475
2055 | 1579.999 | 2856.604 | 1641.3105 | 2780.7913 | 1579.999 | 1563.35 | 2607412.2056 | 568799.64 | 258013.8367 | 0 | 689906.5633
2056 | 1714.12 | 2231.5178 | 1780.636 | 2172.2945 | 1714.12 | 1594.95 | 2881618.906 | 617083.2 | 279915.796 | 0 | 694304.306
2057 | 1622.297 | 1198.2831 | 1198.2831 | 1166.4813 | 1166.4813 | 1759.2 | 2161084.8166 | 419933.2723 | 190486.3983 | 835510.156 | 274946.8848
2058 | 1842.205 | 192.2578 | 192.2578 | 187.1554 | 187.1554 | 1867.45 | 368328.6774 | 67375.9475 | 30562.4784 | 3033705.8991 | 24282.7623
2059 | 1704.336 | 0 | 0 | 0 | 0 | 1864.95 | 0 | 0 | 0 | 5791333.728 | 0
2060 | 1539.2 | 0 | 0 | 0 | 0 | 1846.65 | 0 | 0 | 0 | 5230201.6 | 0
2061 | 1760 | 0 | 0 | 0 | 0 | 1840.95 | 0 | 0 | 0 | 5980480 | 0
2062 | 1748 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1836.3 | 599005.815 | 111351.8261 | 50510.4255 | 4888666.4863 | 50071.5738
2063 | 1951.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1816.05 | 1149549.8871 | 215514.4963 | 97759.7701 | 4595960.2159 | 108898.4
2064 | 1534.4 | 0 | 0 | 0 | 0 | 1789.4 | 0 | 0 | 0 | 2812555.2 | 0
2065 | 1479.2 | 0 | 0 | 0 | 0 | 1722.25 | 0 | 0 | 0 | 1760248 | 0
2066 | 1765.6 | 0 | 0 | 0 | 0 | 1668.9 | 0 | 0 | 0 | 2101064 | 0
2067 | 1462.4 | 0 | 0 | 0 | 0 | 1661.7 | 0 | 0 | 0 | 1740256 | 0
2068 | 1915.2 | 0 | 0 | 0 | 0 | 1659.85 | 0 | 0 | 0 | 2279088 | 0
2069 | 1624.8 | 0 | 0 | 0 | 0 | 1657.7 | 0 | 0 | 0 | 1933512 | 0
2070 | 1568 | 0 | 0 | 0 | 0 | 1667.05 | 0 | 0 | 0 | 1865920 | 0
2071 | 1421.665 | 221.2602 | 221.2602 | 215.3881 | 215.3881 | 1727.75 | 393673.0779 | 77539.7131 | 35172.8754 | 2211105.5727 | 57399.012
2072 | 1488.271 | 1265.2704 | 1265.2704 | 1231.6908 | 1231.6908 | 1695.8 | 2206118.6578 | 443408.6985 | 201135.1124 | 470311.4531 | 366754.7754
2073 | 1486.483 | 1676.4958 | 1544.1656 | 1632.0025 | 1486.483 | 1734.65 | 2722470.3101 | 535133.88 | 242742.6739 | 0 | 394438.264
2074 | 1803.338 | 2669.7407 | 1873.3161 | 2598.8872 | 1803.338 | 1744.75 | 3324212.8203 | 649201.68 | 294485.0954 | 0 | 460302.0245
2075 | 2033.628 | 3650.3755 | 2112.5424 | 3553.4965 | 2033.628 | 1740.75 | 3741906.6386 | 732106.08 | 332091.4524 | 0 | 527218.059
2076 | 1696.775 | 3589.3488 | 1762.6179 | 3494.0894 | 1696.775 | 1709.2 | 3059431.0498 | 610839 | 277083.3575 | 0 | 493422.17
2077 | 1592.548 | 3761.8423 | 1654.3464 | 3662.0051 | 1592.548 | 1673.1 | 2811410.7215 | 573317.28 | 260063.0884 | 0 | 520603.9412
2078 | 1457.42 | 2974.8896 | 1513.9748 | 2895.9376 | 1457.42 | 1748.4 | 2698462.7586 | 524671.2 | 237996.686 | 0 | 366686.872
2079 | 1641.988 | 3105.9618 | 1705.7049 | 3023.5313 | 1641.988 | 1769.85 | 3072985.4939 | 591115.68 | 268136.6404 | 0 | 377903.5382
2080 | 1955.911 | 2308.4236 | 2031.8096 | 2247.1593 | 1955.911 | 1706.2 | 3526718.0809 | 704127.96 | 319400.2663 | 0 | 574646.6518
2081 | 1702.841 | 1246.3694 | 1246.3694 | 1213.2914 | 1213.2914 | 1826.25 | 2338417.6192 | 436784.9042 | 198130.4857 | 897344.416 | 206350.0175
2082 | 1466.806 | 219.1556 | 219.1556 | 213.3393 | 213.3393 | 1886.35 | 424082.4694 | 76802.1584 | 34838.3124 | 2297604.4083 | 23733.0749
2083 | 1663.509 | 0 | 0 | 0 | 0 | 1883.85 | 0 | 0 | 0 | 5652603.582 | 0
2084 | 1294.4 | 0 | 0 | 0 | 0 | 1865.55 | 0 | 0 | 0 | 4398371.2 | 0
2085 | 1368 | 0 | 0 | 0 | 0 | 1850.4 | 0 | 0 | 0 | 4648464 | 0
2086 | 1146.4 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1836.3 | 598792.4395 | 111351.8261 | 50510.4255 | 2844429.6863 | 50071.5738
2087 | 1459.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1816.05 | 1148794.2563 | 215514.4963 | 97759.7701 | 2924144.2159 | 108898.4
2088 | 1268.8 | 0 | 0 | 0 | 0 | 1798.85 | 0 | 0 | 0 | 2325710.4 | 0
2089 | 923.2 | 0 | 0 | 0 | 0 | 1778.2 | 0 | 0 | 0 | 1098608 | 0
2090 | 1351.2 | 0 | 0 | 0 | 0 | 1718.9 | 0 | 0 | 0 | 1607928 | 0
2091 | 1026.4 | 0 | 0 | 0 | 0 | 1668.7 | 0 | 0 | 0 | 1221416 | 0
2092 | 1252.8 | 0 | 0 | 0 | 0 | 1666.85 | 0 | 0 | 0 | 1490832 | 0
2093 | 1265.6 | 0 | 0 | 0 | 0 | 1663.7 | 0 | 0 | 0 | 1506064 | 0
2094 | 918.4 | 0 | 0 | 0 | 0 | 1669.55 | 0 | 0 | 0 | 1092896 | 0
2095 | 1050.829 | 249.8668 | 249.8668 | 243.2355 | 243.2355 | 1779.7 | 457042.881 | 87564.7776 | 39720.3561 | 1480318.8978 | 52451.227
2096 | 806.027 | 837.3047 | 837.3047 | 815.0831 | 806.027 | 1701.8 | 1447330.4809 | 290169.72 | 131624.2091 | 0 | 240357.2514
2097 | 1095.822 | 1536.3766 | 1138.3461 | 1495.602 | 1095.822 | 1786.2 | 2065567.616 | 394495.92 | 178947.7326 | 0 | 234286.7436
2098 | 1270.332 | 3371.9384 | 1319.6269 | 3282.449 | 1270.332 | 1754.25 | 2355628.6959 | 457319.52 | 207445.2156 | 0 | 312184.089
2099 | 1318.43 | 3969.8962 | 1369.5913 | 3864.5373 | 1318.43 | 1752.75 | 2438005.3444 | 474634.8 | 215299.619 | 0 | 325981.8175
2100 | 1137.052 | 4270.4224 | 1181.175 | 4157.0878 | 1137.052 | 1743.7 | 2088301.7672 | 409338.72 | 185680.5916 | 0 | 291426.4276
2101 | 1338.908 | 4287.4962 | 1390.864 | 4173.7084 | 1338.908 | 1726.6 | 2430505.2635 | 482006.88 | 218643.6764 | 0 | 366057.4472
2102 | 1124.637 | 3967.8976 | 1168.2783 | 3862.5917 | 1124.637 | 1850.4 | 2189704.91 | 404869.32 | 183653.2221 | 0 | 168245.6952
2103 | 1168.045 | 3412.7624 | 1213.3707 | 3322.1895 | 1168.045 | 1876.35 | 2304725.2768 | 420496.2 | 190741.7485 | 0 | 144428.7643
2104 | 1479.406 | 2553.5888 | 1536.814 | 2485.8179 | 1479.406 | 1885.2 | 2929278.4152 | 532586.16 | 241586.9998 | 0 | 169835.8088
2105 | 1301.431 | 1404.7289 | 1351.9327 | 1367.4482 | 1301.431 | 1890.7 | 2585142.1346 | 468515.16 | 212523.6823 | 0 | 142246.4083
2106 | 1478.389 | 254.6391 | 254.6391 | 247.8811 | 247.8811 | 1886.35 | 492308.6019 | 89237.1992 | 40478.9851 | 2255520.9644 | 27575.8087
2107 | 1147.38 | 0 | 0 | 0 | 0 | 1883.85 | 0 | 0 | 0 | 3898797.24 | 0
2108 | 1016 | 0 | 0 | 0 | 0 | 1865.55 | 0 | 0 | 0 | 3452368 | 0
2109 | 1436 | 0 | 0 | 0 | 0 | 1850.4 | 0 | 0 | 0 | 4879528 | 0
2110 | 1550.4 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1836.3 | 600009.4157 | 111351.8261 | 50510.4255 | 4217221.6863 | 50071.5738
2111 | 1441.6 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1816.05 | 1149847.3548 | 215514.4963 | 97759.7701 | 2864339.4159 | 108898.4
2112 | 1428 | 0 | 0 | 0 | 0 | 1798.85 | 0 | 0 | 0 | 2617524 | 0
2113 | 1300 | 0 | 0 | 0 | 0 | 1731.7 | 0 | 0 | 0 | 2382900 | 0
2114 | 1284 | 0 | 0 | 0 | 0 | 1775.4 | 0 | 0 | 0 | 2353572 | 0
2115 | 1629.6 | 0 | 0 | 0 | 0 | 1761.75 | 0 | 0 | 0 | 2987056.8 | 0
2116 | 1440 | 0 | 0 | 0 | 0 | 1666.85 | 0 | 0 | 0 | 2639520 | 0
2117 | 1583.2 | 0 | 0 | 0 | 0 | 1709.25 | 0 | 0 | 0 | 2902005.6 | 0
2118 | 1600 | 0 | 0 | 0 | 0 | 1766.6 | 0 | 0 | 0 | 2932800 | 0
2119 | 1140.384 | 305.3338 | 305.3338 | 297.2304 | 297.2304 | 1788.2 | 561017.136 | 107002.9474 | 48537.7259 | 1545500.5315 | 61621.7274
2120 | 204.826 | 813.3114 | 212.7742 | 791.7266 | 204.826 | 1789.4 | 386818.3237 | 73737.36 | 33448.0858 | 0 | 43136.3556
2121 | 307.065 | 2107.0471 | 318.9806 | 2051.1273 | 307.065 | 1842.15 | 596960.9293 | 110543.4 | 50143.7145 | 0 | 48470.2102
2122 | 313.222 | 3320.368 | 325.3765 | 3232.2472 | 313.222 | 1843.3 | 611463.249 | 112759.92 | 51149.1526 | 0 | 49081.8874
2123 | 355.547 | 3827.4699 | 369.3439 | 3725.8909 | 355.547 | 1752.75 | 660211.6854 | 127996.92 | 58060.8251 | 0 | 87908.9958
2124 | 311.517 | 4099.5785 | 323.6053 | 3990.778 | 311.517 | 1740.2 | 572443.0581 | 112146.12 | 50870.7261 | 0 | 80932.1166
2125 | 299.716 | 2807.2992 | 311.3464 | 2732.795 | 299.716 | 1726.6 | 546331.3235 | 107897.76 | 48943.6228 | 0 | 81942.3544
2126 | 315.351 | 3824.8562 | 327.5881 | 3723.3466 | 315.351 | 1751.9 | 583959.2859 | 113526.36 | 51496.8183 | 0 | 78238.5831
2127 | 283.379 | 3271.6719 | 294.3755 | 3184.8435 | 283.379 | 1857.45 | 555656.0695 | 102016.44 | 46275.7907 | 0 | 40395.6764
2128 | 230.684 | 2435.4736 | 239.6356 | 2370.8374 | 230.684 | 1778.7 | 432853.6365 | 83046.24 | 37670.6972 | 0 | 51050.3692
2129 | 250.683 | 1326.4394 | 260.4107 | 1291.2364 | 250.683 | 1881.25 | 496797.4715 | 90245.88 | 40936.5339 | 0 | 29768.6063
2130 | 298.518 | 242.8403 | 242.8403 | 236.3955 | 236.3955 | 1886.35 | 469442.6442 | 85102.3788 | 38603.3846 | 113870.5484 | 26298.0417
2131 | 256.165 | 0 | 0 | 0 | 0 | 1883.85 | 0 | 0 | 0 | 469550.445 | 0
2132 | 318.4 | 0 | 0 | 0 | 0 | 1865.55 | 0 | 0 | 0 | 583627.2 | 0
2133 | 298.4 | 193.9178 | 193.9178 | 188.7714 | 188.7714 | 1850.4 | 368543.2326 | 67957.691 | 30826.3637 | 200949.29 | 27926.4304
2134 | 237.6 | 246.82 | 246.82 | 240.2695 | 237.6 | 1836.3 | 460170.9306 | 85536 | 38800.08 | 0 | 38895.12
2135 | 305.6 | 317.4587 | 317.4587 | 309.0335 | 305.6 | 1816.05 | 586413.417 | 110016 | 49904.48 | 0 | 56215.12
2136 | 168 | 174.5192 | 174.5192 | 169.8876 | 168 | 1789.4 | 317711.6946 | 60480 | 27434.4 | 0 | 35380.8
2137 | 228.8 | 0 | 0 | 0 | 0 | 1720.6 | 0 | 0 | 0 | 272272 | 0
2138 | 226.4 | 0 | 0 | 0 | 0 | 1677.3 | 0 | 0 | 0 | 269416 | 0
2139 | 221.6 | 0 | 0 | 0 | 0 | 1673.75 | 0 | 0 | 0 | 263704 | 0
2140 | 135.2 | 0 | 0 | 0 | 0 | 1671.85 | 0 | 0 | 0 | 160888 | 0
2141 | 148.8 | 0 | 0 | 0 | 0 | 1664.5 | 0 | 0 | 0 | 177072 | 0
2142 | 203.2 | 0 | 0 | 0 | 0 | 1671.4 | 0 | 0 | 0 | 241808 | 0
2143 | 139.948 | 145.3786 | 145.3786 | 141.5204 | 139.948 | 1724.55 | 255044.8943 | 50381.28 | 22853.5084 | 0 | 38548.6766
2144 | 168.345 | 781.3702 | 174.8776 | 760.6331 | 168.345 | 1695.7 | 301460.2252 | 60604.2 | 27490.7385 | 0 | 51227.3835
2145 | 999.188 | 2201.0912 | 1037.9612 | 2142.6754 | 999.188 | 1734.95 | 1833204.7002 | 359707.68 | 163167.4004 | 0 | 264834.7794
2146 | 1188.218 | 2926.2704 | 1234.3265 | 2848.6088 | 1188.218 | 1695.7 | 2130743.6559 | 427758.48 | 194035.9994 | 0 | 361574.7374
2147 | 1369.757 | 2214.6746 | 1422.9101 | 2155.8983 | 1369.757 | 1586.85 | 2290999.4897 | 493112.52 | 223681.3181 | 0 | 565915.1045
2148 | 1382.264 | 2495.0158 | 1435.9024 | 2428.7994 | 1382.264 | 1555.65 | 2259417.7211 | 497615.04 | 225723.7112 | 0 | 614209.0084
2149 | 1401.945 | 3210.8998 | 1456.3471 | 3125.6842 | 1401.945 | 1518.95 | 2239444.4118 | 504700.2 | 228937.6185 | 0 | 674405.6423
2150 | 1395.96 | 2668.4972 | 1450.1299 | 2597.6768 | 1395.96 | 1598.25 | 2348517.3729 | 502545.6 | 227960.268 | 0 | 560826.93
2151 | 1436.28 | 2357.504 | 1492.0145 | 2294.9371 | 1436.28 | 1658.7 | 2512102.5902 | 517060.8 | 234544.524 | 0 | 490202.364
2152 | 1584.287 | 1913.0784 | 1645.7649 | 1862.3063 | 1584.287 | 1591.2 | 2656117.2161 | 570343.32 | 258714.0671 | 0 | 647656.5256
2153 | 1458.461 | 1266.9387 | 1266.9387 | 1233.3149 | 1233.3149 | 1771.3 | 2297572.8239 | 443993.3544 | 201400.3188 | 412692.8502 | 276092.5862
2154 | 1392.377 | 233.0288 | 233.0288 | 226.8444 | 226.8444 | 1803.05 | 429686.1132 | 81663.9761 | 37043.6869 | 2136421.296 | 43731.9597
2155 | 1600.335 | 0 | 0 | 0 | 0 | 1755.65 | 0 | 0 | 0 | 5437938.33 | 0
2156 | 1251.2 | 0 | 0 | 0 | 0 | 1734.3 | 0 | 0 | 0 | 4251577.6 | 0
2157 | 921.6 | 0 | 0 | 0 | 0 | 1722.7 | 0 | 0 | 0 | 3131596.8 | 0
2158 | 1216 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1823.8 | 594294.8683 | 111351.8261 | 50510.4255 | 3080930.4863 | 53894.9988
2159 | 1305.6 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1810.65 | 1144695.6712 | 215514.4963 | 97759.7701 | 2402211.4159 | 112095.2
2160 | 875.2 | 0 | 0 | 0 | 0 | 1734.8 | 0 | 0 | 0 | 1604241.6 | 0
2161 | 1137.6 | 0 | 0 | 0 | 0 | 1721 | 0 | 0 | 0 | 1353744 | 0
2162 | 760 | 0 | 0 | 0 | 0 | 1758.65 | 0 | 0 | 0 | 904400 | 0
2163 | 1196.8 | 0 | 0 | 0 | 0 | 1670.3 | 0 | 0 | 0 | 1424192 | 0
2164 | 1156 | 0 | 0 | 0 | 0 | 1667.6 | 0 | 0 | 0 | 1375640 | 0
2165 | 1220 | 0 | 0 | 0 | 0 | 1665.8 | 0 | 0 | 0 | 1451800 | 0
2166 | 1054.4 | 0 | 0 | 0 | 0 | 1706.65 | 0 | 0 | 0 | 1254736 | 0
2167 | 1293.304 | 283.5168 | 283.5168 | 275.9924 | 275.9924 | 1746.85 | 509134.8741 | 99357.2794 | 45069.5659 | 1864732.0844 | 68389.7383
2168 | 1393.785 | 1085.9343 | 1085.9343 | 1057.1142 | 1057.1142 | 1666.5 | 1859105.5717 | 380561.1038 | 172626.7451 | 617117.6183 | 345090.1255
2169 | 1579.901 | 1817.7868 | 1641.2087 | 1769.5437 | 1579.901 | 1670.75 | 2779754.0502 | 568764.36 | 257997.8333 | 0 | 520182.4042
2170 | 1649.699 | 2759.4383 | 1713.7152 | 2686.2044 | 1649.699 | 1537.75 | 2680605.8108 | 593891.64 | 269395.8467 | 0 | 762573.3627
2171 | 1676.943 | 3726.3048 | 1742.0164 | 3627.4107 | 1676.943 | 1596.45 | 2840542.5754 | 603699.48 | 273844.7919 | 0 | 676730.3476
2172 | 1684.745 | 3992.0747 | 1750.1211 | 3886.1272 | 1684.745 | 1622.85 | 2904537.4583 | 606508.2 | 275118.8585 | 0 | 635401.5768
2173 | 1931.871 | 4008.2136 | 2006.8368 | 3901.8378 | 1931.871 | 1493.5 | 3065450.6717 | 695473.56 | 315474.5343 | 0 | 978492.6615
2174 | 1728.951 | 1820.8263 | 1796.0425 | 1772.5026 | 1728.951 | 1475.4 | 2703966.9774 | 622422.36 | 282337.6983 | 0 | 907007.6946
2175 | 1653.202 | 3081.7618 | 1717.3541 | 2999.9735 | 1653.202 | 1488.95 | 2597723.826 | 595152.72 | 269967.8866 | 0 | 844868.8821
2176 | 1470.106 | 1914.0487 | 1527.1531 | 1863.2508 | 1470.106 | 1522.65 | 2353032.583 | 529238.16 | 240068.3098 | 0 | 701755.0991
2177 | 1634.306 | 1213.6356 | 1213.6356 | 1181.4264 | 1181.4264 | 1684.05 | 2092373.5585 | 425313.4898 | 192926.9247 | 830128.379 | 365375.6383
2178 | 1538.105 | 206.9133 | 206.9133 | 201.4219 | 201.4219 | 1779.3 | 376753.8648 | 72511.8909 | 32892.1994 | 2450140.0871 | 43513.4327
2179 | 1470.4 | 0 | 0 | 0 | 0 | 1832.6 | 0 | 0 | 0 | 4996419.2 | 0
2180 | 1250.4 | 0 | 0 | 0 | 0 | 1816.75 | 0 | 0 | 0 | 4248859.2 | 0
2181 | 1324.8 | 0 | 0 | 0 | 0 | 1802.65 | 0 | 0 | 0 | 4501670.4 | 0
2182 | 1529.6 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1790.75 | 584279.3205 | 111351.8261 | 50510.4255 | 4146543.2863 | 64004.1345
2183 | 1635.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1722.5 | 1088562.3142 | 215514.4963 | 97759.7701 | 3522192.2159 | 164280
2184 | 1508 | 0 | 0 | 0 | 0 | 1751.85 | 0 | 0 | 0 | 2764164 | 0
2185 | 972 | 0 | 0 | 0 | 0 | 1740.9 | 0 | 0 | 0 | 1156680 | 0
2186 | 1086.4 | 0 | 0 | 0 | 0 | 1686.4 | 0 | 0 | 0 | 1292816 | 0
2187 | 1562.4 | 0 | 0 | 0 | 0 | 1682.05 | 0 | 0 | 0 | 1859256 | 0
2188 | 1220 | 0 | 0 | 0 | 0 | 1674.3 | 0 | 0 | 0 | 1451800 | 0
2189 | 1601.6 | 0 | 0 | 0 | 0 | 1667.9 | 0 | 0 | 0 | 1905904 | 0
2190 | 1461.6 | 0 | 0 | 0 | 0 | 1662.8 | 0 | 0 | 0 | 1739304 | 0
2191 | 1554.491 | 203.7377 | 203.7377 | 198.3306 | 198.3306 | 1714.05 | 356579.4463 | 71399.0061 | 32387.3825 | 2485842.0636 | 55512.9033
2192 | 1258.89 | 859.7532 | 859.7532 | 836.9359 | 836.9359 | 1716.4 | 1505504.6718 | 301296.9107 | 136671.6264 | 773441.933 | 232334.1952
2193 | 1130.656 | 1213.9026 | 1174.5308 | 1181.6862 | 1130.656 | 1775.45 | 2102468.2172 | 407036.16 | 184636.1248 | 0 | 253888.8048
2194 | 1493.053 | 2130.065 | 1550.9905 | 2073.5342 | 1493.053 | 1807.65 | 2834347.1751 | 537499.08 | 243815.5549 | 0 | 287188.7445
2195 | 1407.71 | 2974.1686 | 1462.3358 | 2895.2358 | 1407.71 | 1775 | 2627259.4037 | 506775.6 | 229879.043 | 0 | 316734.75
2196 | 1593.023 | 3228.736 | 1654.8399 | 3143.0472 | 1593.023 | 1758.65 | 2944848.4312 | 573488.28 | 260140.6559 | 0 | 384476.1011
2197 | 1931.914 | 3098.0908 | 2006.8814 | 3015.8691 | 1931.914 | 1741 | 3542169.3727 | 695489.04 | 315481.5562 | 0 | 500365.726
2198 | 1327.845 | 2622.2444 | 1379.3717 | 2552.6515 | 1327.845 | 1774 | 2482575.2257 | 478024.2 | 216837.0885 | 0 | 300092.97
2199 | 1348.658 | 3307.7413 | 1400.9923 | 3219.9557 | 1348.658 | 1793.05 | 2549877.0298 | 485516.88 | 220235.8514 | 0 | 279104.7731
2200 | 1472.454 | 2115.5269 | 1529.5922 | 2059.382 | 1472.454 | 1799.45 | 2789934.6942 | 530083.44 | 240451.7382 | 0 | 295300.6497
2201 | 1419.53 | 1353.6436 | 1353.6436 | 1317.7187 | 1317.7187 | 1898.8 | 2630530.2419 | 474378.7141 | 215183.4556 | 186620.204 | 130532.2128
2202 | 938.571 | 141.0842 | 141.0842 | 137.3399 | 137.3399 | 1893.5 | 273606.7544 | 49442.3747 | 22427.6105 | 1468656.5521 | 14317.3275
2203 | 1347.852 | 0 | 0 | 0 | 0 | 1894.45 | 0 | 0 | 0 | 4580001.096 | 0
2204 | 1007.2 | 0 | 0 | 0 | 0 | 1886 | 0 | 0 | 0 | 3422465.6 | 0
2205 | 1144 | 0 | 0 | 0 | 0 | 1871.55 | 0 | 0 | 0 | 3887312 | 0
2206 | 1352 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1857.7 | 607274.3124 | 111351.8261 | 50510.4255 | 3543058.4863 | 43525.8702
2207 | 1520.8 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1835.65 | 1159707.3772 | 215514.4963 | 97759.7701 | 3133461.0159 | 97295.2
2208 | 1532.8 | 0 | 0 | 0 | 0 | 1816.15 | 0 | 0 | 0 | 2809622.4 | 0
2209 | 1087.2 | 0 | 0 | 0 | 0 | 1797.8 | 0 | 0 | 0 | 1293768 | 0
2210 | 1328.8 | 0 | 0 | 0 | 0 | 1788.4 | 0 | 0 | 0 | 1581272 | 0
2211 | 1067.2 | 0 | 0 | 0 | 0 | 1784.05 | 0 | 0 | 0 | 1269968 | 0
2212 | 1069.6 | 0 | 0 | 0 | 0 | 1776.2 | 0 | 0 | 0 | 1272824 | 0
2213 | 964.8 | 0 | 0 | 0 | 0 | 1782.9 | 0 | 0 | 0 | 1148112 | 0
2214 | 1233.6 | 0 | 0 | 0 | 0 | 1788.2 | 0 | 0 | 0 | 1467984 | 0
2215 | 1241.187 | 331.0484 | 331.0484 | 322.2625 | 322.2625 | 1793.55 | 607474.0303 | 116014.5113 | 52625.4714 | 1684388.5509 | 65123.6203
2216 | 1139.749 | 1183.9767 | 1183.9767 | 1152.5546 | 1139.749 | 1806.6 | 2166565.0334 | 410309.64 | 186121.0117 | 0 | 220427.4566
2217 | 1485.342 | 1956.5472 | 1542.9803 | 1904.6215 | 1485.342 | 1854.05 | 2895083.8525 | 534723.12 | 242556.3486 | 0 | 216785.6649
2218 | 1788.565 | 3256.7059 | 1857.9698 | 3170.2747 | 1788.565 | 1874.65 | 3527765.8664 | 643883.4 | 292072.6645 | 0 | 224196.6227
2219 | 1486.331 | 3938.5108 | 1544.0077 | 3833.9849 | 1486.331 | 1839 | 2873419.4414 | 535079.16 | 242717.8523 | 0 | 239299.291
2220 | 1635.414 | 4215.0147 | 1698.8758 | 4103.1505 | 1635.414 | 1764.45 | 3038050.0637 | 588749.04 | 267063.1062 | 0 | 385221.7677
2221 | 1839.255 | 3012.941 | 1910.6268 | 2932.9792 | 1839.255 | 1754 | 3398405.0345 | 662131.8 | 300350.3415 | 0 | 452456.73
2222 | 1431.431 | 3898.0888 | 1486.9773 | 3794.6357 | 1431.431 | 1776.9 | 2689403.2612 | 515315.16 | 233752.6823 | 0 | 319352.2561
2223 | 1727.174 | 3332.3319 | 1794.1966 | 3243.8936 | 1727.174 | 1795.95 | 3275202.2896 | 621782.64 | 282047.5142 | 0 | 352429.8547
2224 | 1726.438 | 2497.9317 | 1793.432 | 2431.638 | 1726.438 | 1819.85 | 3306248.4728 | 621517.68 | 281927.3254 | 0 | 311017.8057
2225 | 1599.501 | 1359.6105 | 1359.6105 | 1323.5272 | 1323.5272 | 1904.7 | 2650979.0558 | 476469.7872 | 216131.9896 | 505859.9999 | 123464.009
2226 | 1633.042 | 240.9601 | 240.9601 | 234.5652 | 234.5652 | 1893.5 | 466443.2637 | 84443.4578 | 38304.4907 | 2563408.0465 | 24452.7195
2227 | 1619.476 | 0 | 0 | 0 | 0 | 1894.45 | 0 | 0 | 0 | 5502979.448 | 0
2228 | 1533.6 | 0 | 0 | 0 | 0 | 1886 | 0 | 0 | 0 | 5211172.8 | 0
2229 | 1748.8 | 0 | 0 | 0 | 0 | 1871.55 | 0 | 0 | 0 | 5942422.4 | 0
2230 | 1145.6 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1857.7 | 606762.124 | 111351.8261 | 50510.4255 | 2841711.2863 | 43525.8702
2231 | 1203.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1835.65 | 1159024.1385 | 215514.4963 | 97759.7701 | 2054256.2159 | 97295.2
2232 | 382.4 | 0 | 0 | 0 | 0 | 1816.15 | 0 | 0 | 0 | 700939.2 | 0
2233 | 120 | 0 | 0 | 0 | 0 | 1797.8 | 0 | 0 | 0 | 142800 | 0
2234 | 126.4 | 0 | 0 | 0 | 0 | 1788.4 | 0 | 0 | 0 | 150416 | 0
2235 | 118.4 | 0 | 0 | 0 | 0 | 1784.05 | 0 | 0 | 0 | 140896 | 0
2236 | 124.8 | 0 | 0 | 0 | 0 | 1782.1 | 0 | 0 | 0 | 148512 | 0
2237 | 127.2 | 0 | 0 | 0 | 0 | 1782.9 | 0 | 0 | 0 | 151368 | 0
2238 | 104.8 | 0 | 0 | 0 | 0 | 1788.2 | 0 | 0 | 0 | 124712 | 0
2239 | 90.455 | 93.9651 | 93.9651 | 91.4713 | 90.455 | 1792.65 | 170404.5339 | 32563.8 | 14771.3015 | 0 | 18755.8442
2240 | 181.636 | 244.2552 | 188.6843 | 237.7728 | 181.636 | 1713.5 | 327034.5913 | 65388.96 | 29661.1588 | 0 | 52038.714
2241 | 1303.888 | 1354.485 | 1354.485 | 1318.5378 | 1303.888 | 1804.45 | 2473656.811 | 469399.68 | 212924.9104 | 0 | 254975.2984
2242 | 1593.999 | 1655.8537 | 1655.8537 | 1611.9083 | 1593.999 | 1812.3 | 3043841.4617 | 573839.64 | 260300.0367 | 0 | 299193.6123
2243 | 1722.687 | 2341.0182 | 1789.5354 | 2278.8888 | 1722.687 | 1730.5 | 3145365.5932 | 620167.32 | 281314.7871 | 0 | 464264.1465
2244 | 1824.597 | 2545.8237 | 1895.4 | 2478.259 | 1824.597 | 1681.3 | 3235793.8233 | 656854.92 | 297956.6901 | 0 | 581499.0639
2245 | 1538.349 | 3152.7236 | 1598.0442 | 3069.052 | 1538.349 | 1538.5 | 2500063.3469 | 553805.64 | 251212.3917 | 0 | 709948.0635
2246 | 1462.819 | 2975.0319 | 1519.5833 | 2896.0762 | 1462.819 | 1732.4 | 2677689.3577 | 526614.84 | 238878.3427 | 0 | 391450.3644
2247 | 1763.062 | 2252.5536 | 1831.4772 | 2192.772 | 1763.062 | 1751.45 | 3250790.6336 | 634702.32 | 287908.0246 | 0 | 438209.0601
2248 | 1727.078 | 1967.0734 | 1794.0968 | 1914.8683 | 1727.078 | 1792.25 | 3257697.0803 | 621748.08 | 282031.8374 | 0 | 358800.4545
2249 | 1726.744 | 282.9496 | 282.9496 | 275.4403 | 275.4403 | 1898.8 | 549010.6642 | 99158.511 | 44979.4023 | 2660239.667 | 27284.9368
2250 | 1440.062 | 54.6567 | 54.6567 | 53.2062 | 53.2062 | 1893.5 | 105656.058 | 19154.2149 | 8688.5647 | 2542106.7685 | 5546.6265
2251 | 1485.876 | 0 | 0 | 0 | 0 | 1894.45 | 0 | 0 | 0 | 5049006.648 | 0
2252 | 1420 | 0 | 0 | 0 | 0 | 1886 | 0 | 0 | 0 | 4825160 | 0
2253 | 1555.2 | 0 | 0 | 0 | 0 | 1871.55 | 0 | 0 | 0 | 5284569.6 | 0
2254 | 1828.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1857.7 | 606812.7682 | 111351.8261 | 50510.4255 | 5163224.8863 | 43525.8702
2255 | 1337.6 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1835.65 | 1159168.3508 | 215514.4963 | 97759.7701 | 2510947.4159 | 97295.2
2256 | 1448.8 | 0 | 0 | 0 | 0 | 1816.15 | 0 | 0 | 0 | 2655650.4 | 0
2257 | 1088.8 | 0 | 0 | 0 | 0 | 1797.8 | 0 | 0 | 0 | 1295672 | 0
2258 | 1398.4 | 0 | 0 | 0 | 0 | 1778.4 | 0 | 0 | 0 | 1664096 | 0
2259 | 1239.2 | 0 | 0 | 0 | 0 | 1773.15 | 0 | 0 | 0 | 1474648 | 0
2260 | 1181.6 | 0 | 0 | 0 | 0 | 1680.1 | 0 | 0 | 0 | 1406104 | 0
2261 | 1463.2 | 0 | 0 | 0 | 0 | 1680.9 | 0 | 0 | 0 | 1741208 | 0
2262 | 1187.2 | 0 | 0 | 0 | 0 | 1686.2 | 0 | 0 | 0 | 1412768 | 0
2263 | 1184.8 | 321.9349 | 321.9349 | 313.391 | 313.391 | 1718.7 | 566506.4218 | 112820.7467 | 51176.7442 | 1597292.765 | 86291.8693
2264 | 1603.456 | 1257.121 | 1257.121 | 1223.7577 | 1223.7577 | 1807.5 | 2325756.5821 | 440552.7674 | 199839.6303 | 695987.0073 | 230590.1675
2265 | 1609.349 | 1671.7994 | 1671.7994 | 1627.4307 | 1609.349 | 1849.05 | 3124231.8848 | 579365.64 | 262806.6917 | 0 | 242931.2316
2266 | 1528.207 | 2006.201 | 1587.5087 | 1952.9575 | 1528.207 | 1812.3 | 2910158.7374 | 550154.52 | 249556.2031 | 0 | 286844.4539
2267 | 1584.409 | 2847.9476 | 1645.8926 | 2772.3646 | 1584.409 | 1754.5 | 2937157.5725 | 570387.24 | 258733.9897 | 0 | 388972.4095
2268 | 1411.614 | 3089.2017 | 1466.3913 | 3007.216 | 1411.614 | 1716.45 | 2554882.7341 | 508181.04 | 230516.5662 | 0 | 400263.1497
2269 | 1807.633 | 3200.065 | 1877.7777 | 3115.1371 | 1807.633 | 1441.3 | 2745876.777 | 650747.88 | 295186.4689 | 0 | 1009924.5571
2270 | 1580.825 | 3118.6591 | 1642.1685 | 3035.8916 | 1580.825 | 1742.8 | 2906713.4829 | 569097 | 258148.7225 | 0 | 406588.19
2271 | 1109.428 | 2487.2684 | 1152.4791 | 2421.2576 | 1109.428 | 1782.95 | 2085410.8581 | 399394.08 | 181169.5924 | 0 | 240801.3474
2272 | 1562.899 | 1929.6318 | 1623.5469 | 1878.4204 | 1562.899 | 1802.35 | 2965786.4405 | 562643.64 | 255221.4067 | 0 | 308906.9874
2273 | 1288.141 | 1069.1742 | 1069.1742 | 1040.7989 | 1040.7989 | 1853.7 | 2024545.0107 | 374687.6057 | 169962.4611 | 453378.0609 | 149047.9529
2274 | 1690.754 | 217.186 | 217.186 | 211.422 | 211.422 | 1887.6 | 418977.1566 | 76111.9295 | 34525.2169 | 2711615.5075 | 23261.0676
2275 | 1651.22 | 0 | 0 | 0 | 0 | 1843.45 | 0 | 0 | 0 | 5610845.56 | 0
2276 | 1392.8 | 0 | 0 | 0 | 0 | 1886 | 0 | 0 | 0 | 4732734.4 | 0
2277 | 1446.4 | 0 | 0 | 0 | 0 | 1871.55 | 0 | 0 | 0 | 4914867.2 | 0
2278 | 1270.4 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1857.7 | 605901.7948 | 111351.8261 | 50510.4255 | 3265781.6863 | 43525.8702
2279 | 1509.6 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1835.65 | 1158628.0096 | 215514.4963 | 97759.7701 | 3095403.4159 | 97295.2
2280 | 1620 | 0 | 0 | 0 | 0 | 1816.15 | 0 | 0 | 0 | 2969460 | 0
2281 | 1519.2 | 0 | 0 | 0 | 0 | 1791.9 | 0 | 0 | 0 | 2784693.6 | 0
2282 | 1356.8 | 0 | 0 | 0 | 0 | 1788.4 | 0 | 0 | 0 | 2487014.4 | 0
2283 | 1847.2 | 0 | 0 | 0 | 0 | 1784.05 | 0 | 0 | 0 | 3385917.6 | 0
2284 | 1688 | 0 | 0 | 0 | 0 | 1782.1 | 0 | 0 | 0 | 3094104 | 0
2285 | 1469.6 | 0 | 0 | 0 | 0 | 1782.9 | 0 | 0 | 0 | 2693776.8 | 0
2286 | 1407.2 | 0 | 0 | 0 | 0 | 1788.2 | 0 | 0 | 0 | 2579397.6 | 0
2287 | 1298.407 | 122.9519 | 122.9519 | 119.6888 | 119.6888 | 1798.55 | 226567.9245 | 43087.9734 | 19545.1835 | 2160590.433 | 23601.2776
2288 | 341.456 | 354.7061 | 354.7061 | 345.2924 | 341.456 | 1818.4 | 653230.7568 | 122924.16 | 55759.7648 | 0 | 62008.4096
2289 | 276.424 | 904.4707 | 287.1506 | 880.4665 | 276.424 | 1859.95 | 539578.8015 | 99512.64 | 45140.0392 | 0 | 38713.1812
2290 | 284.243 | 2286.3168 | 295.274 | 2225.6392 | 284.243 | 1874.65 | 560685.1743 | 102327.48 | 46416.8819 | 0 | 35629.8601
2291 | 269.004 | 3756.9454 | 279.4426 | 3657.2381 | 269.004 | 1792.5 | 509547.415 | 96841.44 | 43928.3532 | 0 | 55818.33
2292 | 333.853 | 3461.0741 | 346.8081 | 3369.2191 | 333.853 | 1754.35 | 618049.3078 | 120187.08 | 54518.1949 | 0 | 82010.9894
2293 | 211.973 | 3034.6156 | 220.1986 | 2954.0786 | 211.973 | 1676 | 373631.9878 | 76310.28 | 34615.1909 | 0 | 68679.252
2294 | 211.252 | 3303.8447 | 219.4496 | 3216.1625 | 211.252 | 1669.9 | 370352.4916 | 76050.72 | 34497.4516 | 0 | 69734.2852
2295 | 343.658 | 2545.457 | 356.9936 | 2477.902 | 343.658 | 1771.95 | 641737.1075 | 123716.88 | 56119.3514 | 0 | 78371.2069
2296 | 393.167 | 1354.3708 | 408.4237 | 1318.4265 | 393.167 | 1819.85 | 753113.4365 | 141540.12 | 64204.1711 | 0 | 70829.0351
2297 | 317.159 | 1105.9479 | 329.4663 | 1076.5966 | 317.159 | 1904.7 | 633508.3952 | 114177.24 | 51792.0647 | 0 | 30225.2527
2298 | 348.83 | 220.1248 | 220.1248 | 214.2828 | 214.2828 | 1893.5 | 426206.0866 | 77141.8121 | 34992.3831 | 246624.9965 | 22338.375
2299 | 281.691 | 0 | 0 | 0 | 0 | 1894.45 | 0 | 0 | 0 | 516339.603 | 0
2300 | 266.4 | 0 | 0 | 0 | 0 | 1880.1 | 0 | 0 | 0 | 488311.2 | 0
2301 | 309.6 | 232.1459 | 232.1459 | 225.9848 | 225.9848 | 1787.05 | 423153.2737 | 81354.5381 | 36903.3224 | 153266.6103 | 47588.7883
2302 | 292 | 303.331 | 303.331 | 295.2807 | 292 | 1857.7 | 568536.0259 | 105120 | 47683.6 | 0 | 41551.6
2303 | 243.2 | 252.6373 | 252.6373 | 245.9325 | 243.2 | 1835.65 | 469503.2183 | 87552 | 39714.56 | 0 | 39969.92
2304 | 139.2 | 144.6016 | 144.6016 | 140.764 | 139.2 | 1816.15 | 265829.9664 | 50112 | 22731.36 | 0 | 25591.92
2305 | 142.4 | 0 | 0 | 0 | 0 | 1798.2 | 0 | 0 | 0 | 169456 | 0
2306 | 124 | 0 | 0 | 0 | 0 | 1796.5 | 0 | 0 | 0 | 147560 | 0
2307 | 118.4 | 0 | 0 | 0 | 0 | 1792.9 | 0 | 0 | 0 | 140896 | 0
2308 | 115.2 | 0 | 0 | 0 | 0 | 1790.7 | 0 | 0 | 0 | 137088 | 0
2309 | 101.6 | 0 | 0 | 0 | 0 | 1777.9 | 0 | 0 | 0 | 120904 | 0
2310 | 99.2 | 0 | 0 | 0 | 0 | 1785.55 | 0 | 0 | 0 | 118048 | 0
2311 | 81.795 | 84.969 | 84.969 | 82.714 | 81.795 | 1762.2 | 151672.2774 | 29446.2 | 13357.1235 | 0 | 19450.851
2312 | 89.489 | 570.5781 | 92.9616 | 555.4352 | 89.489 | 1695.65 | 159818.4083 | 32216.04 | 14613.5537 | 0 | 27235.9771
2313 | 89.121 | 2293.6134 | 92.5793 | 2232.7421 | 89.121 | 1740.35 | 163579.1353 | 32083.56 | 14553.4593 | 0 | 23140.2677
2314 | 88.082 | 3286.049 | 91.5 | 3198.839 | 88.082 | 1709.25 | 159216.2168 | 31709.52 | 14383.7906 | 0 | 25609.8415
2315 | 84.446 | 3791.8731 | 87.7229 | 3691.2389 | 84.446 | 1445.85 | 129324.5636 | 30400.56 | 13790.0318 | 0 | 46795.7509
2316 | 92.13 | 2498.5643 | 95.7051 | 2432.2538 | 92.13 | 1578.35 | 153561.1071 | 33166.8 | 15044.829 | 0 | 38846.6145
2317 | 88.264 | 816.0196 | 91.6891 | 794.3629 | 88.264 | 1429.15 | 132646.467 | 31775.04 | 14413.5112 | 0 | 50385.5044
2318 | 92.708 | 1005.5214 | 96.3055 | 978.8355 | 92.708 | 1591.15 | 155604.534 | 33374.88 | 15139.2164 | 0 | 37903.6658
2319 | 86.801 | 971.404 | 90.1693 | 945.6234 | 86.801 | 1540.75 | 141250.3563 | 31248.36 | 14174.6033 | 0 | 39863.3593
2320 | 98.247 | 170.7431 | 102.0595 | 166.2117 | 98.247 | 1740.3 | 180153.3617 | 35368.92 | 16043.7351 | 0 | 25514.7459
2321 | 88.18 | 475.2251 | 91.6018 | 462.6129 | 88.18 | 1828.1 | 169476.6603 | 31744.8 | 14399.794 | 0 | 15158.142
2322 | 94.896 | 98.5784 | 98.5784 | 95.9622 | 94.896 | 1813.6 | 180800.0279 | 34162.56 | 15496.5168 | 0 | 17688.6144
2323 | 102.069 | 106.0298 | 106.0298 | 103.2158 | 102.069 | 1869 | 200344.305 | 36744.84 | 16667.8677 | 0 | 13371.039
2324 | 104.8 | 108.8667 | 108.8667 | 105.9775 | 104.8 | 1852.2 | 203903.5988 | 37728 | 17113.84 | 0 | 15489.44
2325 | 103.2 | 107.2047 | 107.2047 | 104.3595 | 103.2 | 1797.2 | 194272.5495 | 37152 | 16852.56 | 0 | 20928.96
2326 | 111.2 | 115.5151 | 115.5151 | 112.4494 | 111.2 | 1842.65 | 214469.6246 | 40032 | 18158.96 | 0 | 17497.32
2327 | 101.6 | 105.5426 | 105.5426 | 102.7415 | 101.6 | 1827.2 | 195051.7177 | 36576 | 16591.28 | 0 | 17556.48
2328 | 107.2 | 111.3599 | 111.3599 | 108.4044 | 107.2 | 1809.75 | 204254.1928 | 38592 | 17505.76 | 0 | 20394.8
2329 | 96.8 | 0 | 0 | 0 | 0 | 1778.3 | 0 | 0 | 0 | 115192 | 0
2330 | 103.2 | 0 | 0 | 0 | 0 | 1780.5 | 0 | 0 | 0 | 122808 | 0
2331 | 100 | 0 | 0 | 0 | 0 | 1776.15 | 0 | 0 | 0 | 119000 | 0
2332 | 101.6 | 66.6798 | 66.6798 | 64.9102 | 64.9102 | 1773.9 | 121575.8315 | 23367.6689 | 10599.8343 | 43660.8722 | 14308.9646
2333 | 96 | 99.7253 | 99.7253 | 97.0786 | 96 | 1737.85 | 176228.6092 | 34560 | 15676.8 | 0 | 25166.4
2334 | 101.6 | 105.5426 | 105.5426 | 102.7415 | 101.6 | 1709.25 | 183353.1151 | 36576 | 16591.28 | 0 | 29540.2
2335 | 90.638 | 94.1552 | 94.1552 | 91.6564 | 90.638 | 1713.25 | 163812.1734 | 32629.68 | 14801.1854 | 0 | 25990.4465
2336 | 142.371 | 593.4349 | 147.8957 | 577.6854 | 142.371 | 1493.3 | 224104.754 | 51253.56 | 23249.1843 | 0 | 72139.3857
2337 | 876.805 | 1955.6154 | 910.8292 | 1903.7144 | 876.805 | 1376.85 | 1273610.8949 | 315649.8 | 143182.2565 | 0 | 546381.0358
2338 | 1186.13 | 2404.5671 | 1232.1575 | 2340.7512 | 1186.13 | 1248.4 | 1562416.1004 | 427006.8 | 193695.029 | 0 | 891495.308
2339 | 1409.196 | 2576.5111 | 1463.8795 | 2508.1319 | 1409.196 | 1330.55 | 1982823.5095 | 507310.56 | 230121.7068 | 0 | 943386.2622
2340 | 1645.065 | 4101.9678 | 1708.9013 | 3993.1038 | 1645.065 | 1397.2 | 2435031.1515 | 592223.4 | 268639.1145 | 0 | 991645.182
2341 | 1551.507 | 2157.4157 | 1611.7128 | 2100.159 | 1551.507 | 742.65 | 1219554.5227 | 558542.52 | 253361.0931 | 0 | 1950787.3265
2342 | 1454.836 | 2727.4598 | 1511.2905 | 2655.0745 | 1454.836 | 301.3 | 463632.3836 | 523740.96 | 237574.7188 | 0 | 2471329.9132
2343 | 1456.702 | 1742.0101 | 1513.229 | 1695.7781 | 1456.702 | 1239.25 | 1903526.92 | 524412.72 | 237879.4366 | 0 | 1108186.0465
2344 | 1631.387 | 834.0574 | 834.0574 | 811.9219 | 811.9219 | 1096.15 | 936980.9083 | 292291.8996 | 132586.8533 | 1502079.4489 | 718332.0759
2345 | 1631.553 | 959.2801 | 959.2801 | 933.8213 | 933.8213 | 1559.75 | 1529865.7309 | 336175.6748 | 152493.0214 | 1278942.1713 | 402418.437
2346 | 1765.931 | 188.9285 | 188.9285 | 183.9144 | 183.9144 | 1715.7 | 331444.6627 | 66209.184 | 30033.2215 | 2899836.4276 | 51180.8232
2347 | 1730.86 | 0 | 0 | 0 | 0 | 1844.05 | 0 | 0 | 0 | 5881462.28 | 0
2348 | 1846.4 | 0 | 0 | 0 | 0 | 1844.15 | 0 | 0 | 0 | 6274067.2 | 0
2349 | 1725.6 | 0 | 0 | 0 | 0 | 1828.65 | 0 | 0 | 0 | 5863588.8 | 0
2350 | 1554.4 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1821.45 | 592163.6467 | 111351.8261 | 50510.4255 | 4230813.6863 | 54613.8027
2351 | 1998.4 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1806 | 1136793.8507 | 215514.4963 | 97759.7701 | 4756345.8159 | 114848
2352 | 1700.8 | 0 | 0 | 0 | 0 | 1789.85 | 0 | 0 | 0 | 3117566.4 | 0
2353 | 1940.8 | 0 | 0 | 0 | 0 | 1791.9 | 0 | 0 | 0 | 2309552 | 0
2354 | 1621.6 | 0 | 0 | 0 | 0 | 1703.9 | 0 | 0 | 0 | 1929704 | 0
2355 | 1272.8 | 0 | 0 | 0 | 0 | 1682.05 | 0 | 0 | 0 | 1514632 | 0
2356 | 1277.6 | 0 | 0 | 0 | 0 | 1697.6 | 0 | 0 | 0 | 1520344 | 0
2357 | 1742.4 | 0 | 0 | 0 | 0 | 1680.9 | 0 | 0 | 0 | 2073456 | 0
2358 | 1696 | 0 | 0 | 0 | 0 | 1731.3 | 0 | 0 | 0 | 2018240 | 0
2359 | 1093.028 | 370.8969 | 370.8969 | 361.0535 | 361.0535 | 1798.55 | 683642.3902 | 129979.2682 | 58960.0403 | 1341709.2168 | 71195.6532
2360 | 1153.367 | 1198.1231 | 1198.1231 | 1166.3256 | 1153.367 | 1716.4 | 2081664.1407 | 415212.12 | 188344.8311 | 0 | 327094.8812
2361 | 1724.16 | 1888.8909 | 1791.0656 | 1838.7607 | 1724.16 | 1826.45 | 3311932.734 | 620697.6 | 281555.328 | 0 | 299227.968
2362 | 2138.256 | 3067.4689 | 2221.2305 | 2986.0599 | 2138.256 | 1868.75 | 4224045.8346 | 769772.16 | 349177.2048 | 0 | 280646.1
2363 | 1900.048 | 3708.9828 | 1973.7789 | 3610.5484 | 1900.048 | 1727 | 3470749.6522 | 684017.28 | 310277.8384 | 0 | 518713.104
2364 | 2133.191 | 3955.2709 | 2215.9689 | 3850.3002 | 2133.191 | 1719.95 | 3874602.9446 | 767948.76 | 348350.0903 | 0 | 597400.1396
2365 | 1700.026 | 3973.9008 | 1765.9951 | 3868.4357 | 1700.026 | 1706 | 3051639.3927 | 612009.36 | 277614.2458 | 0 | 499807.644
2366 | 1540.681 | 3740.5697 | 1600.4667 | 3641.297 | 1540.681 | 1742.8 | 2829473.142 | 554645.16 | 251593.2073 | 0 | 396263.1532
2367 | 1354.534 | 3214.2593 | 1407.0964 | 3128.9546 | 1354.534 | 1858.55 | 2654092.3451 | 487632.24 | 221195.4022 | 0 | 191598.8343
2368 | 1652.807 | 2400.1791 | 1716.9438 | 2336.4797 | 1652.807 | 1904.35 | 3306583.2645 | 595010.52 | 269903.3831 | 0 | 158090.9896
2369 | 1811.042 | 1291.0317 | 1291.0317 | 1256.7685 | 1256.7685 | 1904.7 | 2505737.4019 | 452436.6444 | 205230.289 | 1015983.4047 | 117236.5352
2370 | 1517.038 | 233.0236 | 233.0236 | 226.8393 | 226.8393 | 1893.5 | 449759.4864 | 81662.1559 | 37042.8613 | 2364934.1769 | 23647.3665
2371 | 1866.297 | 0 | 0 | 0 | 0 | 1894.45 | 0 | 0 | 0 | 6341677.206 | 0
2372 | 1745.6 | 0 | 0 | 0 | 0 | 1886 | 0 | 0 | 0 | 5931548.8 | 0
2373 | 2057.6 | 0 | 0 | 0 | 0 | 1871.55 | 0 | 0 | 0 | 6991724.8 | 0
2374 | 1675.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1857.7 | 603085.3777 | 111351.8261 | 50510.4255 | 4641292.0863 | 43525.8702
2375 | 1663.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1835.65 | 1154724.6333 | 215514.4963 | 97759.7701 | 3617336.2159 | 97295.2
2376 | 1429.6 | 0 | 0 | 0 | 0 | 1816.15 | 0 | 0 | 0 | 2620456.8 | 0
2377 | 1479.2 | 0 | 0 | 0 | 0 | 1797.3 | 0 | 0 | 0 | 1760248 | 0
2378 | 1613.6 | 0 | 0 | 0 | 0 | 1788.4 | 0 | 0 | 0 | 1920184 | 0
2379 | 1020.8 | 0 | 0 | 0 | 0 | 1784.05 | 0 | 0 | 0 | 1214752 | 0
2380 | 1254.4 | 0 | 0 | 0 | 0 | 1782.1 | 0 | 0 | 0 | 1492736 | 0
2381 | 1267.2 | 0 | 0 | 0 | 0 | 1782.9 | 0 | 0 | 0 | 1507968 | 0
2382 | 1392 | 0 | 0 | 0 | 0 | 1788.2 | 0 | 0 | 0 | 1656480 | 0
2383 | 1293.522 | 382.9429 | 382.9429 | 372.7798 | 372.7798 | 1798.55 | 704574.8657 | 134200.7312 | 60874.9428 | 1687720.4363 | 73508.0978
2384 | 650.269 | 903.7248 | 675.5025 | 879.7404 | 650.269 | 1806.6 | 1239080.5837 | 234096.84 | 106188.9277 | 0 | 125762.0246
2385 | 1468.701 | 2180.3868 | 1525.6936 | 2122.5205 | 1468.701 | 1855.45 | 2872147.8359 | 528732.36 | 239838.8733 | 0 | 212300.7295
2386 | 1476.864 | 3394.7246 | 1534.1733 | 3304.6304 | 1476.864 | 1772.65 | 2768950.5442 | 531671.04 | 241171.8912 | 0 | 335765.0304
2387 | 1368.496 | 3833.23 | 1421.6001 | 3731.4982 | 1368.496 | 1664.5 | 2417151.8318 | 492658.56 | 223475.3968 | 0 | 459130.408
2388 | 1103.419 | 4101.1108 | 1146.2369 | 3992.2695 | 1103.419 | 1521.6 | 1774667.606 | 397230.84 | 180188.3227 | 0 | 527875.6496
2389 | 1738.664 | 4088.6908 | 1806.1324 | 3980.1792 | 1738.664 | 1441.3 | 2644049.225 | 625919.04 | 283923.8312 | 0 | 971391.5768
2390 | 1353.651 | 3756.0292 | 1406.1791 | 3656.3462 | 1353.651 | 1464.2 | 2097572.7375 | 487314.36 | 221051.2083 | 0 | 725286.2058
2391 | 1671.773 | 3198.3323 | 1736.6457 | 3113.4503 | 1671.773 | 1622.95 | 2876100.0397 | 601838.28 | 273000.5309 | 0 | 630342.0096
2392 | 1643.7 | 2360.9757 | 1707.4834 | 2298.3167 | 1643.7 | 1757.85 | 3050163.5095 | 591732 | 268416.21 | 0 | 398021.955
2393 | 1554.145 | 1269.5108 | 1269.5108 | 1235.8187 | 1235.8187 | 1848.7 | 2406206.9693 | 444894.7292 | 201809.1924 | 583492.1221 | 183024.1301
2394 | 1624.376 | 230.7996 | 230.7996 | 224.6743 | 224.6743 | 1860 | 439576.7534 | 80882.7361 | 36689.3078 | 2565653.2769 | 30789.08
2395 | 1597.412 | 0 | 0 | 0 | 0 | 1894.45 | 0 | 0 | 0 | 5428005.976 | 0
2396 | 1305.6 | 0 | 0 | 0 | 0 | 1886 | 0 | 0 | 0 | 4436428.8 | 0
2397 | 1634.4 | 0 | 0 | 0 | 0 | 1865.65 | 0 | 0 | 0 | 5553691.2 | 0
2398 | 1851.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1857.7 | 602566.4395 | 111351.8261 | 50510.4255 | 5239340.0863 | 43525.8702
2399 | 1613.6 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1835.65 | 1156090.455 | 215514.4963 | 97759.7701 | 3448795.4159 | 97295.2
2400 | 1363.2 | 0 | 0 | 0 | 0 | 1816.15 | 0 | 0 | 0 | 2498745.6 | 0
2401 | 1245.6 | 0 | 0 | 0 | 0 | 1786 | 0 | 0 | 0 | 1482264 | 0
2402 | 1235.2 | 0 | 0 | 0 | 0 | 1686.4 | 0 | 0 | 0 | 1469888 | 0
2403 | 1324 | 0 | 0 | 0 | 0 | 1682.05 | 0 | 0 | 0 | 1575560 | 0
2404 | 1393.6 | 0 | 0 | 0 | 0 | 1674.3 | 0 | 0 | 0 | 1658384 | 0
2405 | 1192 | 0 | 0 | 0 | 0 | 1680.9 | 0 | 0 | 0 | 1418480 | 0
2406 | 1108 | 0 | 0 | 0 | 0 | 1686.2 | 0 | 0 | 0 | 1318520 | 0
2407 | 1071.458 | 377.8517 | 377.8517 | 367.8237 | 367.8237 | 1696.55 | 657726.3581 | 132416.5478 | 60065.6174 | 1289761.5912 | 109255.0484
2408 | 700.377 | 852.3912 | 727.555 | 829.7692 | 700.377 | 1685.8 | 1248915.837 | 252135.72 | 114371.5641 | 0 | 220058.4534
2409 | 1179.725 | 1274.0307 | 1225.5039 | 1240.2186 | 1179.725 | 1752.15 | 2185788.1623 | 424701 | 192649.0925 | 0 | 292394.8413
2410 | 1627.857 | 1691.0256 | 1691.0256 | 1646.1467 | 1627.857 | 1724.65 | 2973408.4712 | 586028.52 | 265829.0481 | 0 | 448230.4249
2411 | 1504.309 | 2281.7544 | 1562.6833 | 2221.1979 | 1504.309 | 1727 | 2755707.0057 | 541551.24 | 245653.6597 | 0 | 410676.357
2412 | 1607.655 | 2530.5055 | 1670.0396 | 2463.3473 | 1607.655 | 1623.95 | 2757092.3376 | 578755.8 | 262530.0615 | 0 | 604558.6628
2413 | 1708.11 | 3920.7213 | 1774.3928 | 3816.6675 | 1708.11 | 1441.3 | 2596595.512 | 614919.6 | 278934.363 | 0 | 954321.057
2414 | 1747.615 | 2808.8719 | 1815.4308 | 2734.326 | 1747.615 | 1464.2 | 2702838.4674 | 629141.4 | 285385.5295 | 0 | 936372.117
2415 | 1656.806 | 1979.4217 | 1721.0979 | 1926.8889 | 1656.806 | 1580.45 | 2767683.8083 | 596450.16 | 270556.4198 | 0 | 695112.9573
2416 | 1940.668 | 1178.9852 | 1178.9852 | 1147.6956 | 1147.6956 | 1684.05 | 2036133.4074 | 413170.4129 | 187418.6901 | 1453518.425 | 354943.9171
2417 | 1471.768 | 1218.946 | 1218.946 | 1186.5958 | 1186.5958 | 1847.8 | 2307514.7923 | 427174.4866 | 193771.0935 | 522720.6497 | 176779.6912
2418 | 1831.384 | 215.311 | 215.311 | 209.5967 | 209.5967 | 1860 | 410687.6969 | 75454.8287 | 34227.1487 | 2972736.0357 | 28722.82
2419 | 1741.725 | 0 | 0 | 0 | 0 | 1894.45 | 0 | 0 | 0 | 5918381.55 | 0
2420 | 1332.8 | 0 | 0 | 0 | 0 | 1880.1 | 0 | 0 | 0 | 4528854.4 | 0
2421 | 1913.6 | 0 | 0 | 0 | 0 | 1838.05 | 0 | 0 | 0 | 6502412.8 | 0
2422 | 1916 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1857.7 | 603157.425 | 111351.8261 | 50510.4255 | 5459530.4863 | 43525.8702
2423 | 1797.6 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1835.65 | 1156317.0207 | 215514.4963 | 97759.7701 | 4074027.4159 | 97295.2
2424 | 1308 | 0 | 0 | 0 | 0 | 1816.15 | 0 | 0 | 0 | 2397564 | 0
2425 | 1379.2 | 0 | 0 | 0 | 0 | 1786 | 0 | 0 | 0 | 1641248 | 0
2426 | 1590.4 | 0 | 0 | 0 | 0 | 1686.4 | 0 | 0 | 0 | 1892576 | 0
2427 | 1549.6 | 0 | 0 | 0 | 0 | 1676.25 | 0 | 0 | 0 | 1844024 | 0
2428 | 934.4 | 0 | 0 | 0 | 0 | 1667.1 | 0 | 0 | 0 | 1111936 | 0
2429 | 1459.2 | 0 | 0 | 0 | 0 | 1675.1 | 0 | 0 | 0 | 1736448 | 0
2430 | 1591.2 | 0 | 0 | 0 | 0 | 1683.3 | 0 | 0 | 0 | 1893528 | 0
2431 | 966.93 | 369.2525 | 369.2525 | 359.4527 | 359.4527 | 1714.05 | 649691.799 | 129402.9853 | 58698.632 | 1113505.823 | 100611.2216
2432 | 1477.577 | 1418.7393 | 1418.7393 | 1381.0867 | 1381.0867 | 1689.5 | 2468603.5202 | 497191.2148 | 225531.4594 | 176866.7058 | 419756.256
2433 | 1354.983 | 1786.2715 | 1407.5628 | 1738.8648 | 1354.983 | 1713.45 | 2455284.9414 | 487793.88 | 221268.7239 | 0 | 388270.3786
2434 | 1698.036 | 2703.3439 | 1763.9279 | 2631.5987 | 1698.036 | 1719.65 | 3093336.8947 | 611292.96 | 277289.2788 | 0 | 476044.3926
2435 | 1687.35 | 3638.1041 | 1752.8272 | 3541.5508 | 1687.35 | 1629.35 | 2912639.975 | 607446 | 275544.255 | 0 | 625416.2775
2436 | 1799.841 | 3853.8399 | 1869.6834 | 3751.5611 | 1799.841 | 1591.45 | 3029360.4263 | 647942.76 | 293914.0353 | 0 | 735325.0406
2437 | 1492.56 | 3854.5089 | 1550.4784 | 3752.2123 | 1492.56 | 1441.3 | 2271435.0449 | 537321.6 | 243735.048 | 0 | 833893.272
2438 | 1614.825 | 3583.5585 | 1677.4879 | 3488.4528 | 1614.825 | 1464.2 | 2494857.7902 | 581337 | 263700.9225 | 0 | 865223.235
2439 | 1802.673 | 3072.3939 | 1872.6253 | 2990.8542 | 1802.673 | 1483.25 | 2827774.2306 | 648962.28 | 294376.5009 | 0 | 931531.2728
2440 | 1703.159 | 1743.5953 | 1743.5953 | 1697.3213 | 1697.3213 | 1691.85 | 3028084.7119 | 611035.6553 | 277172.5625 | 10700.5689 | 511965.6486
2441 | 1953.342 | 685.9238 | 685.9238 | 667.7198 | 667.7198 | 1837.7 | 1290247.5173 | 240379.1172 | 109038.6384 | 2356545.5475 | 106078.4685
2442 | 1610.257 | 120.5626 | 120.5626 | 117.363 | 117.363 | 1837.5 | 226932.792 | 42250.6705 | 19165.3736 | 2736474.7505 | 18668.1625
2443 | 1843.247 | 0 | 0 | 0 | 0 | 1888.55 | 0 | 0 | 0 | 6263353.306 | 0
2444 | 1636 | 0 | 0 | 0 | 0 | 1829.1 | 0 | 0 | 0 | 5559128 | 0
2445 | 1706.4 | 0 | 0 | 0 | 0 | 1820.5 | 0 | 0 | 0 | 5798347.2 | 0
2446 | 2003.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1857.7 | 604208.1966 | 111351.8261 | 50510.4255 | 5755836.0863 | 43525.8702
2447 | 1822.4 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1835.65 | 1158780.7718 | 215514.4963 | 97759.7701 | 4158297.8159 | 97295.2
2448 | 1698.4 | 0 | 0 | 0 | 0 | 1815.15 | 0 | 0 | 0 | 3113167.2 | 0
2449 | 1377.6 | 0 | 0 | 0 | 0 | 1791.9 | 0 | 0 | 0 | 2525140.8 | 0
2450 | 1225.6 | 0 | 0 | 0 | 0 | 1686.4 | 0 | 0 | 0 | 2246524.8 | 0
2451 | 1188 | 0 | 0 | 0 | 0 | 1682.05 | 0 | 0 | 0 | 2177604 | 0
2452 | 1199.2 | 0 | 0 | 0 | 0 | 1677.2 | 0 | 0 | 0 | 2198133.6 | 0
2453 | 1212 | 0 | 0 | 0 | 0 | 1632.9 | 0 | 0 | 0 | 2221596 | 0
2454 | 1070.4 | 0 | 0 | 0 | 0 | 1641.7 | 0 | 0 | 0 | 1962043.2 | 0
2455 | 974.019 | 231.8758 | 231.8758 | 225.7219 | 225.7219 | 1693.65 | 403160.2208 | 81259.8864 | 36860.3874 | 1371628.5719 | 67687.1135
2456 | 196.406 | 290.6326 | 204.0275 | 282.9194 | 196.406 | 1633.25 | 338294.9876 | 70706.16 | 32073.0998 | 0 | 72031.9005
2457 | 173.54 | 1925.9669 | 180.2742 | 1874.8527 | 173.54 | 1709.95 | 313205.0763 | 62474.4 | 28339.082 | 0 | 50335.277
2458 | 0 | 3086.9485 | 0 | 3005.0226 | 0 | 1529.8 | 0 | 0 | 0 | 0 | 0
2459 | 0 | 3586.2438 | 0 | 3491.0669 | 0 | 1462.3 | 0 | 0 | 0 | 0 | 0
2460 | 0 | 2932.1438 | 0 | 2854.3263 | 0 | 1451.75 | 0 | 0 | 0 | 0 | 0
2461 | 0 | 3239.5064 | 0 | 3153.5316 | 0 | 1441.3 | 0 | 0 | 0 | 0 | 0
2462 | 267.984 | 2245.3983 | 278.3831 | 2185.8066 | 267.984 | 1464.2 | 414633.7979 | 96474.24 | 43761.7872 | 0 | 143585.8272
2463 | 256.129 | 3105.4123 | 266.068 | 3022.9963 | 256.129 | 1553.1 | 419804.8061 | 92206.44 | 41825.8657 | 0 | 114464.0501
2464 | 126.647 | 2279.6581 | 131.5615 | 2219.1572 | 126.647 | 1629.35 | 217577.3506 | 45592.92 | 20681.4551 | 0 | 46941.7105
2465 | 227.812 | 1214.2568 | 236.6522 | 1182.0311 | 227.812 | 1778.7 | 426119.8839 | 82012.32 | 37201.6996 | 0 | 50414.7956
2466 | 353.747 | 215.1396 | 215.1396 | 209.4299 | 209.4299 | 1833.7 | 404295.3823 | 75394.7613 | 34199.9015 | 264533.2578 | 34091.5
2467 | 216.663 | 197.242 | 197.242 | 192.0073 | 192.0073 | 1837.55 | 370830.3957 | 69122.6342 | 31354.7949 | 45193.8664 | 30845.0313
2468 | 193.6 | 201.1126 | 201.1126 | 195.7752 | 193.6 | 1784 | 363134.6997 | 69696 | 31614.88 | 0 | 41817.6
2469 | 127.2 | 132.136 | 132.136 | 128.6291 | 127.2 | 1814.65 | 242345.9159 | 45792 | 20771.76 | 0 | 23576.52
2470 | 117.6 | 122.1634 | 122.1634 | 118.9213 | 117.6 | 1857.7 | 229254.9947 | 42336 | 19204.08 | 0 | 16734.48
2471 | 128.8 | 133.7981 | 133.7981 | 130.2471 | 128.8 | 1835.65 | 248699.1897 | 46368 | 21033.04 | 0 | 21168.28
2472 | 140.8 | 146.2637 | 146.2637 | 142.3819 | 140.8 | 1816.15 | 269126.6088 | 50688 | 22992.64 | 0 | 25886.08
2473 | 108.8 | 0 | 0 | 0 | 0 | 1792.3 | 0 | 0 | 0 | 129472 | 0
2474 | 100 | 0 | 0 | 0 | 0 | 1694.5 | 0 | 0 | 0 | 119000 | 0
2475 | 89.6 | 0 | 0 | 0 | 0 | 1685.1 | 0 | 0 | 0 | 106624 | 0
2476 | 99.2 | 0 | 0 | 0 | 0 | 1682.9 | 0 | 0 | 0 | 118048 | 0
2477 | 91.2 | 0 | 0 | 0 | 0 | 1681.9 | 0 | 0 | 0 | 108528 | 0
2478 | 98.4 | 0 | 0 | 0 | 0 | 1686.55 | 0 | 0 | 0 | 117096 | 0
2479 | 64.271 | 66.765 | 66.765 | 64.9931 | 64.271 | 1738.8 | 117819.7619 | 23137.56 | 10495.4543 | 0 | 16787.5852
2480 | 44.716 | 799.4673 | 46.4512 | 778.2498 | 44.716 | 1660.65 | 78337.2382 | 16097.76 | 7302.1228 | 0 | 15174.3746
2481 | 503.248 | 1910.1209 | 522.7764 | 1859.4274 | 503.248 | 1695.25 | 898841.1659 | 181169.28 | 82180.3984 | 0 | 153364.828
2482 | 593.572 | 2634.4151 | 616.6054 | 2564.4991 | 593.572 | 1638.95 | 1027347.2935 | 213685.92 | 96930.3076 | 0 | 214309.1706
2483 | 451.248 | 1982.3376 | 468.7586 | 1929.7274 | 451.248 | 1445.85 | 690104.5884 | 162449.28 | 73688.7984 | 0 | 250059.0792
2484 | 445.515 | 4043.5496 | 462.8031 | 3936.236 | 445.515 | 1438.65 | 677164.8164 | 160385.4 | 72752.5995 | 0 | 250089.8453
2485 | 1718.709 | 2748.5673 | 1785.4031 | 2675.6218 | 1718.709 | 1429.15 | 2590734.7216 | 618735.24 | 280665.1797 | 0 | 981125.0326
2486 | 1825.482 | 2865.9896 | 1896.3194 | 2789.9278 | 1825.482 | 1553.8 | 2999539.6798 | 657173.52 | 298101.2106 | 0 | 814530.0684
2487 | 1311.2 | 2167.6998 | 1362.0808 | 2110.1703 | 1311.2 | 1730.6 | 2396216.0654 | 472032 | 214118.96 | 0 | 353237.28
2488 | 1571.2 | 1961.0057 | 1632.17 | 1908.9617 | 1571.2 | 1743.8 | 2887540.0603 | 565632 | 256576.96 | 0 | 402541.44
2489 | 1255.2 | 1200.69 | 1200.69 | 1168.8243 | 1168.8243 | 1828.1 | 2244296.4579 | 420776.7641 | 190869.0155 | 158326.5764 | 196670.79
2490 | 1663.487 | 207.1377 | 207.1377 | 201.6403 | 201.6403 | 1813.6 | 384319.7728 | 72590.5246 | 32927.8685 | 2679564.9167 | 36790.7
2491 | 1610.935 | 0 | 0 | 0 | 0 | 1829.6 | 0 | 0 | 0 | 5473957.13 | 0
2492 | 1180.8 | 0 | 0 | 0 | 0 | 1753.2 | 0 | 0 | 0 | 4012358.4 | 0
2493 | 1295.2 | 0 | 0 | 0 | 0 | 1771.7 | 0 | 0 | 0 | 4401089.6 | 0
2494 | 1408 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1842.65 | 597585.5375 | 111351.8261 | 50510.4255 | 3733346.4863 | 48129.2739
2495 | 1508 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1827.2 | 1149308.6967 | 215514.4963 | 97759.7701 | 3089966.6159 | 102297.6
2496 | 1367.2 | 0 | 0 | 0 | 0 | 1809.75 | 0 | 0 | 0 | 2506077.6 | 0
2497 | 1770.4 | 0 | 0 | 0 | 0 | 1728.2 | 0 | 0 | 0 | 2106776 | 0
2498 | 1622.4 | 0 | 0 | 0 | 0 | 1768.7 | 0 | 0 | 0 | 1930656 | 0
2499 | 1314.4 | 0 | 0 | 0 | 0 | 1674.15 | 0 | 0 | 0 | 1564136 | 0
2500 | 1200.8 | 0 | 0 | 0 | 0 | 1666.1 | 0 | 0 | 0 | 1428952 | 0
2501 | 1348 | 0 | 0 | 0 | 0 | 1667.7 | 0 | 0 | 0 | 1604120 | 0
2502 | 1156 | 0 | 0 | 0 | 0 | 1669.6 | 0 | 0 | 0 | 1375640 | 0
2503 | 1375.182 | 397.6337 | 397.6337 | 387.0807 | 387.0807 | 1685.65 | 690017.7012 | 139349.0522 | 63210.2784 | 1811189.6821 | 119105.0146
2504 | 1228.928 | 1276.6162 | 1276.6162 | 1242.7355 | 1228.928 | 1605.65 | 2088870.8419 | 442414.08 | 200683.9424 | 0 | 484627.7568
2505 | 1763.437 | 1897.1109 | 1831.8667 | 1846.7626 | 1763.437 | 1499.05 | 2803494.845 | 634837.32 | 287969.2621 | 0 | 883393.7652
2506 | 1786.454 | 1070.5579 | 1070.5579 | 1042.1459 | 1042.1459 | 1510.4 | 1671641.2252 | 375172.5133 | 170182.4206 | 1364316.8019 | 502384.9248
2507 | 1601.327 | 3160.0524 | 1663.4661 | 3076.1863 | 1601.327 | 1539.9 | 2620210.4527 | 576477.72 | 261496.6991 | 0 | 736770.5527
2508 | 1886.909 | 3715.9116 | 1960.129 | 3617.2933 | 1886.909 | 1536.9 | 3082053.3509 | 679287.24 | 308132.2397 | 0 | 873827.5579
2509 | 1830.371 | 1902.1024 | 1901.3981 | 1851.6216 | 1830.371 | 1457.3 | 2837239.0267 | 658933.56 | 298899.5843 | 0 | 993342.3417
2510 | 1393.734 | 3723.6081 | 1447.8175 | 3624.7856 | 1393.734 | 1395.6 | 2060908.0558 | 501744.24 | 227596.7622 | 0 | 842372.8296
2511 | 1534.199 | 2160.502 | 1593.7332 | 2103.1634 | 1534.199 | 1572.3 | 2552464.4553 | 552311.64 | 250534.6967 | 0 | 656176.9123
2512 | 1641.378 | 1771.7282 | 1705.0713 | 1724.7075 | 1641.378 | 1638.15 | 2838054.4929 | 590896.08 | 268037.0274 | 0 | 593932.6293
2513 | 1522.665 | 1014.8426 | 1014.8426 | 987.9093 | 987.9093 | 1726.25 | 1797033.9998 | 355647.3368 | 161325.5836 | 980207.2553 | 264719.2612
2514 | 1554.326 | 223.638 | 223.638 | 217.7028 | 217.7028 | 1830.8 | 417674.4815 | 78373.0115 | 35550.8688 | 2450030.3078 | 36056.1816
2515 | 1267.674 | 0 | 0 | 0 | 0 | 1849.95 | 0 | 0 | 0 | 4307556.252 | 0
2516 | 1214.4 | 0 | 0 | 0 | 0 | 1844.15 | 0 | 0 | 0 | 4126531.2 | 0
2517 | 1422.4 | 0 | 0 | 0 | 0 | 1828.65 | 0 | 0 | 0 | 4833315.2 | 0
2518 | 1226.4 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1815.55 | 590120.5406 | 111351.8261 | 50510.4255 | 3116269.6863 | 56418.4593
2519 | 1222.4 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1800.1 | 1132845.5563 | 215514.4963 | 97759.7701 | 2119497.8159 | 118340.8
2520 | 1440.8 | 0 | 0 | 0 | 0 | 1750.45 | 0 | 0 | 0 | 2640986.4 | 0
2521 | 1159.2 | 0 | 0 | 0 | 0 | 1746.8 | 0 | 0 | 0 | 1379448 | 0
2522 | 1145.6 | 0 | 0 | 0 | 0 | 1683.5 | 0 | 0 | 0 | 1363264 | 0
2523 | 1368.8 | 0 | 0 | 0 | 0 | 1655.05 | 0 | 0 | 0 | 1628872 | 0
2524 | 864.8 | 0 | 0 | 0 | 0 | 1632.1 | 0 | 0 | 0 | 1029112 | 0
2525 | 943.2 | 0 | 0 | 0 | 0 | 1636.4 | 0 | 0 | 0 | 1122408 | 0
2526 | 1092 | 0 | 0 | 0 | 0 | 1676.1 | 0 | 0 | 0 | 1299480 | 0
2527 | 1156.517 | 365.5086 | 365.5086 | 355.8082 | 355.8082 | 1696.55 | 635506.788 | 128090.968 | 58103.4863 | 1467699.1487 | 105686.1729
2528 | 715.847 | 862.5456 | 743.6253 | 839.6541 | 715.847 | 1713.5 | 1292132.6752 | 257704.92 | 116897.8151 | 0 | 205090.1655
2529 | 1374.694 | 1643.0879 | 1428.0387 | 1599.4812 | 1374.694 | 1757.95 | 2541833.7651 | 494889.84 | 224487.5302 | 0 | 332744.6827
2530 | 1474.584 | 2755.4504 | 1531.8049 | 2682.3222 | 1474.584 | 1748.65 | 2721326.4899 | 530850.24 | 240799.5672 | 0 | 370636.6884
2531 | 1171.084 | 3723.5842 | 1216.5276 | 3624.7623 | 1171.084 | 1629.35 | 2017924.7757 | 421590.24 | 191238.0172 | 0 | 434062.2846
2532 | 1452.682 | 3941.113 | 1509.053 | 3836.518 | 1452.682 | 1591.45 | 2434544.8189 | 522965.52 | 237222.9706 | 0 | 593493.2311
2533 | 1536.423 | 3286.7055 | 1596.0435 | 3199.4781 | 1536.423 | 1441.3 | 2324355.6006 | 553112.28 | 250897.8759 | 0 | 858399.5301
2534 | 1489.362 | 3019.1271 | 1547.1563 | 2939.0011 | 1489.362 | 1723.9 | 2700697.4251 | 536170.32 | 243212.8146 | 0 | 411212.8482
2535 | 1094.152 | 2537.0406 | 1136.6103 | 2469.709 | 1094.152 | 1772.55 | 2042932.3731 | 393894.72 | 178675.0216 | 0 | 248864.8724
2536 | 1400.201 | 1836.5517 | 1454.5354 | 1787.8107 | 1400.201 | 1799.45 | 2650958.7108 | 504072.36 | 228652.8233 | 0 | 280810.3106
2537 | 1681.075 | 976.3539 | 976.3539 | 950.442 | 950.442 | 1853.2 | 1847222.5782 | 342159.1145 | 155207.1761 | 1339250.3172 | 136573.4716
2538 | 1647.588 | 192.5061 | 192.5061 | 187.3971 | 187.3971 | 1893.5 | 371950.8346 | 67462.9542 | 30601.9456 | 2676529.929 | 19535.6145
2539 | 1122.777 | 0 | 0 | 0 | 0 | 1894.45 | 0 | 0 | 0 | 3815196.246 | 0
2540 | 1656 | 0 | 0 | 0 | 0 | 1886 | 0 | 0 | 0 | 5627088 | 0
2541 | 1400.8 | 0 | 0 | 0 | 0 | 1871.55 | 0 | 0 | 0 | 4759918.4 | 0
2542 | 1624.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1857.7 | 601801.0212 | 111351.8261 | 50510.4255 | 4470032.8863 | 43525.8702
2543 | 1046.4 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1835.65 | 1155096.2488 | 215514.4963 | 97759.7701 | 1521449.8159 | 97295.2
2544 | 1645.6 | 0 | 0 | 0 | 0 | 1816.15 | 0 | 0 | 0 | 3016384.8 | 0
2545 | 1430.4 | 0 | 0 | 0 | 0 | 1797.3 | 0 | 0 | 0 | 1702176 | 0
2546 | 1149.6 | 0 | 0 | 0 | 0 | 1782 | 0 | 0 | 0 | 1368024 | 0
2547 | 1410.4 | 0 | 0 | 0 | 0 | 1699.55 | 0 | 0 | 0 | 1678376 | 0
2548 | 1274.4 | 0 | 0 | 0 | 0 | 1680.1 | 0 | 0 | 0 | 1516536 | 0
2549 | 1276.8 | 0 | 0 | 0 | 0 | 1701.9 | 0 | 0 | 0 | 1519392 | 0
2550 | 1566.4 | 0 | 0 | 0 | 0 | 1782.3 | 0 | 0 | 0 | 1864016 | 0
2551 | 1491.966 | 132.5681 | 132.5681 | 129.0498 | 129.0498 | 1798.05 | 244211.5554 | 46457.9357 | 21073.8358 | 2498225.3552 | 25510.324
2552 | 1493.014 | 534.9273 | 534.9273 | 520.7306 | 520.7306 | 1716.4 | 943434.2157 | 187463.0275 | 85035.3122 | 1782195.4137 | 144555.174
2553 | 1539.824 | 1599.5765 | 1599.5765 | 1557.1246 | 1539.824 | 1757.95 | 2857860.24 | 554336.64 | 251453.2592 | 0 | 372714.3992
2554 | 1782.499 | 2615.9877 | 1851.6684 | 2546.5608 | 1782.499 | 1738.55 | 3272978.533 | 641699.64 | 291082.0867 | 0 | 466034.3635
2555 | 1835.337 | 3611.5688 | 1906.5558 | 3515.7198 | 1835.337 | 1656.7 | 3214226.7482 | 660721.32 | 299710.5321 | 0 | 630071.1921
2556 | 1632.697 | 3993.7067 | 1696.0534 | 3887.7159 | 1632.697 | 1646.15 | 2831734.5592 | 587770.92 | 266619.4201 | 0 | 577729.8334
2557 | 1766.248 | 3954.3786 | 1834.7868 | 3849.4315 | 1766.248 | 1635.7 | 3037659.0851 | 635849.28 | 288428.2984 | 0 | 643444.1464
2558 | 1904.871 | 3652.8883 | 1978.789 | 3555.9427 | 1904.871 | 1732.4 | 3479018.5622 | 685753.56 | 311065.4343 | 0 | 509743.4796
2559 | 1996.523 | 3096.8546 | 2073.9976 | 3014.6658 | 1996.523 | 1765.35 | 3713492.3024 | 718748.28 | 326032.2059 | 0 | 468484.122
2560 | 1909.872 | 1952.8148 | 1952.8148 | 1900.9881 | 1900.9881 | 1775.35 | 3555472.8664 | 684355.7255 | 310431.3611 | 16284.1401 | 418023.3284
2561 | 1550.773 | 256.7385 | 256.7385 | 249.9248 | 249.9248 | 1892.9 | 497824.6101 | 89972.9336 | 40812.7224 | 2384454.7218 | 26200.7298
2562 | 1749.963 | 46.0637 | 46.0637 | 44.8412 | 44.8412 | 1893 | 89196.7575 | 16142.8367 | 7322.5701 | 3125488.2356 | 4696.551
2563 | 2041.861 | 0 | 0 | 0 | 0 | 1894.45 | 0 | 0 | 0 | 6938243.678 | 0
2564 | 1636 | 0 | 0 | 0 | 0 | 1881.5 | 0 | 0 | 0 | 5559128 | 0
2565 | 1492.8 | 0 | 0 | 0 | 0 | 1871.55 | 0 | 0 | 0 | 5072534.4 | 0
2566 | 1684 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1857.7 | 602042.7781 | 111351.8261 | 50510.4255 | 4671194.4863 | 43525.8702
2567 | 1725.6 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1835.65 | 1154107.0196 | 215514.4963 | 97759.7701 | 3829371.4159 | 97295.2
2568 | 1603.2 | 0 | 0 | 0 | 0 | 1816.15 | 0 | 0 | 0 | 2938665.6 | 0
2569 | 792 | 0 | 0 | 0 | 0 | 1746.8 | 0 | 0 | 0 | 942480 | 0
2570 | 863.2 | 0 | 0 | 0 | 0 | 1749 | 0 | 0 | 0 | 1027208 | 0
2571 | 843.2 | 0 | 0 | 0 | 0 | 1682.05 | 0 | 0 | 0 | 1003408 | 0
2572 | 594.4 | 0 | 0 | 0 | 0 | 1680.1 | 0 | 0 | 0 | 707336 | 0
2573 | 836 | 0 | 0 | 0 | 0 | 1698.4 | 0 | 0 | 0 | 994840 | 0
2574 | 635.2 | 0 | 0 | 0 | 0 | 1748.8 | 0 | 0 | 0 | 755888 | 0
2575 | 612.699 | 132.7156 | 132.7156 | 129.1934 | 129.1934 | 1792.15 | 244197.8518 | 46509.6301 | 21097.285 | 886265.7338 | 26284.9188
2576 | 532.414 | 528.7942 | 528.7942 | 514.7603 | 514.7603 | 1713.5 | 932193.6606 | 185313.7072 | 84060.3566 | 32359.236 | 144359.328
2577 | 903.735 | 1551.1131 | 938.8042 | 1509.9474 | 903.735 | 1775.45 | 1691012.6177 | 325344.6 | 147579.9255 | 0 | 202933.6942
2578 | 888.082 | 1671.3745 | 922.5438 | 1627.0171 | 888.082 | 1772.65 | 1665207.2176 | 319709.52 | 145023.7906 | 0 | 201905.4427
2579 | 1104.242 | 3799.7151 | 1147.0918 | 3698.8727 | 1104.242 | 1768.1 | 2063521.1839 | 397527.12 | 180322.7186 | 0 | 256073.7198
2580 | 873.013 | 4034.2938 | 906.89 | 3927.2259 | 873.013 | 1719.95 | 1582726.0411 | 314284.68 | 142563.0229 | 0 | 244487.2906
2581 | 777.272 | 4010.6859 | 807.4338 | 3904.2445 | 777.272 | 1706 | 1395064.5633 | 279817.92 | 126928.5176 | 0 | 228517.968
2582 | 991.14 | 3739.186 | 1029.6009 | 3639.95 | 991.14 | 1732.4 | 1807321.0472 | 356810.4 | 161853.162 | 0 | 265229.064
2583 | 976.907 | 3171.1167 | 1014.8156 | 3086.957 | 976.907 | 1795.95 | 1850414.6726 | 351686.52 | 159528.9131 | 0 | 199337.8733
2584 | 874.205 | 2326.8104 | 908.1283 | 2265.0582 | 874.205 | 1847.45 | 1698533.0358 | 314713.8 | 142757.6765 | 0 | 133359.9727
2585 | 861.226 | 1232.5304 | 894.6457 | 1199.8197 | 861.226 | 1898.3 | 1715180.6309 | 310041.36 | 140638.2058 | 0 | 87586.6842
2586 | 364.693 | 222.9576 | 222.9576 | 217.0405 | 217.0405 | 1893.5 | 431847.7226 | 78134.5622 | 35442.7056 | 270647.1232 | 22625.8185
2587 | 407.546 | 0 | 0 | 0 | 0 | 1894.45 | 0 | 0 | 0 | 1384841.308 | 0
2588 | 380.8 | 0 | 0 | 0 | 0 | 1848 | 0 | 0 | 0 | 1293958.4 | 0
2589 | 503.2 | 0 | 0 | 0 | 0 | 1814.65 | 0 | 0 | 0 | 1709873.6 | 0
2590 | 686.4 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1857.7 | 601522.8861 | 111351.8261 | 50510.4255 | 1281349.6863 | 43525.8702
2591 | 699.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1829.75 | 1148914.3949 | 215514.4963 | 97759.7701 | 341664.2159 | 100788
2592 | 0 | 0 | 0 | 0 | 0 | 1759.25 | 0 | 0 | 0 | 0 | 0
2593 | 0 | 0 | 0 | 0 | 0 | 1730.8 | 0 | 0 | 0 | 0 | 0
2594 | 0 | 0 | 0 | 0 | 0 | 1731.5 | 0 | 0 | 0 | 0 | 0
2595 | 0 | 0 | 0 | 0 | 0 | 1676.25 | 0 | 0 | 0 | 0 | 0
2596 | 0 | 0 | 0 | 0 | 0 | 1639.1 | 0 | 0 | 0 | 0 | 0
2597 | 0 | 0 | 0 | 0 | 0 | 1632.9 | 0 | 0 | 0 | 0 | 0
2598 | 0 | 0 | 0 | 0 | 0 | 1641.7 | 0 | 0 | 0 | 0 | 0
2599 | 1576.944 | 417.3751 | 417.3751 | 406.2982 | 406.2982 | 1605.55 | 686887.1689 | 146267.3587 | 66348.4991 | 2145793.7172 | 156873.9484
2600 | 1498.248 | 1518.4375 | 1518.4375 | 1478.139 | 1478.139 | 1403.7 | 2186286.2586 | 532130.0463 | 241380.1016 | 36859.765 | 862769.1773
2601 | 1510.044 | 1932.181 | 1568.6409 | 1880.902 | 1510.044 | 1445.25 | 2298224.6857 | 543615.84 | 246590.1852 | 0 | 837696.909
2602 | 1902.362 | 2885.9388 | 1976.1827 | 2809.3475 | 1902.362 | 1459.95 | 2930864.2639 | 684850.32 | 310655.7146 | 0 | 1027370.5981
2603 | 1884.636 | 3870.6187 | 1957.7688 | 3767.8946 | 1884.636 | 1462.3 | 2907352.0789 | 678468.96 | 307761.0588 | 0 | 1013368.7772
2604 | 1594.663 | 4116.5755 | 1656.5435 | 4007.3238 | 1594.663 | 1451.75 | 2438173.4388 | 574078.68 | 260408.4679 | 0 | 874273.9898
2605 | 1945.081 | 4093.3696 | 2020.5594 | 3984.7338 | 1945.081 | 1441.3 | 2952022.5963 | 700229.16 | 317631.7273 | 0 | 1086716.7547
2606 | 1916.271 | 3735.7143 | 1990.6314 | 3636.5705 | 1916.271 | 1464.2 | 2960456.9534 | 689857.56 | 312927.0543 | 0 | 1026738.0018
2607 | 2098.686 | 3156.5028 | 2180.125 | 3072.7309 | 2098.686 | 1483.25 | 3292503.9614 | 755526.96 | 342715.4238 | 0 | 1084495.9905
2608 | 1693.969 | 2013.2379 | 1759.703 | 1959.8076 | 1693.969 | 1489.65 | 2665085.8143 | 609828.84 | 276625.1377 | 0 | 864517.0791
2609 | 2117.631 | 818.6571 | 818.6571 | 796.9304 | 796.9304 | 1622.35 | 1360374.3174 | 286894.9361 | 130138.7307 | 2420844.2402 | 294594.5685
2610 | 2089.833 | 163.8351 | 163.8351 | 159.487 | 159.487 | 1708.35 | 286999.1169 | 57415.3189 | 26044.2266 | 3538324.2237 | 45530.6481
2611 | 1694.447 | 0 | 0 | 0 | 0 | 1734.45 | 0 | 0 | 0 | 5757730.906 | 0
2612 | 1517.6 | 0 | 0 | 0 | 0 | 1753.4 | 0 | 0 | 0 | 5156804.8 | 0
2613 | 1688.8 | 0 | 0 | 0 | 0 | 1766.55 | 0 | 0 | 0 | 5738542.4 | 0
2614 | 1653.6 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1857.7 | 604229.6246 | 111351.8261 | 50510.4255 | 4567895.2863 | 43525.8702
2615 | 1461.6 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1829.75 | 1153502.6739 | 215514.4963 | 97759.7701 | 2932299.4159 | 100788
2616 | 0 | 0 | 0 | 0 | 0 | 1776.75 | 0 | 0 | 0 | 0 | 0
2617 | 0 | 0 | 0 | 0 | 0 | 1763.8 | 0 | 0 | 0 | 0 | 0
2618 | 0 | 0 | 0 | 0 | 0 | 1686.4 | 0 | 0 | 0 | 0 | 0
2619 | 0 | 0 | 0 | 0 | 0 | 1682.05 | 0 | 0 | 0 | 0 | 0
2620 | 0 | 0 | 0 | 0 | 0 | 1680.1 | 0 | 0 | 0 | 0 | 0
2621 | 0 | 0 | 0 | 0 | 0 | 1680.9 | 0 | 0 | 0 | 0 | 0
2622 | 0 | 0 | 0 | 0 | 0 | 1703.7 | 0 | 0 | 0 | 0 | 0
2623 | 601.179 | 429.9 | 429.9 | 418.4907 | 418.4907 | 1786.75 | 786970.5487 | 150656.6464 | 68339.5288 | 334867.6826 | 87355.5167
2624 | 322.859 | 912.4123 | 335.3875 | 888.1974 | 322.859 | 1761.5 | 600808.8509 | 116229.24 | 52722.8747 | 0 | 77001.8715
2625 | 345.786 | 2138.256 | 359.2052 | 2081.5078 | 345.786 | 1848.15 | 672912.7295 | 124482.96 | 56466.8538 | 0 | 52507.6041
2626 | 329.02 | 3315.1812 | 341.7875 | 3227.1981 | 329.02 | 1835.25 | 637109.72 | 118447.2 | 53728.966 | 0 | 54206.045
2627 | 281.969 | 3801.3772 | 292.9107 | 3700.4907 | 281.969 | 1751.6 | 520877.4697 | 101508.84 | 46045.5377 | 0 | 70041.0996
2628 | 315.114 | 4047.1095 | 327.3419 | 3939.7015 | 315.114 | 1711.45 | 567710.6448 | 113441.04 | 51458.1162 | 0 | 90926.1447
2629 | 313.792 | 4029.989 | 325.9686 | 3923.0353 | 313.792 | 1721 | 568312.439 | 112965.12 | 51242.2336 | 0 | 87547.968
2630 | 298.368 | 3623.3427 | 309.9461 | 3527.1811 | 298.368 | 1776.9 | 558514.6676 | 107412.48 | 48723.4944 | 0 | 66565.9008
2631 | 287.073 | 3073.5594 | 298.2128 | 2991.9888 | 287.073 | 1858.55 | 562371.6746 | 103346.28 | 46879.0209 | 0 | 40606.4759
2632 | 258.151 | 2263.9264 | 268.1685 | 2203.843 | 258.151 | 1864.95 | 506445.8254 | 92934.36 | 42156.0583 | 0 | 34863.2925
2633 | 315.607 | 1197.5912 | 327.8541 | 1165.8078 | 315.607 | 1892.9 | 626452.5354 | 113618.52 | 51538.6231 | 0 | 33801.5097
2634 | 311.492 | 209.9591 | 209.9591 | 204.3869 | 204.3869 | 1881.7 | 403745.9473 | 73579.2701 | 33376.3745 | 196323.7189 | 23667.4529
2635 | 272.738 | 0 | 0 | 0 | 0 | 1855.05 | 0 | 0 | 0 | 499928.754 | 0
2636 | 274.4 | 149.0415 | 149.0415 | 145.086 | 145.086 | 1874.2 | 285383.3592 | 52230.9575 | 23692.5427 | 237032.5748 | 18049.0292
2637 | 260.8 | 270.9203 | 270.9203 | 263.7302 | 260.8 | 1865.65 | 509990.7714 | 93888 | 42588.64 | 0 | 35038.48
2638 | 225.6 | 234.3544 | 234.3544 | 228.1347 | 225.6 | 1857.7 | 439618.5489 | 81216 | 36840.48 | 0 | 32102.88
2639 | 268 | 278.3997 | 278.3997 | 271.0111 | 268 | 1835.65 | 516504.6968 | 96480 | 43764.4 | 0 | 44045.8
2640 | 0 | 0 | 0 | 0 | 0 | 1816.15 | 0 | 0 | 0 | 0 | 0
2641 | 0 | 0 | 0 | 0 | 0 | 1792.3 | 0 | 0 | 0 | 0 | 0
2642 | 0 | 0 | 0 | 0 | 0 | 1784.7 | 0 | 0 | 0 | 0 | 0
2643 | 0 | 0 | 0 | 0 | 0 | 1781.1 | 0 | 0 | 0 | 0 | 0
2644 | 0 | 0 | 0 | 0 | 0 | 1778.9 | 0 | 0 | 0 | 0 | 0
2645 | 0 | 0 | 0 | 0 | 0 | 1777.9 | 0 | 0 | 0 | 0 | 0
2646 | 0 | 0 | 0 | 0 | 0 | 1779.65 | 0 | 0 | 0 | 0 | 0
2647 | 39.491 | 41.0234 | 41.0234 | 39.9347 | 39.491 | 1756.3 | 72844.0543 | 14216.76 | 6448.8803 | 0 | 9623.9567
2648 | 37.99 | 824.1046 | 39.4642 | 802.2333 | 37.99 | 1708.65 | 68367.9585 | 13676.4 | 6203.767 | 0 | 11068.3865
2649 | 302.112 | 2367.0288 | 313.8354 | 2304.2092 | 302.112 | 1740.35 | 553462.457 | 108760.32 | 49334.8896 | 0 | 78443.3808
2650 | 565.025 | 3151.4105 | 586.9507 | 3067.7738 | 565.025 | 1754.35 | 1045620.7091 | 203409 | 92268.5825 | 0 | 138798.3913
2651 | 324.56 | 1942.6542 | 337.1545 | 1891.0972 | 324.56 | 1738.35 | 596794.2237 | 116841.6 | 53000.648 | 0 | 84921.124
2652 | 314.692 | 3928.8125 | 326.9035 | 3824.544 | 314.692 | 1710.35 | 567804.0011 | 113289.12 | 51389.2036 | 0 | 91150.5378
2653 | 593.521 | 1801.0558 | 616.5524 | 1753.2567 | 593.521 | 1700.85 | 1061541.0084 | 213667.56 | 96921.9793 | 0 | 177551.8072
2654 | 606.677 | 3590.5081 | 630.2189 | 3495.218 | 606.677 | 1740.75 | 1112839.8187 | 218403.72 | 99070.3541 | 0 | 157281.0122
2655 | 413.157 | 1631.2112 | 429.1895 | 1587.9197 | 413.157 | 1783.6 | 777216.8599 | 148736.52 | 67468.5381 | 0 | 89407.1748
2656 | 615.896 | 2210.8134 | 639.7957 | 2152.1396 | 615.896 | 1788.3 | 1157823.0759 | 221722.56 | 100575.8168 | 0 | 130385.1832
2657 | 592.271 | 1164.3183 | 615.2539 | 1133.418 | 592.271 | 1882 | 1171280.3461 | 213217.56 | 96717.8543 | 0 | 69887.978
2658 | 583.145 | 196.8535 | 196.8535 | 191.6291 | 191.6291 | 1864.6 | 375425.7929 | 68986.4815 | 31293.0345 | 717648.6168 | 25397.655
2659 | 752.979 | 0 | 0 | 0 | 0 | 1829.6 | 0 | 0 | 0 | 2558622.642 | 0
2660 | 606.4 | 0 | 0 | 0 | 0 | 1858.1 | 0 | 0 | 0 | 2060547.2 | 0
2661 | 505.6 | 0 | 0 | 0 | 0 | 1848.2 | 0 | 0 | 0 | 1718028.8 | 0
2662 | 594.4 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1842.65 | 598385.8033 | 111351.8261 | 50510.4255 | 968733.6863 | 48129.2739
2663 | 668.8 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1827.2 | 1151456.9048 | 215514.4963 | 97759.7701 | 238365.0159 | 102297.6
2664 | 0 | 0 | 0 | 0 | 0 | 1809.75 | 0 | 0 | 0 | 0 | 0
2665 | 0 | 0 | 0 | 0 | 0 | 1778.3 | 0 | 0 | 0 | 0 | 0
2666 | 0 | 0 | 0 | 0 | 0 | 1768.7 | 0 | 0 | 0 | 0 | 0
2667 | 0 | 0 | 0 | 0 | 0 | 1764.35 | 0 | 0 | 0 | 0 | 0
2668 | 0 | 0 | 0 | 0 | 0 | 1762.1 | 0 | 0 | 0 | 0 | 0
2669 | 0 | 0 | 0 | 0 | 0 | 1705.6 | 0 | 0 | 0 | 0 | 0
2670 | 0 | 0 | 0 | 0 | 0 | 1714.7 | 0 | 0 | 0 | 0 | 0
2671 | 1652.413 | 430.2023 | 430.2023 | 418.785 | 418.785 | 1703.15 | 749509.7681 | 150762.5834 | 68387.583 | 2261240.2086 | 121686.5331
2672 | 1082.942 | 1124.9653 | 1124.9653 | 1095.1093 | 1082.942 | 1670.75 | 1909284.6175 | 389859.12 | 176844.4286 | 0 | 356558.6535
2673 | 1038.061 | 1947.227 | 1078.3427 | 1895.5487 | 1038.061 | 1609.9 | 1762750.8284 | 373701.96 | 169515.3613 | 0 | 404947.5961
2674 | 1455.5 | 3289.6484 | 1511.9813 | 3202.343 | 1455.5 | 1612.9 | 2475973.0795 | 523980 | 237683.15 | 0 | 563424.05
2675 | 1822.657 | 3743.3256 | 1893.3847 | 3643.9798 | 1822.657 | 1648.4 | 3165750.8704 | 656156.52 | 297639.8881 | 0 | 640846.2012
2676 | 1569.698 | 3977.815 | 1630.6097 | 3872.246 | 1569.698 | 1661.9 | 2757899.258 | 565091.28 | 256331.6834 | 0 | 530714.8938
2677 | 1627.187 | 3961.3157 | 1690.3296 | 3856.1845 | 1627.187 | 1632.15 | 2805603.5263 | 585787.32 | 265719.6371 | 0 | 598560.7379
2678 | 1849.064 | 3670.843 | 1920.8165 | 3573.4209 | 1849.064 | 1623.8 | 3174277.1958 | 665663.04 | 301952.1512 | 0 | 695617.8768
2679 | 1544.646 | 3110.385 | 1604.5856 | 3027.8371 | 1544.646 | 1577.9 | 2571962.8929 | 556072.56 | 252240.6918 | 0 | 651995.0766
2680 | 1277.5 | 2291.8702 | 1327.0731 | 2231.0453 | 1277.5 | 1553.15 | 2090190.0305 | 459900 | 208615.75 | 0 | 570850.875
2681 | 1415.472 | 1204.4806 | 1204.4806 | 1172.5143 | 1172.5143 | 1592.7 | 1964085.9359 | 422105.1634 | 191471.5922 | 445341.3858 | 467463.0976
2682 | 1528.819 | 161.5466 | 161.5466 | 157.2592 | 157.2592 | 1695.2 | 279522.8547 | 56613.3283 | 25680.4347 | 2514069.0305 | 46918.7784
2683 | 1597.596 | 0 | 0 | 0 | 0 | 1765.45 | 0 | 0 | 0 | 5428631.208 | 0
2684 | 1565.6 | 0 | 0 | 0 | 0 | 1787.25 | 0 | 0 | 0 | 5319908.8 | 0
2685 | 1574.4 | 0 | 0 | 0 | 0 | 1771.75 | 0 | 0 | 0 | 5349811.2 | 0
2686 | 2055.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1809.65 | 587420.0916 | 111351.8261 | 50510.4255 | 5932532.0863 | 58223.1159
2687 | 2027.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1800.1 | 1131408.3479 | 215514.4963 | 97759.7701 | 4854208.2159 | 118340.8
2688 | 0 | 0 | 0 | 0 | 0 | 1789.85 | 0 | 0 | 0 | 0 | 0
2689 | 0 | 0 | 0 | 0 | 0 | 1791.9 | 0 | 0 | 0 | 0 | 0
2690 | 0 | 0 | 0 | 0 | 0 | 1776.6 | 0 | 0 | 0 | 0 | 0
2691 | 0 | 0 | 0 | 0 | 0 | 1682.05 | 0 | 0 | 0 | 0 | 0
2692 | 0 | 0 | 0 | 0 | 0 | 1680.1 | 0 | 0 | 0 | 0 | 0
2693 | 0 | 0 | 0 | 0 | 0 | 1680.9 | 0 | 0 | 0 | 0 | 0
2694 | 0 | 0 | 0 | 0 | 0 | 1703.7 | 0 | 0 | 0 | 0 | 0
2695 | 1539.86 | 315.6834 | 315.6834 | 307.3053 | 307.3053 | 1696.55 | 548113.8737 | 110629.9253 | 50182.9633 | 2259272.677 | 91279.2772
2696 | 753.773 | 924.8614 | 783.023 | 900.3161 | 753.773 | 1693 | 1340459.4146 | 271358.28 | 123091.1309 | 0 | 231408.311
2697 | 1086.631 | 2125.6355 | 1128.7985 | 2069.2223 | 1086.631 | 1747.85 | 1992110.1491 | 391187.16 | 177446.8423 | 0 | 273994.0066
2698 | 1522.957 | 3286.7169 | 1582.055 | 3199.4893 | 1522.957 | 1769.75 | 2833764.8299 | 548264.52 | 248698.8781 | 0 | 350660.8493
2699 | 1186.075 | 3775.5982 | 1232.1003 | 3675.3959 | 1186.075 | 1769.2 | 2209947.5927 | 426987 | 193686.0475 | 0 | 273746.11
2700 | 1273.679 | 4001.1933 | 1323.1038 | 3895.0038 | 1273.679 | 1751.35 | 2339870.9669 | 458524.44 | 207991.7807 | 0 | 316700.2834
2701 | 1087.344 | 3997.0423 | 1129.5381 | 3890.9629 | 1087.344 | 1713 | 1952426.5694 | 391443.84 | 177563.2752 | 0 | 312067.728
2702 | 1231.626 | 3710.9762 | 1279.4189 | 3612.4889 | 1231.626 | 1753.5 | 2271633.1045 | 443385.36 | 201124.5258 | 0 | 303595.809
2703 | 1034.934 | 3166.7464 | 1075.0944 | 3082.7027 | 1034.934 | 1793.05 | 1951300.1453 | 372576.24 | 169004.7222 | 0 | 214179.5913
2704 | 806.512 | 2350.437 | 837.8085 | 2288.0577 | 806.512 | 1847.45 | 1564001.627 | 290344.32 | 131703.4096 | 0 | 123033.4056
2705 | 1209.862 | 849.3455 | 849.3455 | 826.8043 | 826.8043 | 1865.3 | 1617016.9446 | 297649.5463 | 135017.1414 | 702144.7729 | 109014.5958
2706 | 1026.622 | 193.092 | 193.092 | 187.9674 | 187.9674 | 1881.7 | 371211.2883 | 67668.2754 | 30695.0816 | 1537253.8237 | 21766.1353
2707 | 1116.444 | 0 | 0 | 0 | 0 | 1882.65 | 0 | 0 | 0 | 3793676.712 | 0
2708 | 1189.6 | 0 | 0 | 0 | 0 | 1874.2 | 0 | 0 | 0 | 4042260.8 | 0
2709 | 1585.6 | 0 | 0 | 0 | 0 | 1859.75 | 0 | 0 | 0 | 5387868.8 | 0
2710 | 1313.6 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1857.7 | 603177.5684 | 111351.8261 | 50510.4255 | 3412575.2863 | 43525.8702
2711 | 1244.8 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1835.65 | 1156086.5487 | 215514.4963 | 97759.7701 | 2195613.0159 | 97295.2
2712 | 0 | 0 | 0 | 0 | 0 | 1816.15 | 0 | 0 | 0 | 0 | 0
2713 | 0 | 0 | 0 | 0 | 0 | 1797.8 | 0 | 0 | 0 | 0 | 0
2714 | 0 | 0 | 0 | 0 | 0 | 1788.4 | 0 | 0 | 0 | 0 | 0
2715 | 0 | 0 | 0 | 0 | 0 | 1772.25 | 0 | 0 | 0 | 0 | 0
2716 | 0 | 0 | 0 | 0 | 0 | 1770.3 | 0 | 0 | 0 | 0 | 0
2717 | 0 | 0 | 0 | 0 | 0 | 1771.1 | 0 | 0 | 0 | 0 | 0
2718 | 0 | 0 | 0 | 0 | 0 | 1776.4 | 0 | 0 | 0 | 0 | 0
2719 | 726.714 | 445.9329 | 445.9329 | 434.0981 | 434.0981 | 1786.75 | 815355.8625 | 156275.3131 | 70888.2184 | 536364.9593 | 90613.337
2720 | 674.256 | 100.0888 | 100.0888 | 97.4325 | 97.4325 | 1689.5 | 172930.9892 | 35075.7124 | 15910.7329 | 1057317.4126 | 29612.6955
2721 | 632.529 | 2017.3786 | 657.0741 | 1963.8384 | 632.529 | 1765.35 | 1173302.055 | 227710.44 | 103291.9857 | 0 | 148422.9298
2722 | 561.581 | 2978.9191 | 583.373 | 2899.8602 | 561.581 | 1769.75 | 1045696.084 | 202169.16 | 91706.1773 | 0 | 129304.0252
2723 | 451.698 | 3845.3124 | 469.226 | 3743.2599 | 451.698 | 1730.5 | 822824.6947 | 162611.28 | 73762.2834 | 0 | 121732.611
2724 | 423.123 | 4082.9369 | 439.5422 | 3974.578 | 423.123 | 1661.3 | 738051.712 | 152324.28 | 69095.9859 | 0 | 143311.7601
2725 | 1088.675 | 4050.2675 | 1130.9208 | 3942.7756 | 1088.675 | 1650.85 | 1883859.0231 | 391923 | 177780.6275 | 0 | 380110.8763
2726 | 1337.162 | 3765.2309 | 1389.0502 | 3665.3037 | 1337.162 | 1732.9 | 2435641.9291 | 481378.32 | 218358.5546 | 0 | 357155.9702
2727 | 1171.09 | 3188.5156 | 1216.5339 | 3103.8941 | 1171.09 | 1795.95 | 2211346.2207 | 421592.4 | 191238.997 | 0 | 238960.9145
2728 | 1325.832 | 2348.2722 | 1377.2806 | 2285.9503 | 1325.832 | 1837.35 | 2559115.0396 | 477299.52 | 216508.3656 | 0 | 215646.5748
2729 | 1450.922 | 1239.1549 | 1239.1549 | 1206.2684 | 1206.2684 | 1865.3 | 2361713.8407 | 434256.6133 | 196983.6249 | 448450.1032 | 159047.1597
2730 | 1693.945 | 211.4082 | 211.4082 | 205.7975 | 205.7975 | 1887.6 | 407775.1639 | 74087.1126 | 33606.7375 | 2727774.3035 | 22642.3056
2731 | 1224.801 | 0 | 0 | 0 | 0 | 1888.55 | 0 | 0 | 0 | 4161873.798 | 0
2732 | 1521.6 | 0 | 0 | 0 | 0 | 1880.1 | 0 | 0 | 0 | 5170396.8 | 0
2733 | 1564 | 0 | 0 | 0 | 0 | 1865.65 | 0 | 0 | 0 | 5314472 | 0
2734 | 1750.4 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1857.7 | 602787.513 | 111351.8261 | 50510.4255 | 4896821.6863 | 43525.8702
2735 | 1775.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1835.65 | 1154025.6839 | 215514.4963 | 97759.7701 | 3997912.2159 | 97295.2
2736 | 0 | 0 | 0 | 0 | 0 | 1816.15 | 0 | 0 | 0 | 0 | 0
2737 | 0 | 0 | 0 | 0 | 0 | 1797.8 | 0 | 0 | 0 | 0 | 0
2738 | 0 | 0 | 0 | 0 | 0 | 1776.6 | 0 | 0 | 0 | 0 | 0
2739 | 0 | 0 | 0 | 0 | 0 | 1682.05 | 0 | 0 | 0 | 0 | 0
2740 | 0 | 0 | 0 | 0 | 0 | 1680.1 | 0 | 0 | 0 | 0 | 0
2741 | 0 | 0 | 0 | 0 | 0 | 1680.9 | 0 | 0 | 0 | 0 | 0
2742 | 0 | 0 | 0 | 0 | 0 | 1703.7 | 0 | 0 | 0 | 0 | 0
2743 | 1263.257 | 444.839 | 444.839 | 433.0333 | 433.0333 | 1731.55 | 788697.531 | 155891.974 | 70714.3315 | 1521800.1133 | 113788.7069
2744 | 953.993 | 991.0125 | 991.0125 | 964.7115 | 953.993 | 1716.4 | 1724227.4067 | 343437.48 | 155787.0569 | 0 | 270552.4148
2745 | 1386.66 | 1989.3745 | 1440.47 | 1936.5775 | 1386.66 | 1757.95 | 2569435.9467 | 499197.6 | 226441.578 | 0 | 335641.053
2746 | 1396.16 | 3249.3885 | 1450.3376 | 3163.1515 | 1396.16 | 1766.85 | 2605469.8698 | 502617.6 | 227992.928 | 0 | 325514.704
2747 | 1632.597 | 3789.0642 | 1695.9495 | 3688.5045 | 1632.597 | 1670.1 | 2875615.325 | 587734.92 | 266603.0901 | 0 | 538593.7503
2748 | 1604.417 | 4039.3029 | 1666.676 | 3932.102 | 1604.417 | 1521.6 | 2569672.0692 | 577590.12 | 262001.2961 | 0 | 767553.0928
2749 | 1737.845 | 4024.5425 | 1805.2816 | 3917.7334 | 1737.845 | 1441.3 | 2631607.2893 | 625624.2 | 283790.0885 | 0 | 970934.0015
2750 | 1592.395 | 3690.0817 | 1654.1875 | 3592.1489 | 1592.395 | 1697.25 | 2850189.6409 | 573262.2 | 260038.1035 | 0 | 482097.5863
2751 | 1657.388 | 3132.6871 | 1721.7025 | 3049.5473 | 1657.388 | 1790.15 | 3131051.5473 | 596659.68 | 270651.4604 | 0 | 347802.8718
2752 | 1478.101 | 2300.3749 | 1535.4583 | 2239.3242 | 1478.101 | 1792.25 | 2786632.819 | 532116.36 | 241373.8933 | 0 | 307075.4828
2753 | 1658.613 | 977.9921 | 977.9921 | 952.0367 | 952.0367 | 1865.3 | 1864725.68 | 342733.2131 | 155467.5936 | 1295154.3525 | 125526.6606
2754 | 1608.759 | 192.5954 | 192.5954 | 187.4841 | 187.4841 | 1887.6 | 371798.135 | 67494.262 | 30616.1472 | 2605196.9628 | 20627.4232
2755 | 1122.711 | 0 | 0 | 0 | 0 | 1882.65 | 0 | 0 | 0 | 3814971.978 | 0
2756 | 1280.8 | 0 | 0 | 0 | 0 | 1880.1 | 0 | 0 | 0 | 4352158.4 | 0
2757 | 1492 | 0 | 0 | 0 | 0 | 1865.65 | 0 | 0 | 0 | 5069816 | 0
2758 | 1771.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1857.7 | 605877.5271 | 111351.8261 | 50510.4255 | 4967500.0863 | 43525.8702
2759 | 1771.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1835.65 | 1158586.6121 | 215514.4963 | 97759.7701 | 3984320.2159 | 97295.2
2760 | 0 | 0 | 0 | 0 | 0 | 1816.15 | 0 | 0 | 0 | 0 | 0
2761 | 0 | 0 | 0 | 0 | 0 | 1797.8 | 0 | 0 | 0 | 0 | 0
2762 | 0 | 0 | 0 | 0 | 0 | 1776.6 | 0 | 0 | 0 | 0 | 0
2763 | 0 | 0 | 0 | 0 | 0 | 1772.25 | 0 | 0 | 0 | 0 | 0
2764 | 0 | 0 | 0 | 0 | 0 | 1715.1 | 0 | 0 | 0 | 0 | 0
2765 | 0 | 0 | 0 | 0 | 0 | 1698.4 | 0 | 0 | 0 | 0 | 0
2766 | 0 | 0 | 0 | 0 | 0 | 1748.8 | 0 | 0 | 0 | 0 | 0
2767 | 1162.556 | 390.2883 | 390.2883 | 379.9303 | 379.9303 | 1741.65 | 696339.122 | 136774.8917 | 62042.6106 | 1434552.9912 | 96078.8149
2768 | 970.887 | 1008.562 | 1008.562 | 981.7953 | 970.887 | 1716.4 | 1756176.3682 | 349519.32 | 158545.8471 | 0 | 275343.5532
2769 | 1196.422 | 1738.0429 | 1242.8489 | 1691.9162 | 1196.422 | 1775.45 | 2233741.8679 | 430711.92 | 195375.7126 | 0 | 268656.5601
2770 | 1332.16 | 3067.2559 | 1383.8541 | 2985.8526 | 1332.16 | 1769.75 | 2484368.1817 | 479577.6 | 217541.728 | 0 | 306729.84
2771 | 1301.099 | 3669.6256 | 1351.5878 | 3572.2357 | 1301.099 | 1727 | 2370070.6577 | 468395.64 | 212469.4667 | 0 | 355200.027
2772 | 1262.025 | 3904.3934 | 1310.9976 | 3800.7729 | 1262.025 | 1716.45 | 2280708.1882 | 454329 | 206088.6825 | 0 | 357847.1887
2773 | 1431.18 | 3895.4981 | 1486.7166 | 3792.1137 | 1431.18 | 1670.85 | 2517869.837 | 515224.8 | 233711.694 | 0 | 471072.897
2774 | 1472.893 | 3014.9926 | 1530.0482 | 2934.9764 | 1472.893 | 1763.9 | 2735790.6332 | 530241.48 | 240523.4269 | 0 | 347750.0373
2775 | 1483.656 | 2309.8312 | 1541.2289 | 2248.5295 | 1483.656 | 1790.15 | 2794965.7739 | 534116.16 | 242281.0248 | 0 | 311345.2116
2776 | 1473.083 | 1456.2038 | 1456.2038 | 1417.5569 | 1417.5569 | 1819.85 | 2709667.32 | 510320.4889 | 231487.044 | 101779.3162 | 249970.9157
2777 | 1294.28 | 420.6567 | 420.6567 | 409.4927 | 409.4927 | 1847.8 | 795108.6726 | 147417.3761 | 66870.1598 | 1621815.1 | 61006.4782
2778 | 1058.51 | 82.8374 | 82.8374 | 80.6389 | 80.6389 | 1842.5 | 156194.8971 | 29030.0211 | 13168.3401 | 1792437.6394 | 12431.9475
2779 | 1464.006 | 0 | 0 | 0 | 0 | 1882.65 | 0 | 0 | 0 | 4974692.388 | 0
2780 | 1241.6 | 0 | 0 | 0 | 0 | 1874.2 | 0 | 0 | 0 | 4218956.8 | 0
2781 | 1408.8 | 0 | 0 | 0 | 0 | 1865.65 | 0 | 0 | 0 | 4787102.4 | 0
2782 | 1203.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1857.7 | 604488.3907 | 111351.8261 | 50510.4255 | 3037436.0863 | 43525.8702
2783 | 1300 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1835.65 | 1157413.1857 | 215514.4963 | 97759.7701 | 2383182.6159 | 97295.2
2784 | 0 | 0 | 0 | 0 | 0 | 1816.15 | 0 | 0 | 0 | 0 | 0
2785 | 0 | 0 | 0 | 0 | 0 | 1797.8 | 0 | 0 | 0 | 0 | 0
2786 | 0 | 0 | 0 | 0 | 0 | 1788.4 | 0 | 0 | 0 | 0 | 0
2787 | 0 | 0 | 0 | 0 | 0 | 1772.25 | 0 | 0 | 0 | 0 | 0
2788 | 0 | 0 | 0 | 0 | 0 | 1770.3 | 0 | 0 | 0 | 0 | 0
2789 | 0 | 0 | 0 | 0 | 0 | 1771.1 | 0 | 0 | 0 | 0 | 0
2790 | 0 | 0 | 0 | 0 | 0 | 1776.4 | 0 | 0 | 0 | 0 | 0
2791 | 1083.813 | 457.2767 | 457.2767 | 445.1408 | 445.1408 | 1759.15 | 823044.9421 | 160250.6819 | 72691.4899 | 1170686.1737 | 104944.1254
2792 | 1008.77 | 1047.9151 | 1047.9151 | 1020.104 | 1008.77 | 1713.5 | 1821103.2704 | 363157.2 | 164732.141 | 0 | 289012.605
2793 | 934.389 | 2066.1099 | 970.6477 | 2011.2765 | 934.389 | 1775.45 | 1744476.023 | 336380.04 | 152585.7237 | 0 | 209817.0499
2794 | 1123.825 | 3318.0442 | 1167.4347 | 3229.9851 | 1123.825 | 1769.75 | 2093237.2215 | 404577 | 183520.6225 | 0 | 258760.7062
2795 | 930.985 | 3819.8648 | 967.1116 | 3718.4876 | 930.985 | 1727 | 1692040.4563 | 335154.6 | 152029.8505 | 0 | 254158.905
2796 | 972.383 | 4048.3104 | 1010.1161 | 3940.8705 | 972.383 | 1716.45 | 1754164.7972 | 350057.88 | 158790.1439 | 0 | 275719.1996
2797 | 958.182 | 4020.5681 | 995.364 | 3913.8644 | 958.182 | 1723.4 | 1733048.3209 | 344945.52 | 156471.1206 | 0 | 265033.1412
2798 | 1202.344 | 3693.275 | 1249.0007 | 3595.2575 | 1202.344 | 1822 | 2305720.7188 | 432843.84 | 196342.7752 | 0 | 214017.232
2799 | 871.996 | 3124.6738 | 905.8336 | 3041.7466 | 871.996 | 1886.15 | 1733828.7938 | 313918.56 | 142396.9468 | 0 | 99276.7446
2800 | 905.877 | 2297.6242 | 941.0293 | 2236.6465 | 905.877 | 1904.35 | 1816884.2054 | 326115.72 | 147929.7141 | 0 | 86647.1351
2801 | 1065.211 | 1203.7597 | 1106.5462 | 1171.8125 | 1065.211 | 1904.7 | 2130629.0813 | 383475.96 | 173948.9563 | 0 | 101514.6083
2802 | 1003.197 | 211.3843 | 211.3843 | 205.7743 | 205.7743 | 1887.6 | 407883.4849 | 74078.7395 | 33602.9394 | 1461675.8521 | 22639.7204
2803 | 1253.158 | 0 | 0 | 0 | 0 | 1882.65 | 0 | 0 | 0 | 2297038.614 | 0
2804 | 1226.4 | 0 | 0 | 0 | 0 | 1874.2 | 0 | 0 | 0 | 2247991.2 | 0
2805 | 1049.6 | 0 | 0 | 0 | 0 | 1865.65 | 0 | 0 | 0 | 1923916.8 | 0
2806 | 1300 | 0 | 0 | 0 | 0 | 1857.7 | 0 | 0 | 0 | 2382900 | 0
2807 | 1016.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1835.65 | 596329.2822 | 111351.8261 | 50510.4255 | 1296828.019 | 50270.3919
2808 | 0 | 0 | 0 | 0 | 0 | 1816.15 | 0 | 0 | 0 | 0 | 0
2809 | 0 | 0 | 0 | 0 | 0 | 1798.2 | 0 | 0 | 0 | 0 | 0
2810 | 0 | 0 | 0 | 0 | 0 | 1796.5 | 0 | 0 | 0 | 0 | 0
2811 | 0 | 0 | 0 | 0 | 0 | 1792.9 | 0 | 0 | 0 | 0 | 0
2812 | 0 | 0 | 0 | 0 | 0 | 1790.7 | 0 | 0 | 0 | 0 | 0
2813 | 0 | 0 | 0 | 0 | 0 | 1777.9 | 0 | 0 | 0 | 0 | 0
2814 | 0 | 0 | 0 | 0 | 0 | 1779.65 | 0 | 0 | 0 | 0 | 0
2815 | 976.828 | 923.7717 | 923.7717 | 899.2553 | 899.2553 | 1728.7 | 1631448.5582 | 323731.897 | 146848.3855 | 142190.8154 | 240438.2685
2816 | 949.208 | 986.0418 | 986.0418 | 959.8728 | 949.208 | 1702.75 | 1698665.6765 | 341714.88 | 155005.6664 | 0 | 282152.078
2817 | 1320.769 | 1808.8458 | 1372.0211 | 1760.84 | 1320.769 | 1740.25 | 2415493.7015 | 475476.84 | 215681.5777 | 0 | 343069.7478
2818 | 1344.335 | 3163.47 | 1396.5016 | 3079.5133 | 1344.335 | 1733.75 | 2454800.2061 | 483960.6 | 219529.9055 | 0 | 357929.1938
2819 | 1328.345 | 3678.177 | 1379.8911 | 3580.5602 | 1328.345 | 1710.55 | 2396261.5678 | 478204.2 | 216918.7385 | 0 | 384489.4603
2820 | 1413.067 | 3382.4116 | 1467.9007 | 3292.6443 | 1413.067 | 1703.35 | 2537188.9958 | 508704.12 | 230753.8411 | 0 | 419186.3256
2821 | 1334.168 | 2754.771 | 1385.9401 | 2681.6609 | 1334.168 | 1697.35 | 2385640.2946 | 480300.48 | 217869.6344 | 0 | 403785.9452
2822 | 1503.829 | 2724.8337 | 1562.1847 | 2652.5181 | 1503.829 | 1778.75 | 2821605.2561 | 541378.44 | 245575.2757 | 0 | 332722.1663
2823 | 1371.782 | 1325.2801 | 1325.2801 | 1290.1079 | 1290.1079 | 1874.7 | 2552281.0259 | 464438.836 | 210674.6165 | 149708.6658 | 158231.0954
2824 | 1502.032 | 756.3122 | 756.3122 | 736.2401 | 736.2401 | 1851.8 | 1437948.8814 | 265046.4259 | 120228.0038 | 1403696.6041 | 106802.7012
2825 | 1377.423 | 682.3036 | 682.3036 | 664.1956 | 664.1956 | 1887.9 | 1319916.0639 | 239110.4212 | 108463.1439 | 1307345.7976 | 72881.3666
2826 | 1514.373 | 136.9155 | 136.9155 | 133.2818 | 133.2818 | 1837 | 257456.9123 | 47981.463 | 21764.9248 | 2531540.093 | 21265.306
2827 | 1132.464 | 0 | 0 | 0 | 0 | 1858.1 | 0 | 0 | 0 | 3848112.672 | 0
2828 | 1019.2 | 0 | 0 | 0 | 0 | 1858.1 | 0 | 0 | 0 | 3463241.6 | 0
2829 | 1064.8 | 0 | 0 | 0 | 0 | 1848.2 | 0 | 0 | 0 | 3618190.4 | 0
2830 | 1386.4 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1842.65 | 597953.245 | 111351.8261 | 50510.4255 | 3659949.6863 | 48129.2739
2831 | 1148 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1827.2 | 1148892.0566 | 215514.4963 | 97759.7701 | 1866686.6159 | 102297.6
2832 | 0 | 0 | 0 | 0 | 0 | 1809.75 | 0 | 0 | 0 | 0 | 0
2833 | 0 | 0 | 0 | 0 | 0 | 1784.2 | 0 | 0 | 0 | 0 | 0
2834 | 0 | 0 | 0 | 0 | 0 | 1780.5 | 0 | 0 | 0 | 0 | 0
2835 | 0 | 0 | 0 | 0 | 0 | 1776.15 | 0 | 0 | 0 | 0 | 0
2836 | 0 | 0 | 0 | 0 | 0 | 1773.9 | 0 | 0 | 0 | 0 | 0
2837 | 0 | 0 | 0 | 0 | 0 | 1772.6 | 0 | 0 | 0 | 0 | 0
2838 | 0 | 0 | 0 | 0 | 0 | 1765.7 | 0 | 0 | 0 | 0 | 0
2839 | 989.561 | 406.02 | 406.02 | 395.2444 | 395.2444 | 1758.35 | 732715.2299 | 142287.9855 | 64543.4112 | 1089382.3203 | 93490.277
2840 | 970.741 | 1008.4104 | 1008.4104 | 981.6477 | 970.741 | 1669.65 | 1714994.057 | 349466.76 | 158522.0053 | 0 | 320684.2893
2841 | 1081.276 | 2012.1212 | 1123.2346 | 1958.7206 | 1081.276 | 1658.95 | 1895004.8831 | 389259.36 | 176572.3708 | 0 | 368769.1798
2842 | 1571.813 | 1632.8068 | 1632.8068 | 1589.473 | 1571.813 | 1652.9 | 2745320.714 | 565852.68 | 256677.0629 | 0 | 545576.2923
2843 | 1519.172 | 2778.4786 | 1578.1231 | 2704.7393 | 1519.172 | 1664.9 | 2672571.7858 | 546901.92 | 248080.7876 | 0 | 509074.5372
2844 | 1461.244 | 3525.2525 | 1517.9472 | 3431.6942 | 1461.244 | 1661.9 | 2572726.7013 | 526047.84 | 238621.1452 | 0 | 494046.5964
2845 | 1711.452 | 4014.997 | 1777.8645 | 3908.4411 | 1711.452 | 1652.15 | 2994096.2366 | 616122.72 | 279480.1116 | 0 | 595328.5782
2846 | 1173.122 | 3720.876 | 1218.6447 | 3622.126 | 1173.122 | 1663.8 | 2064099.6724 | 422323.92 | 191570.8226 | 0 | 394403.6164
2847 | 1493.09 | 198.7815 | 198.7815 | 193.506 | 193.506 | 1673.45 | 342860.4856 | 69662.1486 | 31599.5246 | 2382137.5303 | 61852.8151
2848 | 1648.072 | 718.9588 | 718.9588 | 699.8781 | 699.8781 | 1678.15 | 1241366.4465 | 251956.1045 | 114290.0885 | 1738039.4771 | 220490.745
2849 | 1134.203 | 88.2901 | 88.2901 | 85.9469 | 85.9469 | 1717.15 | 155714.8937 | 30940.892 | 14035.1324 | 1921453.3906 | 23795.8876
2850 | 1182.912 | 10.7101 | 10.7101 | 10.4258 | 10.4258 | 1757.2 | 19369.879 | 3753.3014 | 1702.5392 | 2149167.1361 | 2477.774
2851 | 1420.356 | 0 | 0 | 0 | 0 | 1839.05 | 0 | 0 | 0 | 4826369.688 | 0
2852 | 1311.2 | 0 | 0 | 0 | 0 | 1839.15 | 0 | 0 | 0 | 4455457.6 | 0
2853 | 1405.6 | 0 | 0 | 0 | 0 | 1828.65 | 0 | 0 | 0 | 4776228.8 | 0
2854 | 1212 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1821.45 | 593308.6311 | 111351.8261 | 50510.4255 | 3067338.4863 | 54613.8027
2855 | 1395.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1806 | 1138653.6362 | 215514.4963 | 97759.7701 | 2706672.2159 | 114848
2856 | 0 | 0 | 0 | 0 | 0 | 1789.85 | 0 | 0 | 0 | 0 | 0
2857 | 0 | 0 | 0 | 0 | 0 | 1797.8 | 0 | 0 | 0 | 0 | 0
2858 | 0 | 0 | 0 | 0 | 0 | 1788.4 | 0 | 0 | 0 | 0 | 0
2859 | 0 | 0 | 0 | 0 | 0 | 1784.05 | 0 | 0 | 0 | 0 | 0
2860 | 0 | 0 | 0 | 0 | 0 | 1782.1 | 0 | 0 | 0 | 0 | 0
2861 | 0 | 0 | 0 | 0 | 0 | 1782.9 | 0 | 0 | 0 | 0 | 0
2862 | 0 | 0 | 0 | 0 | 0 | 1783.2 | 0 | 0 | 0 | 0 | 0
2863 | 1384.773 | 455.0526 | 455.0526 | 442.9757 | 442.9757 | 1741.65 | 815591.3708 | 159471.2621 | 72337.9364 | 1726314.3997 | 112021.8517
2864 | 330.448 | 343.271 | 343.271 | 334.1607 | 330.448 | 1693 | 590952.7211 | 118961.28 | 53962.1584 | 0 | 101447.536
2865 | 66.072 | 1407.6573 | 68.6359 | 1370.2988 | 66.072 | 1709.95 | 119276.7749 | 23785.92 | 10789.5576 | 0 | 19164.1836
2866 | 69.845 | 1820.1127 | 72.5553 | 1771.8079 | 69.845 | 1724.65 | 127071.3621 | 25144.2 | 11405.6885 | 0 | 19231.8207
2867 | 66.865 | 1761.8752 | 69.4597 | 1715.116 | 66.865 | 1690 | 119786.8763 | 24071.4 | 10919.0545 | 0 | 20728.15
2868 | 69.874 | 778.5956 | 72.5854 | 757.9321 | 69.874 | 1716.45 | 127050.3552 | 25154.64 | 11410.4242 | 0 | 19812.7727
2869 | 62.387 | 330.9653 | 64.8079 | 322.1816 | 62.387 | 1706 | 112446.4994 | 22459.32 | 10187.7971 | 0 | 18341.778
2870 | 65.31 | 624.9023 | 67.8443 | 608.3178 | 65.31 | 1732.4 | 119102.7901 | 23511.6 | 10665.123 | 0 | 17476.956
2871 | 60.338 | 1057.1272 | 62.6794 | 1029.0716 | 60.338 | 1751.45 | 110838.9608 | 21721.68 | 9853.1954 | 0 | 14997.0099
2872 | 69.75 | 1106.5327 | 72.4566 | 1077.166 | 69.75 | 1777.85 | 130206.5036 | 25110 | 11390.175 | 0 | 15494.9625
2873 | 62.252 | 598.9997 | 64.6677 | 583.1026 | 62.252 | 1816.2 | 119031.3532 | 22410.72 | 10165.7516 | 0 | 11441.9176
2874 | 69.556 | 121.0831 | 72.2551 | 117.8696 | 69.556 | 1854.1 | 136538.2002 | 25040.16 | 11358.4948 | 0 | 10148.2204
2875 | 70.538 | 73.2752 | 73.2752 | 71.3305 | 70.538 | 1792.45 | 133344.1343 | 25393.68 | 11518.8554 | 0 | 14640.1619
2876 | 76.8 | 79.7802 | 79.7802 | 77.6629 | 76.8 | 1819 | 147148.301 | 27648 | 12541.44 | 0 | 13900.8
2877 | 72.8 | 75.625 | 75.625 | 73.6179 | 72.8 | 1833.05 | 140196.9135 | 26208 | 11888.24 | 0 | 12153.96
2878 | 78.4 | 81.4423 | 81.4423 | 79.2809 | 78.4 | 1857.7 | 152845.4171 | 28224 | 12802.72 | 0 | 11156.32
2879 | 72 | 74.7939 | 74.7939 | 72.809 | 72 | 1835.65 | 139095.7145 | 25920 | 11757.6 | 0 | 11833.2
2880 | 0 | 0 | 0 | 0 | 0 | 1816.15 | 0 | 0 | 0 | 0 | 0
2881 | 0 | 0 | 0 | 0 | 0 | 1793.3 | 0 | 0 | 0 | 0 | 0
2882 | 0 | 0 | 0 | 0 | 0 | 1788.4 | 0 | 0 | 0 | 0 | 0
2883 | 0 | 0 | 0 | 0 | 0 | 1784.05 | 0 | 0 | 0 | 0 | 0
2884 | 0 | 0 | 0 | 0 | 0 | 1782.1 | 0 | 0 | 0 | 0 | 0
2885 | 0 | 0 | 0 | 0 | 0 | 1782.9 | 0 | 0 | 0 | 0 | 0
2886 | 0 | 0 | 0 | 0 | 0 | 1776.4 | 0 | 0 | 0 | 0 | 0
2887 | 59.935 | 62.2608 | 62.2608 | 60.6084 | 59.935 | 1738.75 | 109990.4524 | 21576.6 | 9787.3855 | 0 | 15658.0187
2888 | 60.615 | 1481.2213 | 62.9682 | 1441.9105 | 60.615 | 1668.4 | 106874.4366 | 21821.4 | 9898.4295 | 0 | 20099.934
2889 | 57.444 | 2592.2832 | 59.6731 | 2523.4854 | 57.444 | 1617.9 | 98367.5509 | 20679.84 | 9380.6052 | 0 | 21949.3524
2890 | 63.569 | 3275.4511 | 66.0358 | 3188.5224 | 63.569 | 1637.75 | 110129.8006 | 22884.84 | 10380.8177 | 0 | 23027.8702
2891 | 57.64 | 3716.9722 | 59.8767 | 3618.3258 | 57.64 | 1613.2 | 98575.9454 | 20750.4 | 9412.612 | 0 | 22295.152
2892 | 64.133 | 3935.1347 | 66.6217 | 3830.6984 | 64.133 | 1662.8 | 112720.2265 | 23087.88 | 10472.9189 | 0 | 21625.6476
2893 | 56.963 | 973.545 | 59.1734 | 947.7076 | 56.963 | 1669 | 100247.4336 | 20506.68 | 9302.0579 | 0 | 18854.753
2894 | 68.404 | 1509.3532 | 71.0584 | 1469.2958 | 68.404 | 1710.4 | 123831.4567 | 24625.44 | 11170.3732 | 0 | 19809.7984
2895 | 60.106 | 716.6111 | 62.4384 | 697.5927 | 60.106 | 1691.05 | 107353.2741 | 21638.16 | 9815.3098 | 0 | 18569.7487
2896 | 68.887 | 242.1838 | 71.5601 | 235.7564 | 68.887 | 1719.2 | 124755.7256 | 24799.32 | 11249.2471 | 0 | 19343.4696
2897 | 59.771 | 111.9759 | 62.0904 | 109.0041 | 59.771 | 1684.4 | 106286.8717 | 21517.56 | 9760.6043 | 0 | 18863.7276
2898 | 69.059 | 71.7388 | 71.7388 | 69.8349 | 69.059 | 1681 | 122456.0719 | 24861.24 | 11277.3347 | 0 | 22029.821
2899 | 74.479 | 77.3691 | 77.3691 | 75.3158 | 74.479 | 1681.95 | 131801.199 | 26812.44 | 12162.4207 | 0 | 23688.0459
2900 | 85.6 | 88.9217 | 88.9217 | 86.5618 | 85.6 | 1771 | 159419.4994 | 30816 | 13978.48 | 0 | 19602.4
2901 | 76 | 78.9492 | 78.9492 | 76.8539 | 76 | 1766.65 | 141038.7185 | 27360 | 12410.8 | 0 | 17734.6
2902 | 78.4 | 81.4423 | 81.4423 | 79.2809 | 78.4 | 1818.3 | 149951.2565 | 28224 | 12802.72 | 0 | 14245.28
2903 | 72.8 | 75.625 | 75.625 | 73.6179 | 72.8 | 1830.65 | 140628.1617 | 26208 | 11888.24 | 0 | 12328.68
2904 | 0 | 0 | 0 | 0 | 0 | 1816.15 | 0 | 0 | 0 | 0 | 0
2905 | 0 | 0 | 0 | 0 | 0 | 1777.05 | 0 | 0 | 0 | 0 | 0
2906 | 0 | 0 | 0 | 0 | 0 | 1749.7 | 0 | 0 | 0 | 0 | 0
2907 | 0 | 0 | 0 | 0 | 0 | 1705.25 | 0 | 0 | 0 | 0 | 0
2908 | 0 | 0 | 0 | 0 | 0 | 1699.1 | 0 | 0 | 0 | 0 | 0
2909 | 0 | 0 | 0 | 0 | 0 | 1645.35 | 0 | 0 | 0 | 0 | 0
2910 | 0 | 0 | 0 | 0 | 0 | 1591 | 0 | 0 | 0 | 0 | 0
2911 | 59.139 | 61.4339 | 61.4339 | 59.8035 | 59.139 | 1471.7 | 91570.0701 | 21290.04 | 9657.3987 | 0 | 31243.1337
2912 | 159.508 | 1467.0832 | 165.6977 | 1428.1476 | 159.508 | 841.6 | 140892.9826 | 57422.88 | 26047.6564 | 0 | 184774.0672
2913 | 1257.452 | 2571.1415 | 1306.2471 | 2502.9048 | 1257.452 | 363.7 | 481410.8619 | 452682.72 | 205341.9116 | 0 | 2057568.7076
2914 | 1452.636 | 3286.3502 | 1509.0052 | 3199.1323 | 1452.636 | 1353.45 | 2081338.3186 | 522948.96 | 237215.4588 | 0 | 939201.8058
2915 | 1793.298 | 3715.1803 | 1862.8865 | 3616.5814 | 1793.298 | 1432.8 | 2714500.196 | 645587.28 | 292845.5634 | 0 | 1017158.6256
2916 | 1328.98 | 3916.0197 | 1380.5507 | 3812.0906 | 1328.98 | 1429.15 | 2009421.7392 | 478432.8 | 217022.434 | 0 | 758648.233
2917 | 1338.234 | 3874.2618 | 1390.1638 | 3771.441 | 1338.234 | 1427.9 | 2020297.2145 | 481764.24 | 218533.6122 | 0 | 765603.6714
2918 | 1057.156 | 2721.8471 | 1098.1787 | 2649.6108 | 1057.156 | 1449.05 | 1625562.7837 | 380576.16 | 172633.5748 | 0 | 582440.0982
2919 | 1280.998 | 1330.7068 | 1330.7068 | 1295.3906 | 1280.998 | 412.85 | 560759.3548 | 461159.28 | 209186.9734 | 0 | 2033135.9757
2920 | 1089.986 | 1902.5979 | 1132.2826 | 1852.104 | 1089.986 | 411.15 | 472892.8441 | 392394.96 | 177994.7138 | 0 | 1731824.2561
2921 | 1851.164 | 957.2523 | 957.2523 | 931.8474 | 931.8474 | 398.4 | 390606.1321 | 335465.0595 | 152170.6784 | 1685107.3508 | 1460875.416
2922 | 1796.006 | 197.8113 | 197.8113 | 192.5615 | 192.5615 | 1461.15 | 295948.3229 | 69322.1308 | 31445.2888 | 2939113.8156 | 101566.7588
2923 | 1783.629 | 0 | 0 | 0 | 0 | 1458.3 | 0 | 0 | 0 | 6060771.342 | 0
2924 | 1345.6 | 0 | 0 | 0 | 0 | 1590 | 0 | 0 | 0 | 4572348.8 | 0
2925 | 1422.4 | 0 | 0 | 0 | 0 | 1660.65 | 0 | 0 | 0 | 4833315.2 | 0
2926 | 1416.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1784 | 578898.9123 | 111351.8261 | 50510.4255 | 3763248.8863 | 66068.784
2927 | 1570.4 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1773.25 | 1116449.9398 | 215514.4963 | 97759.7701 | 3302001.8159 | 134236
2928 | 0 | 0 | 0 | 0 | 0 | 1748.7 | 0 | 0 | 0 | 0 | 0
2929 | 0 | 0 | 0 | 0 | 0 | 1775.5 | 0 | 0 | 0 | 0 | 0
2930 | 0 | 0 | 0 | 0 | 0 | 1661.75 | 0 | 0 | 0 | 0 | 0
2931 | 0 | 0 | 0 | 0 | 0 | 1520.55 | 0 | 0 | 0 | 0 | 0
2932 | 0 | 0 | 0 | 0 | 0 | 1382.8 | 0 | 0 | 0 | 0 | 0
2933 | 0 | 0 | 0 | 0 | 0 | 1379.45 | 0 | 0 | 0 | 0 | 0
2934 | 0 | 0 | 0 | 0 | 0 | 1561.85 | 0 | 0 | 0 | 0 | 0
2935 | 1555.098 | 462.1673 | 462.1673 | 449.9017 | 449.9017 | 1700.6 | 805946.6992 | 161964.6046 | 73468.9443 | 2025824.8556 | 131851.269
2936 | 1292.903 | 1343.0738 | 1343.0738 | 1307.4293 | 1292.903 | 1726.4 | 2345160.3858 | 465445.08 | 211131.0599 | 0 | 353738.2608
2937 | 1616.041 | 1973.6272 | 1678.7511 | 1921.2482 | 1616.041 | 1788.7 | 3030024.7244 | 581774.76 | 263899.4953 | 0 | 341469.4633
2938 | 1859.685 | 3129.8865 | 1931.8496 | 3046.821 | 1859.685 | 1797.4 | 3521620.0856 | 669486.6 | 303686.5605 | 0 | 376772.181
2939 | 1608.786 | 3053.8533 | 1671.2145 | 2972.8057 | 1608.786 | 1794.45 | 3050603.2218 | 579162.96 | 262714.7538 | 0 | 330685.9623
2940 | 1823.532 | 3987.4905 | 1894.2937 | 3881.6646 | 1823.532 | 1778.3 | 3421588.56 | 656471.52 | 297782.7756 | 0 | 404277.0444
2941 | 1798.158 | 2114.5328 | 1867.9351 | 2058.4142 | 1798.158 | 1711.6 | 3242191.1883 | 647336.88 | 293639.2014 | 0 | 518588.7672
2942 | 1525.044 | 1504.6204 | 1504.6204 | 1464.6886 | 1464.6886 | 1788.4 | 2759187.34 | 527287.887 | 239183.6443 | 110631.4942 | 300436.8744
2943 | 1520.027 | 1579.0113 | 1579.0113 | 1537.1052 | 1520.027 | 1821.15 | 2917658.7461 | 547209.72 | 248220.4091 | 0 | 271856.8289
2944 | 1553.305 | 500.1533 | 500.1533 | 486.8795 | 486.8795 | 1836.15 | 939841.6943 | 175276.6292 | 79507.4265 | 1954757.8945 | 78087.633
2945 | 1531.346 | 32.3255 | 32.3255 | 31.4676 | 31.4676 | 1906.2 | 62948.1048 | 11328.3448 | 5138.6631 | 2749277.0626 | 2889.2276
2946 | 1537.263 | 0 | 0 | 0 | 0 | 1876.95 | 0 | 0 | 0 | 2817803.079 | 0
2947 | 1394.4 | 0 | 0 | 0 | 0 | 1868.9 | 0 | 0 | 0 | 4738171.2 | 0
2948 | 1347.2 | 0 | 0 | 0 | 0 | 1874.7 | 0 | 0 | 0 | 4577785.6 | 0
2949 | 1466.4 | 0 | 0 | 0 | 0 | 1874.25 | 0 | 0 | 0 | 4982827.2 | 0
2950 | 1319.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1876 | 610635.2574 | 111351.8261 | 50510.4255 | 3431604.0863 | 37928.376
2951 | 1240 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1865.25 | 1176726.2989 | 215514.4963 | 97759.7701 | 2179302.6159 | 79772
2952 | 0 | 0 | 0 | 0 | 0 | 1847.5 | 0 | 0 | 0 | 0 | 0
2953 | 0 | 0 | 0 | 0 | 0 | 1827.05 | 0 | 0 | 0 | 0 | 0
2954 | 0 | 0 | 0 | 0 | 0 | 1790.5 | 0 | 0 | 0 | 0 | 0
2955 | 0 | 0 | 0 | 0 | 0 | 1733.25 | 0 | 0 | 0 | 0 | 0
2956 | 0 | 0 | 0 | 0 | 0 | 1715.8 | 0 | 0 | 0 | 0 | 0
2957 | 0 | 0 | 0 | 0 | 0 | 1712.45 | 0 | 0 | 0 | 0 | 0
2958 | 0 | 0 | 0 | 0 | 0 | 1745.6 | 0 | 0 | 0 | 0 | 0
2959 | 1206.214 | 465.7865 | 465.7865 | 453.4248 | 453.4248 | 1758.1 | 837793.1393 | 163232.9365 | 74044.2737 | 1379862.5601 | 107363.2027
2960 | 1033.754 | 1073.8686 | 1073.8686 | 1045.3687 | 1033.754 | 1727.1 | 1875707.7701 | 372151.44 | 168812.0282 | 0 | 282111.4666
2961 | 1422.494 | 2016.1133 | 1477.6935 | 1962.6067 | 1422.494 | 1809.55 | 2708433.2594 | 512097.84 | 232293.2702 | 0 | 270913.9823
2962 | 1530.86 | 2626.6355 | 1590.2646 | 2556.926 | 1530.86 | 1797.4 | 2906731.9913 | 551109.6 | 249989.438 | 0 | 310152.236
2963 | 1656.662 | 3856.2946 | 1720.9484 | 3753.9507 | 1656.662 | 1770.8 | 3101645.3775 | 596398.32 | 270532.9046 | 0 | 379706.9304
2964 | 1345.486 | 3409.8766 | 1397.6972 | 3319.3803 | 1345.486 | 1707.55 | 2420916.895 | 484374.96 | 219717.8638 | 0 | 393487.3807
2965 | 1497.656 | 914.3871 | 914.3871 | 890.1198 | 890.1198 | 1560.7 | 1461449.6631 | 320443.1166 | 145356.5582 | 1113613.9126 | 382758.1363
2966 | 1691.038 | 289.6801 | 289.6801 | 281.9921 | 281.9921 | 1797.7 | 534722.2638 | 101517.1569 | 46049.3104 | 2582781.1299 | 55840.2621
2967 | 1889.882 | 552.2193 | 552.2193 | 537.5637 | 537.5637 | 1841.85 | 1044101.5503 | 193522.9165 | 87784.1452 | 2478799.5227 | 83217.423
2968 | 1787.216 | 1118.1009 | 1118.1009 | 1088.4271 | 1088.4271 | 1918.95 | 2198080.1557 | 391833.7497 | 177740.1426 | 1280880.0859 | 86350.9131
2969 | 1100.388 | 658.0859 | 658.0859 | 640.6207 | 640.6207 | 1907.4 | 1283976.6864 | 230623.4458 | 104613.3575 | 842753.4924 | 58066.682
2970 | 1874.444 | 138.3813 | 138.3813 | 134.7087 | 134.7087 | 1836.15 | 259913.7875 | 48495.1302 | 21997.9299 | 3188934.8141 | 21605.261
2971 | 1314.638 | 0 | 0 | 0 | 0 | 1846.55 | 0 | 0 | 0 | 2409731.454 | 0
2972 | 1416 | 0 | 0 | 0 | 0 | 1874.7 | 0 | 0 | 0 | 2595528 | 0
2973 | 988.8 | 0 | 0 | 0 | 0 | 1873.05 | 0 | 0 | 0 | 1812470.4 | 0
2974 | 963.2 | 0 | 0 | 0 | 0 | 1876 | 0 | 0 | 0 | 1765545.6 | 0
2975 | 1384 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1864.05 | 606024.6175 | 111351.8261 | 50510.4255 | 1969905.619 | 41583.5703
2976 | 0 | 0 | 0 | 0 | 0 | 1848.7 | 0 | 0 | 0 | 0 | 0
2977 | 0 | 0 | 0 | 0 | 0 | 1821 | 0 | 0 | 0 | 0 | 0
2978 | 0 | 0 | 0 | 0 | 0 | 1813.8 | 0 | 0 | 0 | 0 | 0
2979 | 0 | 0 | 0 | 0 | 0 | 1806.2 | 0 | 0 | 0 | 0 | 0
2980 | 0 | 0 | 0 | 0 | 0 | 1802.05 | 0 | 0 | 0 | 0 | 0
2981 | 0 | 0 | 0 | 0 | 0 | 1799.8 | 0 | 0 | 0 | 0 | 0
2982 | 0 | 0 | 0 | 0 | 0 | 1800.35 | 0 | 0 | 0 | 0 | 0
2983 | 1212.52 | 1081.8829 | 1081.8829 | 1053.1704 | 1053.1704 | 1801.75 | 1996484.1284 | 379141.3292 | 171982.7196 | 292087.8921 | 205566.218
2984 | 1002.061 | 1040.9457 | 1040.9457 | 1013.3196 | 1002.061 | 1799.55 | 1899872.9951 | 360741.96 | 163636.5613 | 0 | 200863.1274
2985 | 965.107 | 1002.5577 | 1002.5577 | 975.9504 | 965.107 | 1840.1 | 1871496.7635 | 347438.52 | 157601.9731 | 0 | 154320.6093
2986 | 1411.917 | 3142.615 | 1466.7061 | 3059.2117 | 1411.917 | 1852.75 | 2768360.301 | 508290.12 | 230566.0461 | 0 | 207904.7783
2987 | 1427.898 | 2154.4821 | 1483.3072 | 2097.3033 | 1427.898 | 1792.6 | 2712512.3769 | 514043.28 | 233175.7434 | 0 | 296146.0452
2988 | 1337.421 | 1693.4148 | 1389.3193 | 1648.4725 | 1337.421 | 1775.35 | 2512100.0361 | 481471.56 | 218400.8493 | 0 | 300451.6277
2989 | 1072.122 | 2291.5326 | 1113.7254 | 2230.7166 | 1072.122 | 1756.45 | 1980641.7015 | 385963.92 | 175077.5226 | 0 | 261115.3131
2990 | 1193.708 | 2910.9418 | 1240.0295 | 2833.687 | 1193.708 | 1832.95 | 2306188.51 | 429734.88 | 194932.5164 | 0 | 199408.9214
2991 | 980.197 | 2796.5891 | 1018.2333 | 2722.3692 | 980.197 | 1911.15 | 1976308.3801 | 352870.92 | 160066.1701 | 0 | 87090.5034
2992 | 1206.253 | 2106.5901 | 1253.0613 | 2050.6823 | 1206.253 | 1908 | 2420143.468 | 434251.08 | 196981.1149 | 0 | 110975.276
2993 | 1386.057 | 687.4675 | 687.4675 | 669.2225 | 669.2225 | 1888 | 1327832.8282 | 240920.0877 | 109284.0287 | 1313957.701 | 73367.392
2994 | 1219.223 | 145.8513 | 145.8513 | 141.9805 | 141.9805 | 1810.35 | 271211.425 | 51112.976 | 23185.4139 | 1974585.5226 | 26356.9881
2995 | 1409.584 | 0 | 0 | 0 | 0 | 1763.25 | 0 | 0 | 0 | 4789766.432 | 0
2996 | 1578.4 | 0 | 0 | 0 | 0 | 1810.7 | 0 | 0 | 0 | 5363403.2 | 0
2997 | 1444.8 | 0 | 0 | 0 | 0 | 1833.95 | 0 | 0 | 0 | 4909430.4 | 0
2998 | 1684 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1862.2 | 603957.0186 | 111351.8261 | 50510.4255 | 4671194.4863 | 42149.4372
2999 | 1376.8 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1854.3 | 1167958.4841 | 215514.4963 | 97759.7701 | 2644149.0159 | 86254.4
3000 | 0 | 0 | 0 | 0 | 0 | 1837.05 | 0 | 0 | 0 | 0 | 0
3001 | 0 | 0 | 0 | 0 | 0 | 1762.4 | 0 | 0 | 0 | 0 | 0
3002 | 0 | 0 | 0 | 0 | 0 | 1808.65 | 0 | 0 | 0 | 0 | 0
3003 | 0 | 0 | 0 | 0 | 0 | 1801.25 | 0 | 0 | 0 | 0 | 0
3004 | 0 | 0 | 0 | 0 | 0 | 1794.35 | 0 | 0 | 0 | 0 | 0
3005 | 0 | 0 | 0 | 0 | 0 | 1749.2 | 0 | 0 | 0 | 0 | 0
3006 | 0 | 0 | 0 | 0 | 0 | 1761.1 | 0 | 0 | 0 | 0 | 0
3007 | 781.83 | 294.15 | 294.15 | 286.3434 | 286.3434 | 1716.25 | 517149.3243 | 103083.6415 | 46759.8852 | 908226.8485 | 79531.4363
3008 | 709.607 | 996.1545 | 737.1431 | 969.7171 | 709.607 | 1683.1 | 1259697.6006 | 255458.52 | 115878.8231 | 0 | 224874.4583
3009 | 1534.229 | 2202.103 | 1593.7644 | 2143.6604 | 1534.229 | 1569.25 | 2551121.0427 | 552322.44 | 250539.5957 | 0 | 660869.1417
3010 | 1020.516 | 3356.8747 | 1060.1169 | 3267.7851 | 1020.516 | 1571.95 | 1699984.6407 | 367385.76 | 166650.2628 | 0 | 436831.8738
3011 | 1287.992 | 2648.0525 | 1337.9722 | 2577.7746 | 1287.992 | 1541.35 | 2095515.114 | 463677.12 | 210329.0936 | 0 | 590737.5308
3012 | 1475.707 | 4024.2403 | 1532.9714 | 3917.4391 | 1475.707 | 1501.65 | 2346657.7656 | 531254.52 | 240982.9531 | 0 | 735418.5834
3013 | 1238.1 | 3985.6809 | 1286.1442 | 3879.9031 | 1238.1 | 1419.85 | 1859255.4051 | 445716 | 202181.73 | 0 | 718283.715
3014 | 1241.662 | 2538.3475 | 1289.8444 | 2470.9811 | 1241.662 | 1477.15 | 1942546.8649 | 446998.32 | 202763.4046 | 0 | 649202.9767
3015 | 1191.082 | 1904.314 | 1237.3016 | 1853.7746 | 1191.082 | 1641.7 | 2074298.1723 | 428789.52 | 194503.6906 | 0 | 426764.6806
3016 | 1159.838 | 1608.6556 | 1204.8452 | 1565.9628 | 1159.838 | 1751.5 | 2158270.8984 | 417541.68 | 189401.5454 | 0 | 288219.743
3017 | 1030.094 | 783.3502 | 783.3502 | 762.5605 | 762.5605 | 1770.8 | 1430239.5022 | 274521.7829 | 124526.1309 | 490388.891 | 171081.756
3018 | 1147.534 | 168.0225 | 168.0225 | 163.5633 | 163.5633 | 1773.7 | 306763.1588 | 58882.7833 | 26709.8848 | 1803618.3171 | 36231.5352
3019 | 1455.483 | 0 | 0 | 0 | 0 | 1821.2 | 0 | 0 | 0 | 4945731.234 | 0
3020 | 1283.2 | 0 | 0 | 0 | 0 | 1814.5 | 0 | 0 | 0 | 4360313.6 | 0
3021 | 1238.4 | 0 | 0 | 0 | 0 | 1796.55 | 0 | 0 | 0 | 4208083.2 | 0
3022 | 1134.4 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1842 | 600581.0643 | 111351.8261 | 50510.4255 | 2803653.6863 | 48328.092
3023 | 1165.6 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1817.3 | 1147147.7403 | 215514.4963 | 97759.7701 | 1926491.4159 | 108158.4
3024 | 0 | 0 | 0 | 0 | 0 | 1731.5 | 0 | 0 | 0 | 0 | 0
3025 | 0 | 0 | 0 | 0 | 0 | 1755.9 | 0 | 0 | 0 | 0 | 0
3026 | 0 | 0 | 0 | 0 | 0 | 1720.85 | 0 | 0 | 0 | 0 | 0
3027 | 0 | 0 | 0 | 0 | 0 | 1704.9 | 0 | 0 | 0 | 0 | 0
3028 | 0 | 0 | 0 | 0 | 0 | 1699.1 | 0 | 0 | 0 | 0 | 0
3029 | 0 | 0 | 0 | 0 | 0 | 1696.45 | 0 | 0 | 0 | 0 | 0
3030 | 0 | 0 | 0 | 0 | 0 | 1704.75 | 0 | 0 | 0 | 0 | 0
3031 | 1273.643 | 474.8647 | 474.8647 | 462.262 | 462.262 | 1738.15 | 845380.254 | 166414.3237 | 75487.3863 | 1487261.3543 | 118482.9354
3032 | 802.242 | 971.9192 | 833.3728 | 946.125 | 802.242 | 1755.95 | 1485716.3815 | 288807.12 | 131006.1186 | 0 | 195787.1601
3033 | 1200.115 | 1398.0234 | 1246.6852 | 1360.9207 | 1200.115 | 1847.05 | 2343921.0893 | 432041.4 | 195978.7795 | 0 | 183557.5893
3034 | 1471.92 | 3300.8873 | 1529.0375 | 3213.2835 | 1471.92 | 1826.25 | 2848625.6312 | 529891.2 | 240364.536 | 0 | 255746.1
3035 | 1380.935 | 3680.7138 | 1434.5218 | 3583.0296 | 1380.935 | 1770.8 | 2584394.2566 | 497136.6 | 225506.6855 | 0 | 316510.302
3036 | 1423.39 | 3850.2509 | 1478.6243 | 3748.0673 | 1423.39 | 1668.8 | 2510971.3608 | 512420.4 | 232439.587 | 0 | 471426.768
3037 | 1393.065 | 3070.4191 | 1447.1225 | 2988.9318 | 1393.065 | 1635.85 | 2399434.7871 | 501503.4 | 227487.5145 | 0 | 507284.6198
3038 | 1542.057 | 3128.2691 | 1601.8961 | 3045.2465 | 1542.057 | 1758.95 | 2861762.6511 | 555140.52 | 251817.9081 | 0 | 371712.8399
3039 | 1458.87 | 2575.3756 | 1515.4811 | 2507.0266 | 1458.87 | 1821.15 | 2805277.3978 | 525193.2 | 238233.471 | 0 | 260918.8995
3040 | 2088.377 | 316.1748 | 316.1748 | 307.7837 | 307.7837 | 1819.45 | 590831.6453 | 110802.1185 | 50261.0721 | 3263827.5878 | 54394.8401
3041 | 1746.298 | 318.8944 | 318.8944 | 310.4311 | 310.4311 | 1836.25 | 600389.7498 | 111755.1876 | 50693.3948 | 2631944.0702 | 49757.8937
3042 | 1528.475 | 63.1853 | 63.1853 | 61.5084 | 61.5084 | 1826.95 | 118507.9476 | 22143.0224 | 10044.321 | 2688949.7862 | 10418.8214
3043 | 1628.348 | 0 | 0 | 0 | 0 | 1805.75 | 0 | 0 | 0 | 5533126.504 | 0
3044 | 1763.2 | 0 | 0 | 0 | 0 | 1852.35 | 0 | 0 | 0 | 5991353.6 | 0
3045 | 1925.6 | 0 | 0 | 0 | 0 | 1824.25 | 0 | 0 | 0 | 6543188.8 | 0
3046 | 2003.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1876 | 608830.1256 | 111351.8261 | 50510.4255 | 5755836.0863 | 37928.376
3047 | 1744 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1865.25 | 1174121.8305 | 215514.4963 | 97759.7701 | 3891894.6159 | 79772
3048 | 0 | 0 | 0 | 0 | 0 | 1847.5 | 0 | 0 | 0 | 0 | 0
3049 | 0 | 0 | 0 | 0 | 0 | 1827.05 | 0 | 0 | 0 | 0 | 0
3050 | 0 | 0 | 0 | 0 | 0 | 1791.7 | 0 | 0 | 0 | 0 | 0
3051 | 0 | 0 | 0 | 0 | 0 | 1742.1 | 0 | 0 | 0 | 0 | 0
3052 | 0 | 0 | 0 | 0 | 0 | 1715.8 | 0 | 0 | 0 | 0 | 0
3053 | 0 | 0 | 0 | 0 | 0 | 1754.15 | 0 | 0 | 0 | 0 | 0
3054 | 0 | 0 | 0 | 0 | 0 | 1795.55 | 0 | 0 | 0 | 0 | 0
3055 | 1371.414 | 307.7168 | 307.7168 | 299.5502 | 299.5502 | 1780.15 | 560202.0046 | 107838.0661 | 48916.545 | 1964726.3756 | 64463.0979
3056 | 1360.451 | 935.4769 | 935.4769 | 910.6499 | 910.6499 | 1763.95 | 1691365.8196 | 327833.9533 | 148709.1238 | 824485.4709 | 210411.6653
3057 | 1498.823 | 1475.2534 | 1475.2534 | 1436.1009 | 1436.1009 | 1870.3 | 2832992.9427 | 516996.3417 | 234515.285 | 114969.5192 | 182322.1434
3058 | 2067.103 | 2147.3164 | 2147.3164 | 2090.3278 | 2067.103 | 1818.25 | 3976161.3118 | 744157.08 | 337557.9199 | 0 | 375695.9702
3059 | 1900.996 | 3009.9129 | 1974.7637 | 2930.0314 | 1900.996 | 1743.7 | 3519158.3344 | 684358.56 | 310432.6468 | 0 | 487225.2748
3060 | 2047.677 | 3788.2062 | 2127.1366 | 3687.6692 | 2047.677 | 1658.95 | 3601732.0797 | 737163.72 | 334385.6541 | 0 | 698360.2409
3061 | 1737.954 | 3367.4134 | 1805.3949 | 3278.044 | 1737.954 | 1666.05 | 3047616.9577 | 625663.44 | 283807.8882 | 0 | 580389.7383
3062 | 1834.925 | 2992.6905 | 1906.1288 | 2913.2661 | 1834.925 | 1817.7 | 3526857.9967 | 660573 | 299643.2525 | 0 | 334506.8275
3063 | 1799.821 | 1052.8515 | 1052.8515 | 1024.9094 | 1024.9094 | 1850.7 | 2004856.5211 | 368967.3704 | 167367.6988 | 1420413.0321 | 149782.0897
3064 | 1674.824 | 191.2294 | 191.2294 | 186.1543 | 186.1543 | 1828.15 | 359445.9972 | 67015.5432 | 30398.995 | 2728731.5847 | 31313.8196
3065 | 1838.59 | 331.172 | 331.172 | 322.3829 | 322.3829 | 1885.05 | 639292.1999 | 116057.8326 | 52645.1224 | 2779207.6722 | 36274.0818
3066 | 1892.738 | 67.7332 | 67.7332 | 65.9356 | 65.9356 | 1836.15 | 127438.5254 | 23736.8103 | 10767.2809 | 3348528.8282 | 10575.0428
3067 | 1857.119 | 0 | 0 | 0 | 0 | 1846.55 | 0 | 0 | 0 | 6310490.362 | 0
3068 | 1924 | 0 | 0 | 0 | 0 | 1873.5 | 0 | 0 | 0 | 6537752 | 0
3069 | 1824.8 | 0 | 0 | 0 | 0 | 1832.25 | 0 | 0 | 0 | 6200670.4 | 0
3070 | 2112.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1876 | 608741.7488 | 111351.8261 | 50510.4255 | 6128256.8863 | 37928.376
3071 | 1693.6 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1865.25 | 1175884.0118 | 215514.4963 | 97759.7701 | 3720635.4159 | 79772
3072 | 0 | 0 | 0 | 0 | 0 | 1848.7 | 0 | 0 | 0 | 0 | 0
3073 | 0 | 0 | 0 | 0 | 0 | 1827.05 | 0 | 0 | 0 | 0 | 0
3074 | 0 | 0 | 0 | 0 | 0 | 1812.85 | 0 | 0 | 0 | 0 | 0
3075 | 0 | 0 | 0 | 0 | 0 | 1805.25 | 0 | 0 | 0 | 0 | 0
3076 | 0 | 0 | 0 | 0 | 0 | 1777.45 | 0 | 0 | 0 | 0 | 0
3077 | 0 | 0 | 0 | 0 | 0 | 1754.15 | 0 | 0 | 0 | 0 | 0
3078 | 0 | 0 | 0 | 0 | 0 | 1774.4 | 0 | 0 | 0 | 0 | 0
3079 | 1151.437 | 478.2532 | 478.2532 | 465.5607 | 465.5607 | 1770.1 | 867811.4925 | 167601.8377 | 76026.0558 | 1257211.3309 | 104768.4187
3080 | 1016.173 | 1055.6053 | 1055.6053 | 1027.5901 | 1016.173 | 1743.1 | 1867148.1756 | 365822.28 | 165941.0509 | 0 | 261054.8437
3081 | 1393.713 | 2065.8658 | 1447.7967 | 2011.0389 | 1393.713 | 1809.55 | 2659646.4084 | 501736.68 | 227593.3329 | 0 | 265432.6409
3082 | 1742.288 | 3318.8004 | 1809.897 | 3230.7213 | 1742.288 | 1789.05 | 3290296.1965 | 627223.68 | 284515.6304 | 0 | 367535.6536
3083 | 1918.198 | 2393.5557 | 1992.6332 | 2330.0321 | 1918.198 | 1732.05 | 3516443.0458 | 690551.28 | 313241.7334 | 0 | 513981.1541
3084 | 1389.518 | 3991.3288 | 1443.4379 | 3885.4012 | 1389.518 | 1605.95 | 2355262.9411 | 500226.48 | 226908.2894 | 0 | 547539.5679
3085 | 1454.847 | 3935.2822 | 1511.302 | 3830.842 | 1454.847 | 1603.2 | 2460174.6012 | 523744.92 | 237576.5151 | 0 | 577283.2896
3086 | 1572.945 | 3616.9488 | 1633.9827 | 3520.957 | 1572.945 | 1552.95 | 2579636.0241 | 566260.2 | 256861.9185 | 0 | 703185.0622
3087 | 1407.007 | 1203.4698 | 1203.4698 | 1171.5304 | 1171.5304 | 1592.25 | 1968627.9957 | 421750.9478 | 191310.9161 | 431628.5883 | 467586.497
3088 | 1270.866 | 269.4244 | 269.4244 | 262.274 | 262.274 | 1769.4 | 489838.5962 | 94418.6482 | 42829.3479 | 1848749.0941 | 59201.0156
3089 | 1921.03 | 122.42 | 122.42 | 119.1711 | 119.1711 | 1815.4 | 227773.4837 | 42901.5825 | 19460.6345 | 3302807.4324 | 21533.59
3090 | 1338.785 | 18.5281 | 18.5281 | 18.0364 | 18.0364 | 1807 | 34349.4193 | 6493.1023 | 2945.3433 | 2420932.1925 | 3407.415
3091 | 1455.323 | 0 | 0 | 0 | 0 | 1788.9 | 0 | 0 | 0 | 4945187.554 | 0
3092 | 1472 | 0 | 0 | 0 | 0 | 1852.35 | 0 | 0 | 0 | 5001856 | 0
3093 | 1682.4 | 0 | 0 | 0 | 0 | 1873.05 | 0 | 0 | 0 | 5716795.2 | 0
3094 | 1751.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1876 | 609162.4152 | 111351.8261 | 50510.4255 | 4899540.0863 | 37928.376
3095 | 1388 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1865.25 | 1175273.3221 | 215514.4963 | 97759.7701 | 2682206.6159 | 79772
3096 | 0 | 0 | 0 | 0 | 0 | 1848.7 | 0 | 0 | 0 | 0 | 0
3097 | 0 | 0 | 0 | 0 | 0 | 1777.05 | 0 | 0 | 0 | 0 | 0
3098 | 0 | 0 | 0 | 0 | 0 | 1812.85 | 0 | 0 | 0 | 0 | 0
3099 | 0 | 0 | 0 | 0 | 0 | 1804.05 | 0 | 0 | 0 | 0 | 0
3100 | 0 | 0 | 0 | 0 | 0 | 1764.3 | 0 | 0 | 0 | 0 | 0
3101 | 0 | 0 | 0 | 0 | 0 | 1712.45 | 0 | 0 | 0 | 0 | 0
3102 | 0 | 0 | 0 | 0 | 0 | 1724.75 | 0 | 0 | 0 | 0 | 0
3103 | 596.8 | 474.9831 | 474.9831 | 462.3773 | 462.3773 | 1721.3 | 838531.6956 | 166455.8248 | 75506.2116 | 246396.8255 | 126138.5052
3104 | 559.198 | 580.8975 | 580.8975 | 565.4808 | 559.198 | 1726.4 | 1018601.1984 | 201311.28 | 91317.0334 | 0 | 152996.5728
3105 | 533.643 | 1290.9092 | 554.3509 | 1256.6491 | 533.643 | 1772 | 998291.0847 | 192111.48 | 87143.9019 | 0 | 121670.604
3106 | 918.03 | 2083.9524 | 953.6539 | 2028.6455 | 918.03 | 1726.65 | 1676419.4742 | 330490.8 | 149914.299 | 0 | 250943.5005
3107 | 967.693 | 2508.2398 | 1005.2441 | 2441.6725 | 967.693 | 1522.7 | 1562068.0006 | 348369.48 | 158024.2669 | 0 | 461879.8689
3108 | 627.109 | 3306.8251 | 651.4438 | 3219.0637 | 627.109 | 1480.05 | 980709.8251 | 225759.24 | 102406.8997 | 0 | 326065.3246
3109 | 812.063 | 3246.3189 | 843.5749 | 3160.1633 | 812.063 | 1477.3 | 1261070.2197 | 292342.68 | 132609.8879 | 0 | 424465.3301
3110 | 905.477 | 2960.3588 | 940.6138 | 2881.7925 | 905.477 | 1678.35 | 1606076.3656 | 325971.72 | 147864.3941 | 0 | 291246.6771
3111 | 596.201 | 2225.3078 | 619.3364 | 2166.2493 | 596.201 | 1700 | 1071427.7376 | 214632.36 | 97359.6233 | 0 | 178860.3
3112 | 817.356 | 106.5471 | 106.5471 | 103.7194 | 103.7194 | 1658.25 | 181564.1419 | 37338.9786 | 16937.3756 | 1308095.9152 | 34696.1687
3113 | 855.171 | 36.3239 | 36.3239 | 35.3599 | 35.3599 | 1827.05 | 67990.6871 | 12729.553 | 5774.2667 | 1502713.8022 | 5986.1454
3114 | 864.861 | 0 | 0 | 0 | 0 | 1822.65 | 0 | 0 | 0 | 1585290.213 | 0
3115 | 824.194 | 0 | 0 | 0 | 0 | 1826.9 | 0 | 0 | 0 | 2800611.212 | 0
3116 | 626.4 | 0 | 0 | 0 | 0 | 1873.5 | 0 | 0 | 0 | 2128507.2 | 0
3117 | 780 | 0 | 0 | 0 | 0 | 1832.25 | 0 | 0 | 0 | 2650440 | 0
3118 | 831.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1876 | 610197.1808 | 111351.8261 | 50510.4255 | 1773380.0863 | 37928.376
3119 | 764 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1865.25 | 1177885.5699 | 215514.4963 | 97759.7701 | 561854.6159 | 79772
3120 | 0 | 0 | 0 | 0 | 0 | 1847.5 | 0 | 0 | 0 | 0 | 0
3121 | 0 | 0 | 0 | 0 | 0 | 1777.05 | 0 | 0 | 0 | 0 | 0
3122 | 0 | 0 | 0 | 0 | 0 | 1712.15 | 0 | 0 | 0 | 0 | 0
3123 | 0 | 0 | 0 | 0 | 0 | 1704.55 | 0 | 0 | 0 | 0 | 0
3124 | 0 | 0 | 0 | 0 | 0 | 1699.1 | 0 | 0 | 0 | 0 | 0
3125 | 0 | 0 | 0 | 0 | 0 | 1674.8 | 0 | 0 | 0 | 0 | 0
3126 | 0 | 0 | 0 | 0 | 0 | 1646 | 0 | 0 | 0 | 0 | 0
3127 | 1606.824 | 354.0589 | 354.0589 | 344.6624 | 344.6624 | 1680 | 609737.8801 | 124078.4667 | 56283.3712 | 2313542.1989 | 107959.04
3128 | 1031.203 | 1071.2186 | 1071.2186 | 1042.789 | 1031.203 | 1575.05 | 1711851.1101 | 371233.08 | 168395.4499 | 0 | 438209.7149
3129 | 1251.649 | 1300.2189 | 1300.2189 | 1265.7118 | 1251.649 | 1721.6 | 2277346.4206 | 450593.64 | 204394.2817 | 0 | 348459.0816
3130 | 1182.361 | 2482.0484 | 1228.2422 | 2416.1762 | 1182.361 | 1696.45 | 2125140.5099 | 425649.96 | 193079.5513 | 0 | 358905.6815
3131 | 1327.158 | 3145.0655 | 1378.658 | 3061.5972 | 1327.158 | 1305.6 | 1841694.4088 | 477776.88 | 216724.9014 | 0 | 921578.5152
3132 | 662.126 | 3278.2361 | 687.8196 | 3191.2335 | 662.126 | 1300.95 | 912322.3005 | 238365.36 | 108125.1758 | 0 | 462859.1803
3133 | 803.013 | 3367.5858 | 834.1737 | 3278.2119 | 803.013 | 1522.2 | 1288658.3849 | 289084.68 | 131132.0229 | 0 | 383679.6114
3134 | 839.44 | 2908.1973 | 872.0143 | 2831.0153 | 839.44 | 1615.5 | 1433071.8856 | 302198.4 | 137080.552 | 0 | 322764.68
3135 | 881.612 | 2673.7899 | 915.8227 | 2602.829 | 881.612 | 1770.75 | 1651228.7737 | 317380.32 | 143967.2396 | 0 | 202109.551
3136 | 723.729 | 1746.6172 | 751.8131 | 1700.2629 | 723.729 | 1819.45 | 1390918.8188 | 260542.44 | 118184.9457 | 0 | 130669.2709
3137 | 1037.81 | 774.2316 | 774.2316 | 753.6839 | 753.6839 | 1851.55 | 1470075.558 | 271326.198 | 123076.5781 | 520803.172 | 109517.6515
3138 | 1280.783 | 167.8927 | 167.8927 | 163.4369 | 163.4369 | 1826.95 | 315110.236 | 58837.2777 | 26689.2429 | 2048095.4334 | 27684.539
3139 | 1299.258 | 0 | 0 | 0 | 0 | 1822.4 | 0 | 0 | 0 | 2381539.914 | 0
3140 | 1091.2 | 0 | 0 | 0 | 0 | 1870.2 | 0 | 0 | 0 | 2000169.6 | 0
3141 | 1475.2 | 0 | 0 | 0 | 0 | 1824.25 | 0 | 0 | 0 | 2704041.6 | 0
3142 | 901.6 | 0 | 0 | 0 | 0 | 1876 | 0 | 0 | 0 | 1652632.8 | 0
3143 | 1424.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1865.25 | 607038.9204 | 111351.8261 | 50510.4255 | 2044692.019 | 41216.5215
3144 | 0 | 0 | 0 | 0 | 0 | 1848.7 | 0 | 0 | 0 | 0 | 0
3145 | 0 | 0 | 0 | 0 | 0 | 1821 | 0 | 0 | 0 | 0 | 0
3146 | 0 | 0 | 0 | 0 | 0 | 1813.8 | 0 | 0 | 0 | 0 | 0
3147 | 0 | 0 | 0 | 0 | 0 | 1806.2 | 0 | 0 | 0 | 0 | 0
3148 | 0 | 0 | 0 | 0 | 0 | 1802.05 | 0 | 0 | 0 | 0 | 0
3149 | 0 | 0 | 0 | 0 | 0 | 1799.8 | 0 | 0 | 0 | 0 | 0
3150 | 0 | 0 | 0 | 0 | 0 | 1800.35 | 0 | 0 | 0 | 0 | 0
3151 | 1360.959 | 1062.047 | 1062.047 | 1033.8608 | 1033.8608 | 1751.75 | 1910052.3942 | 372189.8946 | 168829.4716 | 599570.9671 | 252719.2447
3152 | 1089.279 | 1131.5482 | 1131.5482 | 1101.5175 | 1089.279 | 1721.2 | 1980710.1969 | 392140.44 | 177879.2607 | 0 | 303690.9852
3153 | 1352.296 | 1972.8045 | 1404.7715 | 1920.4473 | 1352.296 | 1761.75 | 2518655.4239 | 486826.56 | 220829.9368 | 0 | 322184.522
3154 | 1592.847 | 3095.4969 | 1654.657 | 3013.3441 | 1592.847 | 1766.05 | 2981693.3832 | 573424.92 | 260111.9151 | 0 | 372646.5556
3155 | 1626.609 | 2885.5534 | 1689.7292 | 2808.9724 | 1626.609 | 1622.7 | 2798896.3729 | 585579.24 | 265625.2497 | 0 | 613719.5757
3156 | 1541.713 | 2734.3315 | 1601.5388 | 2661.7638 | 1541.713 | 1448.25 | 2363797.8061 | 555016.68 | 251761.7329 | 0 | 850640.1478
3157 | 1622.298 | 3023.006 | 1685.2509 | 2942.777 | 1622.298 | 1514.75 | 2596088.195 | 584027.28 | 264921.2634 | 0 | 787220.1045
3158 | 1448.694 | 2157.9953 | 1504.9102 | 2100.7233 | 1448.694 | 1721 | 2636563.8929 | 521529.84 | 236571.7302 | 0 | 404185.626
3159 | 1620.387 | 1695.2244 | 1683.2657 | 1650.2341 | 1620.387 | 1812 | 3108786.3597 | 583339.32 | 264609.1971 | 0 | 303681.288
3160 | 1509.994 | 1115.8944 | 1115.8944 | 1086.2792 | 1086.2792 | 1807.65 | 2073342.1876 | 391060.5186 | 177389.3964 | 776669.1947 | 204525.9474
3161 | 1315.27 | 842.3605 | 842.3605 | 820.0047 | 820.0047 | 1836.8 | 1585826.6685 | 295201.7093 | 133906.7754 | 907821.2067 | 130993.9488
3162 | 1693.54 | 182.8431 | 182.8431 | 177.9906 | 177.9906 | 1800.8 | 338163.2981 | 64076.6098 | 29065.8622 | 2778002.0815 | 34705.62
3163 | 1887.87 | 0 | 0 | 0 | 0 | 1755.25 | 0 | 0 | 0 | 6414982.26 | 0
3164 | 1574.4 | 0 | 0 | 0 | 0 | 1850.6 | 0 | 0 | 0 | 5349811.2 | 0
3165 | 1738.4 | 0 | 0 | 0 | 0 | 1813.1 | 0 | 0 | 0 | 5907083.2 | 0
3166 | 1488 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1862.2 | 604978.6995 | 111351.8261 | 50510.4255 | 4005186.4863 | 42149.4372
3167 | 1567.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1854.3 | 1167769.005 | 215514.4963 | 97759.7701 | 3291128.2159 | 86254.4
3168 | 0 | 0 | 0 | 0 | 0 | 1837.05 | 0 | 0 | 0 | 0 | 0
3169 | 0 | 0 | 0 | 0 | 0 | 1770.75 | 0 | 0 | 0 | 0 | 0
3170 | 0 | 0 | 0 | 0 | 0 | 1808.65 | 0 | 0 | 0 | 0 | 0
3171 | 0 | 0 | 0 | 0 | 0 | 1801.25 | 0 | 0 | 0 | 0 | 0
3172 | 0 | 0 | 0 | 0 | 0 | 1795.55 | 0 | 0 | 0 | 0 | 0
3173 | 0 | 0 | 0 | 0 | 0 | 1791.5 | 0 | 0 | 0 | 0 | 0
3174 | 0 | 0 | 0 | 0 | 0 | 1787.25 | 0 | 0 | 0 | 0 | 0
3175 | 1222.398 | 451.2682 | 451.2682 | 439.2918 | 439.2918 | 1779.4 | 824953.0708 | 158145.047 | 71736.3505 | 1435433.6696 | 94857.7794
3176 | 1224.246 | 1271.7526 | 1271.7526 | 1238.0009 | 1224.246 | 1691.45 | 2193901.5114 | 440728.56 | 199919.3718 | 0 | 377741.1033
3177 | 1405.356 | 1987.998 | 1459.8905 | 1935.2377 | 1405.356 | 1598.7 | 2375488.4148 | 505928.16 | 229494.6348 | 0 | 563969.3628
3178 | 1702.904 | 2935.3558 | 1768.9848 | 2857.453 | 1702.904 | 1552.25 | 2794927.4418 | 613045.44 | 278084.2232 | 0 | 762475.266
3179 | 1163.639 | 3200.2489 | 1208.7937 | 3115.316 | 1163.639 | 1498.85 | 1841256.8736 | 418910.04 | 190022.2487 | 0 | 583157.6849
3180 | 1654.093 | 3139.3344 | 1718.2797 | 3056.0182 | 1654.093 | 1463.15 | 2564146.9182 | 595473.48 | 270113.3869 | 0 | 887999.827
3181 | 1527.881 | 3425.0099 | 1587.17 | 3334.112 | 1527.881 | 1426.25 | 2314156.7959 | 550037.16 | 249502.9673 | 0 | 876621.7237
3182 | 1582.693 | 3610.1831 | 1644.109 | 3514.3708 | 1582.693 | 1524.25 | 2561794.5296 | 569769.48 | 258453.7669 | 0 | 752966.1948
3183 | 1693.198 | 2615.8215 | 1758.9021 | 2546.399 | 1693.198 | 1347 | 2415881.658 | 609551.28 | 276499.2334 | 0 | 1105658.294
3184 | 1547.887 | 1368.3635 | 1368.3635 | 1332.0479 | 1332.0479 | 1477.8 | 2086373.5158 | 479537.2283 | 217523.415 | 395633.1502 | 680881.4362
3185 | 1494.49 | 860.1792 | 860.1792 | 837.3505 | 837.3505 | 1662.5 | 1475703.6395 | 301446.1691 | 136739.3317 | 1204536.7593 | 276627.825
3186 | 1557.6 | 189.2661 | 189.2661 | 184.2431 | 184.2431 | 1761.7 | 343145.9478 | 66327.4986 | 30086.8903 | 2517363.2864 | 42976.2135
3187 | 1736.8 | 0 | 0 | 0 | 0 | 1826.2 | 0 | 0 | 0 | 5901646.4 | 0
3188 | 1518.4 | 0 | 0 | 0 | 0 | 1836.85 | 0 | 0 | 0 | 5159523.2 | 0
3189 | 1556 | 0 | 0 | 0 | 0 | 1838.85 | 0 | 0 | 0 | 5287288 | 0
3190 | 1313.6 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1844.4 | 601252.5647 | 111351.8261 | 50510.4255 | 3412575.2863 | 47593.9944
3191 | 1468.8 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1839.65 | 1160229.7864 | 215514.4963 | 97759.7701 | 2956765.0159 | 94927.2
3192 | 0 | 0 | 0 | 0 | 0 | 1822.3 | 0 | 0 | 0 | 0 | 0
3193 | 0 | 0 | 0 | 0 | 0 | 1785.05 | 0 | 0 | 0 | 0 | 0
3194 | 0 | 0 | 0 | 0 | 0 | 1712.5 | 0 | 0 | 0 | 0 | 0
3195 | 0 | 0 | 0 | 0 | 0 | 1704.55 | 0 | 0 | 0 | 0 | 0
3196 | 0 | 0 | 0 | 0 | 0 | 1678.15 | 0 | 0 | 0 | 0 | 0
3197 | 0 | 0 | 0 | 0 | 0 | 1695.75 | 0 | 0 | 0 | 0 | 0
3198 | 0 | 0 | 0 | 0 | 0 | 1696.4 | 0 | 0 | 0 | 0 | 0
3199 | 1067.464 | 490.4893 | 490.4893 | 477.472 | 477.472 | 1700.95 | 853221.0181 | 171889.9209 | 77971.178 | 1081455.3316 | 139767.5966
3200 | 1283.562 | 1333.3703 | 1333.3703 | 1297.9834 | 1283.562 | 1676 | 2263144.2227 | 462082.32 | 209605.6746 | 0 | 415874.088
3201 | 1599.831 | 1661.912 | 1661.912 | 1617.8058 | 1599.831 | 1780.7 | 3005070.1228 | 575939.16 | 261252.4023 | 0 | 350842.9383
3202 | 1734.369 | 2632.1391 | 1801.6708 | 2562.2835 | 1734.369 | 1789.05 | 3281141.2431 | 624372.84 | 283222.4577 | 0 | 365865.1406
3203 | 1623.038 | 3723.3006 | 1686.0196 | 3624.4862 | 1623.038 | 1794.1 | 3088427.9656 | 584293.68 | 265042.1054 | 0 | 334183.5242
3204 | 1636.443 | 4014.1213 | 1699.9448 | 3907.5887 | 1636.443 | 1707.55 | 2954987.3034 | 589119.48 | 267231.1419 | 0 | 478577.7554
3205 | 1725.917 | 3972.032 | 1792.8908 | 3866.6164 | 1725.917 | 1686.4 | 3071357.4109 | 621330.12 | 281842.2461 | 0 | 541247.5712
3206 | 2012.075 | 3651.2803 | 2090.1531 | 3554.3773 | 2012.075 | 1758.95 | 3735379.5531 | 724347 | 328571.8475 | 0 | 485010.6788
3207 | 1948.007 | 3074.7717 | 2023.5989 | 2993.1689 | 1948.007 | 1829.85 | 3758638.682 | 701282.52 | 318109.5431 | 0 | 331453.3911
3208 | 1556.628 | 2258.6981 | 1617.0326 | 2198.7535 | 1556.628 | 1876.95 | 3075927.3307 | 560386.08 | 254197.3524 | 0 | 191543.0754
3209 | 1721.903 | 1166.6671 | 1166.6671 | 1135.7044 | 1135.7044 | 1907.4 | 2276156.7847 | 408853.5702 | 185460.5222 | 1074502.1042 | 102941.568
3210 | 1737.852 | 193.6654 | 193.6654 | 188.5256 | 188.5256 | 1876.95 | 372040.4813 | 67869.2281 | 30786.236 | 2839915.2295 | 22707.4009
3211 | 1568.995 | 0 | 0 | 0 | 0 | 1867.7 | 0 | 0 | 0 | 5331445.01 | 0
3212 | 1459.2 | 0 | 0 | 0 | 0 | 1873.5 | 0 | 0 | 0 | 4958361.6 | 0
3213 | 1577.6 | 0 | 0 | 0 | 0 | 1873.05 | 0 | 0 | 0 | 5360684.8 | 0
3214 | 1764.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1876 | 608116.4594 | 111351.8261 | 50510.4255 | 4945752.8863 | 37928.376
3215 | 1724 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1865.25 | 1172104.7591 | 215514.4963 | 97759.7701 | 3823934.6159 | 79772
3216 | 0 | 0 | 0 | 0 | 0 | 1848.7 | 0 | 0 | 0 | 0 | 0
3217 | 0 | 0 | 0 | 0 | 0 | 1827.05 | 0 | 0 | 0 | 0 | 0
3218 | 0 | 0 | 0 | 0 | 0 | 1812.85 | 0 | 0 | 0 | 0 | 0
3219 | 0 | 0 | 0 | 0 | 0 | 1805.25 | 0 | 0 | 0 | 0 | 0
3220 | 0 | 0 | 0 | 0 | 0 | 1799.8 | 0 | 0 | 0 | 0 | 0
3221 | 0 | 0 | 0 | 0 | 0 | 1796.45 | 0 | 0 | 0 | 0 | 0
3222 | 0 | 0 | 0 | 0 | 0 | 1796.75 | 0 | 0 | 0 | 0 | 0
3223 | 1482.886 | 165.0889 | 165.0889 | 160.7076 | 160.7076 | 1801.3 | 304120.3139 | 57854.7209 | 26243.5442 | 2423553.0841 | 31257.0996
3224 | 905.259 | 517.6759 | 517.6759 | 503.937 | 503.937 | 1827.1 | 966615.3108 | 181417.3362 | 82292.9195 | 735623.1435 | 85287.5933
3225 | 1293.998 | 1272.1785 | 1272.1785 | 1238.4155 | 1238.4155 | 1872.7 | 2435224.2152 | 445829.5962 | 202233.2585 | 101882.6403 | 154315.4787
3226 | 1538.464 | 1598.1637 | 1598.1637 | 1555.7493 | 1538.464 | 1868.25 | 3028590.0253 | 553847.04 | 251231.1712 | 0 | 202692.632
3227 | 1566.084 | 1964.3299 | 1626.8555 | 1912.1977 | 1566.084 | 1794.8 | 2970623.2 | 563790.24 | 255741.5172 | 0 | 321360.4368
3228 | 1519.876 | 2768.1373 | 1578.8534 | 2694.6724 | 1519.876 | 1789.95 | 2867228.1416 | 547155.36 | 248195.7508 | 0 | 319249.9538
3229 | 2001.861 | 2177.7004 | 2079.5427 | 2119.9054 | 2001.861 | 1754.6 | 3688219.9575 | 720669.96 | 326903.9013 | 0 | 491256.6894
3230 | 1474.906 | 642.2919 | 642.2919 | 625.2459 | 625.2459 | 1809.7 | 1191643.0163 | 225088.5093 | 102102.6488 | 1557427.038 | 113358.2846
3231 | 1790.369 | 1859.8438 | 1859.8438 | 1810.4846 | 1790.369 | 1837.85 | 3462590.0288 | 644532.84 | 292367.2577 | 0 | 290308.3334
3232 | 1829.06 | 1001.5657 | 1001.5657 | 974.9847 | 974.9847 | 1857 | 1902935.86 | 350994.4807 | 159214.9964 | 1565520.0823 | 136473.48
3233 | 1677.484 | 92.7019 | 92.7019 | 90.2416 | 90.2416 | 1901.9 | 180005.9681 | 32486.9901 | 14736.4597 | 2909415.2475 | 8665.4673
3234 | 2026.099 | 14.8559 | 14.8559 | 14.4617 | 14.4617 | 1857 | 28220.0567 | 5206.2041 | 2361.592 | 3687331.2113 | 2024.308
3235 | 1587.2 | 0 | 0 | 0 | 0 | 1847.75 | 0 | 0 | 0 | 5393305.6 | 0
3236 | 1344 | 0 | 0 | 0 | 0 | 1874.7 | 0 | 0 | 0 | 4566912 | 0
3237 | 1775.2 | 0 | 0 | 0 | 0 | 1874.25 | 0 | 0 | 0 | 6032129.6 | 0
3238 | 1706.4 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1876 | 608508.263 | 111351.8261 | 50510.4255 | 4747309.6863 | 37928.376
3239 | 1422.4 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1865.25 | 1173849.8786 | 215514.4963 | 97759.7701 | 2799097.8159 | 79772
3240 | 0 | 0 | 0 | 0 | 0 | 1848.7 | 0 | 0 | 0 | 0 | 0
3241 | 0 | 0 | 0 | 0 | 0 | 1785.05 | 0 | 0 | 0 | 0 | 0
3242 | 0 | 0 | 0 | 0 | 0 | 1812.85 | 0 | 0 | 0 | 0 | 0
3243 | 0 | 0 | 0 | 0 | 0 | 1805.25 | 0 | 0 | 0 | 0 | 0
3244 | 0 | 0 | 0 | 0 | 0 | 1799.8 | 0 | 0 | 0 | 0 | 0
3245 | 0 | 0 | 0 | 0 | 0 | 1796.45 | 0 | 0 | 0 | 0 | 0
3246 | 0 | 0 | 0 | 0 | 0 | 1796.75 | 0 | 0 | 0 | 0 | 0
3247 | 1055.099 | 327.9787 | 327.9787 | 319.2743 | 319.2743 | 1800.1 | 605912.5769 | 114938.7591 | 52137.4982 | 1348766.6188 | 62472.9479
3248 | 1425.043 | 989.7254 | 989.7254 | 963.4586 | 963.4586 | 1726.75 | 1753532.2329 | 346845.0986 | 157332.7906 | 846084.192 | 257696.0635
3249 | 1508.333 | 1566.8635 | 1566.8635 | 1525.2798 | 1508.333 | 1830.7 | 2909845.0783 | 542999.88 | 246310.7789 | 0 | 255360.7769
3250 | 1700.252 | 2165.5599 | 1766.2299 | 2108.0871 | 1700.252 | 1846.2 | 3319151.3498 | 612090.72 | 277651.1516 | 0 | 261498.7576
3251 | 1839.549 | 3078.9279 | 1910.9322 | 2997.2149 | 1839.549 | 1711.7 | 3339963.5798 | 662237.64 | 300398.3517 | 0 | 530341.9767
3252 | 1816.85 | 3141.5232 | 1887.3524 | 3058.1489 | 1816.85 | 1604.7 | 3082549.8553 | 654066 | 296691.605 | 0 | 718200.805
3253 | 1707.886 | 3389.2958 | 1774.1601 | 3299.3457 | 1707.886 | 1483.7 | 2673294.6601 | 614838.96 | 278897.7838 | 0 | 881781.5418
3254 | 1728.169 | 2876.3569 | 1795.2302 | 2800.0199 | 1728.169 | 1767.45 | 3227257.0258 | 622140.84 | 282209.9977 | 0 | 401885.701
3255 | 1703.789 | 2384.4537 | 1769.9041 | 2321.1716 | 1703.789 | 1821.15 | 3272986.9227 | 613364.04 | 278228.7437 | 0 | 304722.6626
3256 | 1569.14 | 2026.0058 | 1630.0301 | 1972.2367 | 1569.14 | 1820.15 | 3007514.474 | 564890.4 | 256240.562 | 0 | 282209.829
3257 | 1690.426 | 958.4345 | 958.4345 | 932.9982 | 932.9982 | 1864.2 | 1828917.4186 | 335879.3424 | 152358.6017 | 1388365.2062 | 124020.9796
3258 | 1602.301 | 207.5345 | 207.5345 | 202.0266 | 202.0266 | 1785.8 | 379975.7906 | 72729.5897 | 32990.95 | 2566702.9055 | 42358.6926
3259 | 1476.806 | 0 | 0 | 0 | 0 | 1768.2 | 0 | 0 | 0 | 5018186.788 | 0
3260 | 1332.8 | 0 | 0 | 0 | 0 | 1774.35 | 0 | 0 | 0 | 4528854.4 | 0
3261 | 1378.4 | 0 | 0 | 0 | 0 | 1772.3 | 0 | 0 | 0 | 4683803.2 | 0
3262 | 1814.4 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1876 | 608861.3725 | 111351.8261 | 50510.4255 | 5114293.6863 | 37928.376
3263 | 1490.4 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1865.25 | 1175017.6504 | 215514.4963 | 97759.7701 | 3030161.8159 | 79772
3264 | 0 | 0 | 0 | 0 | 0 | 1848.7 | 0 | 0 | 0 | 0 | 0
3265 | 0 | 0 | 0 | 0 | 0 | 1726.35 | 0 | 0 | 0 | 0 | 0
3266 | 0 | 0 | 0 | 0 | 0 | 1707.5 | 0 | 0 | 0 | 0 | 0
3267 | 0 | 0 | 0 | 0 | 0 | 1704.55 | 0 | 0 | 0 | 0 | 0
3268 | 0 | 0 | 0 | 0 | 0 | 1598.3 | 0 | 0 | 0 | 0 | 0
3269 | 0 | 0 | 0 | 0 | 0 | 1594.95 | 0 | 0 | 0 | 0 | 0
3270 | 0 | 0 | 0 | 0 | 0 | 1675.1 | 0 | 0 | 0 | 0 | 0
3271 | 1106.227 | 369.1819 | 369.1819 | 359.384 | 359.384 | 1680 | 635198.0182 | 129378.2303 | 58687.4028 | 1368963.2684 | 112569.92
3272 | 998.236 | 1036.9723 | 1036.9723 | 1009.4516 | 998.236 | 1625.6 | 1709010.9859 | 359364.96 | 163011.9388 | 0 | 373739.5584
3273 | 1435.791 | 1943.1871 | 1491.5065 | 1891.616 | 1435.791 | 1772 | 2684103.8002 | 516884.76 | 234464.6703 | 0 | 327360.348
3274 | 1831.647 | 2185.9693 | 1902.7226 | 2127.9549 | 1831.647 | 1722.4 | 3336126.6772 | 659392.92 | 299107.9551 | 0 | 508465.2072
3275 | 1511.408 | 3173.884 | 1570.0578 | 3089.6509 | 1511.408 | 1065.9 | 1706954.5066 | 544106.88 | 246812.9264 | 0 | 1411806.2128
3276 | 1131.45 | 2949.229 | 1175.3556 | 2870.9581 | 1131.45 | 381.65 | 456584.7218 | 407322 | 184765.785 | 0 | 1831082.1075
3277 | 1343.015 | 1395.1304 | 1395.1304 | 1358.1044 | 1343.015 | 718.95 | 1017249.0871 | 483485.4 | 219314.3495 | 0 | 1720469.3658
3278 | 1463.195 | 2699.1981 | 1519.9739 | 2627.5628 | 1463.195 | 1580.45 | 2440274.5929 | 526750.2 | 238939.7435 | 0 | 613883.4622
3279 | 1538.188 | 2560.5197 | 1597.877 | 2492.5649 | 1538.188 | 1695.75 | 2755583.7266 | 553747.68 | 251186.1004 | 0 | 467993.699
3280 | 1937.529 | 569.7491 | 569.7491 | 554.6283 | 554.6283 | 1819.45 | 1063470.3235 | 199666.1718 | 90570.794 | 2534857.0656 | 98019.8728
3281 | 1784.662 | 565.2365 | 565.2365 | 550.2354 | 550.2354 | 1807.05 | 1044219.2788 | 198084.7614 | 89853.4487 | 2262703.8694 | 103922.0982
3282 | 1641.186 | 157.2418 | 157.2418 | 153.0687 | 153.0687 | 1735.4 | 279523.39 | 55104.7268 | 24996.1164 | 2727719.0374 | 39645.018
3283 | 1082.752 | 0 | 0 | 0 | 0 | 1717.8 | 0 | 0 | 0 | 3679191.296 | 0
3284 | 1290.4 | 0 | 0 | 0 | 0 | 1774.35 | 0 | 0 | 0 | 4384779.2 | 0
3285 | 1324.8 | 0 | 0 | 0 | 0 | 1773.9 | 0 | 0 | 0 | 4501670.4 | 0
3286 | 1139.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1873.6 | 608342.5439 | 111351.8261 | 50510.4255 | 2819964.0863 | 38662.4736
3287 | 1259.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1822.05 | 1147467.358 | 215514.4963 | 97759.7701 | 2244544.2159 | 105346.4
3288 | 0 | 0 | 0 | 0 | 0 | 1748.7 | 0 | 0 | 0 | 0 | 0
3289 | 0 | 0 | 0 | 0 | 0 | 1734.7 | 0 | 0 | 0 | 0 | 0
3290 | 0 | 0 | 0 | 0 | 0 | 1712.15 | 0 | 0 | 0 | 0 | 0
3291 | 0 | 0 | 0 | 0 | 0 | 1704.55 | 0 | 0 | 0 | 0 | 0
3292 | 0 | 0 | 0 | 0 | 0 | 1657.2 | 0 | 0 | 0 | 0 | 0
3293 | 0 | 0 | 0 | 0 | 0 | 1653.85 | 0 | 0 | 0 | 0 | 0
3294 | 0 | 0 | 0 | 0 | 0 | 1675.1 | 0 | 0 | 0 | 0 | 0
3295 | 1182.657 | 493.6888 | 493.6888 | 480.5866 | 480.5866 | 1700.6 | 857882.9841 | 173011.1787 | 78479.793 | 1286895.0294 | 140844.0474
3296 | 936.672 | 973.0193 | 973.0193 | 947.1959 | 936.672 | 1655.05 | 1627919.4404 | 337201.92 | 152958.5376 | 0 | 323105.0064
3297 | 1006.925 | 1045.9985 | 1045.9985 | 1018.2382 | 1006.925 | 1772.35 | 1874102.8251 | 362493 | 164430.8525 | 0 | 229226.4763
3298 | 980.994 | 1298.9505 | 1019.0602 | 1264.4771 | 980.994 | 1789.4 | 1851400.3931 | 353157.84 | 160196.3202 | 0 | 206597.3364
3299 | 1100.227 | 1881.4738 | 1142.921 | 1831.5405 | 1100.227 | 1770.8 | 2065354.6504 | 396081.72 | 179667.0691 | 0 | 252172.0284
3300 | 1192.407 | 3239.1272 | 1238.6781 | 3153.1625 | 1192.407 | 1605.9 | 2024786.7647 | 429266.52 | 194720.0631 | 0 | 469927.5987
3301 | 1178.5 | 3246.5079 | 1224.2314 | 3160.3474 | 1178.5 | 1582.8 | 1965593.4238 | 424260 | 192449.05 | 0 | 491670.2
3302 | 1218.473 | 3559.5008 | 1265.7555 | 3465.0336 | 1218.473 | 1817.7 | 2333433.3178 | 438650.28 | 198976.6409 | 0 | 222127.6279
3303 | 1017.622 | 3030.7419 | 1057.1106 | 2950.3077 | 1017.622 | 1919.45 | 2054266.9984 | 366343.92 | 166177.6726 | 0 | 81969.4521
3304 | 339.258 | 2243.1212 | 352.4228 | 2183.59 | 339.258 | 1920.15 | 683567.6277 | 122132.88 | 55400.8314 | 0 | 27089.7513
3305 | 224.739 | 1168.1515 | 233.4599 | 1137.1494 | 224.739 | 1907.4 | 449513.6627 | 80906.04 | 36699.8787 | 0 | 20810.8314
3306 | 209.471 | 239.6533 | 217.5995 | 233.293 | 209.471 | 1836.15 | 404088.191 | 75409.56 | 34206.6143 | 0 | 34321.8233
3307 | 115.054 | 119.5186 | 119.5186 | 116.3467 | 115.054 | 1768.55 | 214025.3972 | 41419.44 | 18788.3182 | 0 | 26629.2483
3308 | 0 | 0 | 0 | 0 | 0 | 1774.35 | 0 | 0 | 0 | 0 | 0
3309 | 0 | 0 | 0 | 0 | 0 | 1701.3 | 0 | 0 | 0 | 0 | 0
3310 | 0 | 0 | 0 | 0 | 0 | 1876 | 0 | 0 | 0 | 0 | 0
3311 | 0 | 0 | 0 | 0 | 0 | 1864.05 | 0 | 0 | 0 | 0 | 0
3312 | 0 | 0 | 0 | 0 | 0 | 1805.5 | 0 | 0 | 0 | 0 | 0
3313 | 0 | 0 | 0 | 0 | 0 | 1728.65 | 0 | 0 | 0 | 0 | 0
3314 | 0 | 0 | 0 | 0 | 0 | 1713.8 | 0 | 0 | 0 | 0 | 0
3315 | 0 | 0 | 0 | 0 | 0 | 1705.5 | 0 | 0 | 0 | 0 | 0
3316 | 0 | 0 | 0 | 0 | 0 | 1701.35 | 0 | 0 | 0 | 0 | 0
3317 | 0 | 0 | 0 | 0 | 0 | 1648.7 | 0 | 0 | 0 | 0 | 0
3318 | 0 | 0 | 0 | 0 | 0 | 1598.85 | 0 | 0 | 0 | 0 | 0
3319 | 79.923 | 196.3746 | 83.0244 | 191.1629 | 79.923 | 1629.7 | 135580.0855 | 28772.28 | 13051.4259 | 0 | 29595.4869
3320 | 156.96 | 1576.0039 | 163.0508 | 1534.1776 | 156.96 | 1505.95 | 246067.5457 | 56505.6 | 25631.568 | 0 | 77546.088
3321 | 637.627 | 2581.8277 | 662.37 | 2513.3074 | 637.627 | 1761.75 | 1172578.0818 | 229545.72 | 104124.4891 | 0 | 151914.6328
3322 | 1024.991 | 3316.8672 | 1064.7655 | 3228.8394 | 1024.991 | 1754.4 | 1885621.426 | 368996.76 | 167381.0303 | 0 | 251737.7896
3323 | 1410.943 | 2774.34 | 1465.6943 | 2700.7105 | 1410.943 | 1491.1 | 2212474.0466 | 507939.48 | 230406.9919 | 0 | 718028.8927
3324 | 1071.439 | 2938.1107 | 1113.0159 | 2860.1348 | 1071.439 | 1105.45 | 1247445.6781 | 385718.04 | 174965.9887 | 0 | 958455.7574
3325 | 1560.347 | 3964.858 | 1620.8959 | 3859.6329 | 1560.347 | 716.05 | 1173031.4474 | 561724.92 | 254804.6651 | 0 | 2003407.5307
3326 | 1408.139 | 2908.8891 | 1462.7815 | 2831.6888 | 1408.139 | 1721 | 2533731.3064 | 506930.04 | 229949.0987 | 0 | 392870.781
3327 | 996.949 | 230.5336 | 230.5336 | 224.4154 | 224.4154 | 1807 | 422551.6099 | 80789.5406 | 36647.0333 | 1416054.1061 | 42395.924
3328 | 1328.349 | 560.5879 | 560.5879 | 545.7102 | 545.7102 | 1807.65 | 1027752.8252 | 196455.6611 | 89114.4707 | 1434576.976 | 102747.0224
3329 | 1340.192 | 1115.6285 | 1115.6285 | 1086.0203 | 1086.0203 | 1788 | 2022406.4448 | 390967.3232 | 177347.1219 | 465896.6489 | 225366.176
3330 | 1479.054 | 201.8917 | 201.8917 | 196.5336 | 196.5336 | 1701.6 | 349385.9942 | 70752.0986 | 32093.938 | 2350859.8802 | 57405.2968
3331 | 1458.236 | 0 | 0 | 0 | 0 | 1654.85 | 0 | 0 | 0 | 4955085.928 | 0
3332 | 1057.6 | 0 | 0 | 0 | 0 | 1752.65 | 0 | 0 | 0 | 3593724.8 | 0
3333 | 1518.4 | 0 | 0 | 0 | 0 | 1754.75 | 0 | 0 | 0 | 5159523.2 | 0
3334 | 1292 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1839.85 | 594520.9014 | 111351.8261 | 50510.4255 | 3339178.4863 | 48985.7211
3335 | 1396.8 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1831.95 | 1146066.6175 | 215514.4963 | 97759.7701 | 2712109.0159 | 99485.6
3336 | 0 | 0 | 0 | 0 | 0 | 1745.05 | 0 | 0 | 0 | 0 | 0
3337 | 0 | 0 | 0 | 0 | 0 | 1641.3 | 0 | 0 | 0 | 0 | 0
3338 | 0 | 0 | 0 | 0 | 0 | 1707.95 | 0 | 0 | 0 | 0 | 0
3339 | 0 | 0 | 0 | 0 | 0 | 1700.55 | 0 | 0 | 0 | 0 | 0
3340 | 0 | 0 | 0 | 0 | 0 | 1694.85 | 0 | 0 | 0 | 0 | 0
3341 | 0 | 0 | 0 | 0 | 0 | 1690.8 | 0 | 0 | 0 | 0 | 0
3342 | 0 | 0 | 0 | 0 | 0 | 1636.15 | 0 | 0 | 0 | 0 | 0
3343 | 1413.981 | 468.8386 | 468.8386 | 456.3958 | 456.3958 | 1678.7 | 800673.9429 | 164302.5 | 74529.4396 | 1755253.6103 | 143537.8833
3344 | 1218.646 | 1265.9353 | 1265.9353 | 1232.338 | 1218.646 | 1231.2 | 1568203.5642 | 438712.56 | 199004.8918 | 0 | 936895.0448
3345 | 1283.48 | 1987.0164 | 1333.2851 | 1934.282 | 1283.48 | 669.2 | 898003.6632 | 462052.8 | 209592.284 | 0 | 1708055.184
3346 | 1235.312 | 3235.6431 | 1283.248 | 3149.7709 | 1235.312 | 1059.65 | 1367415.9127 | 444712.32 | 201726.4496 | 0 | 1161625.6392
3347 | 1227.421 | 3029.0383 | 1275.0508 | 2948.6493 | 1227.421 | 694.3 | 888541.3447 | 441871.56 | 200437.8493 | 0 | 1602643.5997
3348 | 1268.221 | 3998.1008 | 1317.434 | 3891.9934 | 1268.221 | 1074.35 | 1424575.1718 | 456559.56 | 207100.4893 | 0 | 1173928.7686
3349 | 1361.861 | 1792.1782 | 1414.7077 | 1744.6147 | 1361.861 | 1075.95 | 1532706.7569 | 490269.96 | 222391.9013 | 0 | 1258427.6571
3350 | 1362.378 | 2759.1527 | 1415.2447 | 2685.9263 | 1362.378 | 1088.35 | 1552148.1934 | 490456.08 | 222476.3274 | 0 | 1242011.9037
3351 | 1092.7 | 568.4599 | 568.4599 | 553.3733 | 553.3733 | 1092.55 | 629419.1438 | 199214.3922 | 90365.8618 | 988585.8195 | 491535.7192
3352 | 1161.964 | 132.6865 | 132.6865 | 129.1651 | 129.1651 | 1365.5 | 184210.5016 | 46499.4368 | 21092.6612 | 1893120.3794 | 80221.7385
3353 | 1302.91 | 383.4696 | 383.4696 | 373.2925 | 373.2925 | 1226.7 | 478314.5075 | 134385.3019 | 60958.6661 | 1703988.8679 | 282560.7268
3354 | 1031.53 | 123.5617 | 123.5617 | 120.2824 | 120.2824 | 1371.4 | 172002.4781 | 43301.6677 | 19642.1176 | 1670316.832 | 74010.1068
3355 | 1155.338 | 0 | 0 | 0 | 0 | 1706.1 | 0 | 0 | 0 | 3925838.524 | 0
3356 | 992.8 | 0 | 0 | 0 | 0 | 1736.85 | 0 | 0 | 0 | 3373534.4 | 0
3357 | 1484 | 0 | 0 | 0 | 0 | 1738.5 | 0 | 0 | 0 | 5042632 | 0
3358 | 1380 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1760.4 | 568484.1034 | 111351.8261 | 50510.4255 | 3638202.4863 | 73287.4104
3359 | 799.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1747.65 | 1092890.458 | 215514.4963 | 97759.7701 | 681464.2159 | 149391.2
3360 | 0 | 0 | 0 | 0 | 0 | 1672.4 | 0 | 0 | 0 | 0 | 0
3361 | 0 | 0 | 0 | 0 | 0 | 1592.7 | 0 | 0 | 0 | 0 | 0
3362 | 0 | 0 | 0 | 0 | 0 | 1712.15 | 0 | 0 | 0 | 0 | 0
3363 | 0 | 0 | 0 | 0 | 0 | 1583.4 | 0 | 0 | 0 | 0 | 0
3364 | 0 | 0 | 0 | 0 | 0 | 1547.75 | 0 | 0 | 0 | 0 | 0
3365 | 0 | 0 | 0 | 0 | 0 | 1012.45 | 0 | 0 | 0 | 0 | 0
3366 | 0 | 0 | 0 | 0 | 0 | 1012.75 | 0 | 0 | 0 | 0 | 0
3367 | 1303.011 | 474.2383 | 474.2383 | 461.6522 | 461.6522 | 1062.2 | 507340.3894 | 166194.8047 | 75387.81 | 1542210.6158 | 423778.6908
3368 | 993.966 | 1032.5366 | 1032.5366 | 1005.1336 | 993.966 | 998.2 | 1029379.5093 | 357827.76 | 162314.6478 | 0 | 995755.1388
3369 | 1093.9 | 2100.4663 | 1136.3485 | 2044.7211 | 1093.9 | 1772.35 | 2013377.9794 | 393804 | 178633.87 | 0 | 249026.335
3370 | 1363.693 | 3323.6735 | 1416.6108 | 3235.465 | 1363.693 | 1777.05 | 2522963.8656 | 490929.48 | 222691.0669 | 0 | 304035.3544
3371 | 1239.039 | 3823.0695 | 1287.1196 | 3721.6073 | 1239.039 | 1471.2 | 1911007.8792 | 446054.04 | 202335.0687 | 0 | 655203.8232
3372 | 1503.503 | 4051.646 | 1561.8461 | 3944.1175 | 1503.503 | 1106.65 | 1751045.2782 | 541261.08 | 245522.0399 | 0 | 1343154.405
3373 | 1361.769 | 4011.1347 | 1414.6121 | 3904.6814 | 1361.769 | 1059 | 1512243.3101 | 490236.84 | 222376.8777 | 0 | 1281424.629
3374 | 1532.198 | 3669.5663 | 1591.6546 | 3572.1781 | 1532.198 | 1311.6 | 2098385.0114 | 551591.28 | 250207.9334 | 0 | 1054765.1032
3375 | 1256.603 | 3084.7899 | 1305.3652 | 3002.9213 | 1256.603 | 1750.75 | 2297836.1193 | 452377.08 | 205203.2699 | 0 | 313208.2977
3376 | 1138.22 | 2262.0752 | 1182.3883 | 2202.041 | 1138.22 | 1836.15 | 2183483.3422 | 409759.2 | 185871.326 | 0 | 186497.347
3377 | 1339.573 | 548.0443 | 548.0443 | 533.4995 | 533.4995 | 1844.25 | 1028231.5471 | 192059.8206 | 87120.4686 | 1477532.7223 | 81334.8305
3378 | 1110.796 | 55.9054 | 55.9054 | 54.4217 | 54.4217 | 1786.15 | 101779.925 | 19591.7967 | 8887.0567 | 1936334.1698 | 11391.7895
3379 | 989.602 | 0 | 0 | 0 | 0 | 1813.9 | 0 | 0 | 0 | 3362667.596 | 0
3380 | 1045.6 | 0 | 0 | 0 | 0 | 1819.2 | 0 | 0 | 0 | 3552948.8 | 0
3381 | 1416.8 | 0 | 0 | 0 | 0 | 1760.95 | 0 | 0 | 0 | 4814286.4 | 0
3382 | 1268 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1832.8 | 591273.0937 | 111351.8261 | 50510.4255 | 3257626.4863 | 51142.1328
3383 | 1352.8 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1773.25 | 1107694.8482 | 215514.4963 | 97759.7701 | 2562597.0159 | 134236
3384 | 0 | 0 | 0 | 0 | 0 | 1677.6 | 0 | 0 | 0 | 0 | 0
3385 | 0 | 0 | 0 | 0 | 0 | 1503.4 | 0 | 0 | 0 | 0 | 0
3386 | 0 | 0 | 0 | 0 | 0 | 1398.85 | 0 | 0 | 0 | 0 | 0
3387 | 0 | 0 | 0 | 0 | 0 | 1437.75 | 0 | 0 | 0 | 0 | 0
3388 | 0 | 0 | 0 | 0 | 0 | 1432.8 | 0 | 0 | 0 | 0 | 0
3389 | 0 | 0 | 0 | 0 | 0 | 1428.95 | 0 | 0 | 0 | 0 | 0
3390 | 0 | 0 | 0 | 0 | 0 | 1508.25 | 0 | 0 | 0 | 0 | 0
3391 | 1304.669 | 454.4199 | 454.4199 | 442.3599 | 442.3599 | 1595.55 | 735464.3928 | 159249.5588 | 72237.3693 | 1580612.6067 | 175127.6589
3392 | 935.942 | 972.261 | 972.261 | 946.4577 | 935.942 | 1676 | 1633093.0021 | 336939.12 | 152839.3286 | 0 | 303245.208
3393 | 898.574 | 1387.6676 | 933.4429 | 1350.8396 | 898.574 | 1780.7 | 1670821.7485 | 323486.64 | 146737.1342 | 0 | 197057.2782
3394 | 1261.705 | 2334.9921 | 1310.6662 | 2273.0227 | 1261.705 | 1797.05 | 2379140.4762 | 454213.8 | 206036.4265 | 0 | 256063.0298
3395 | 1281.246 | 2692.9102 | 1330.9644 | 2621.4418 | 1281.246 | 1418.7 | 1914575.4643 | 461248.56 | 209227.4718 | 0 | 744788.2998
3396 | 1130.342 | 2572.7495 | 1174.2046 | 2504.4702 | 1130.342 | 1106.65 | 1319590.4929 | 406923.12 | 184584.8486 | 0 | 1009791.0257
3397 | 1247.462 | 2875.6172 | 1295.8694 | 2799.2999 | 1247.462 | 1059 | 1383427.4134 | 449086.32 | 203710.5446 | 0 | 1173861.742
3398 | 1339.387 | 1746.1851 | 1391.3616 | 1699.8423 | 1339.387 | 1357 | 1901494.2978 | 482179.32 | 218721.8971 | 0 | 861225.841
3399 | 1391.303 | 1537.0664 | 1445.2922 | 1496.2735 | 1391.303 | 1679.65 | 2445162.4222 | 500869.08 | 227199.7799 | 0 | 445703.916
3400 | 1345.155 | 1835.5992 | 1397.3534 | 1786.8834 | 1345.155 | 1827.8 | 2567421.2436 | 484255.8 | 219663.8115 | 0 | 231635.691
3401 | 1198.38 | 984.5802 | 984.5802 | 958.45 | 958.45 | 1844.25 | 1843377.2465 | 345041.9849 | 156514.8782 | 439791.7669 | 146120.912
3402 | 1181.647 | 234.425 | 234.425 | 228.2035 | 228.2035 | 1822.65 | 435244.892 | 82153.2523 | 37265.628 | 1747661.9749 | 39615.7336
3403 | 1283.014 | 0 | 0 | 0 | 0 | 1776.55 | 0 | 0 | 0 | 4359681.572 | 0
3404 | 1180.8 | 0 | 0 | 0 | 0 | 1790.7 | 0 | 0 | 0 | 4012358.4 | 0
3405 | 1619.2 | 0 | 0 | 0 | 0 | 1824.25 | 0 | 0 | 0 | 5502041.6 | 0
3406 | 1483.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1876 | 604895.2007 | 111351.8261 | 50510.4255 | 3988876.0863 | 37928.376
3407 | 1326.4 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1865.25 | 1163803.6211 | 215514.4963 | 97759.7701 | 2472889.8159 | 79772
3408 | 0 | 0 | 0 | 0 | 0 | 1847.5 | 0 | 0 | 0 | 0 | 0
3409 | 0 | 0 | 0 | 0 | 0 | 1654.1 | 0 | 0 | 0 | 0 | 0
3410 | 0 | 0 | 0 | 0 | 0 | 1700.5 | 0 | 0 | 0 | 0 | 0
3411 | 0 | 0 | 0 | 0 | 0 | 1704.55 | 0 | 0 | 0 | 0 | 0
3412 | 0 | 0 | 0 | 0 | 0 | 1675.8 | 0 | 0 | 0 | 0 | 0
3413 | 0 | 0 | 0 | 0 | 0 | 1672.45 | 0 | 0 | 0 | 0 | 0
3414 | 0 | 0 | 0 | 0 | 0 | 1696.05 | 0 | 0 | 0 | 0 | 0
3415 | 619.025 | 319.4034 | 319.4034 | 310.9266 | 310.9266 | 1608.35 | 520781.5149 | 111933.5696 | 50774.3109 | 564744.3999 | 119198.2859
3416 | 887.264 | 921.6941 | 921.6941 | 897.2328 | 887.264 | 1273.55 | 1176368.2377 | 319415.04 | 144890.2112 | 0 | 644552.9328
3417 | 690.747 | 1963.3545 | 717.5513 | 1911.2481 | 690.747 | 1705.7 | 1229095.0704 | 248668.92 | 112798.9851 | 0 | 203286.8421
3418 | 307.348 | 2903.0687 | 319.2746 | 2826.0228 | 307.348 | 1726.65 | 556308.3457 | 110645.28 | 50189.9284 | 0 | 84013.5758
3419 | 235.767 | 3780.3414 | 244.9159 | 3680.0132 | 235.767 | 1296.35 | 321343.4436 | 84876.12 | 38500.7511 | 0 | 165897.4495
3420 | 197.082 | 3981.8072 | 204.7297 | 3876.1322 | 197.082 | 721.7 | 149434.7177 | 70949.52 | 32183.4906 | 0 | 251929.9206
3421 | 683.53 | 3346.4015 | 710.0542 | 3257.5898 | 683.53 | 378.9 | 270197.325 | 246070.8 | 111620.449 | 0 | 1108070.483
3422 | 1150.936 | 3164.0372 | 1195.5978 | 3080.0654 | 1150.936 | 1081.15 | 1297667.0666 | 414336.96 | 187947.8488 | 0 | 1057537.5436
3423 | 1786.232 | 359.0805 | 359.0805 | 349.5507 | 349.5507 | 1595.55 | 581576.5855 | 125838.2591 | 57081.6325 | 2633436.7868 | 138384.9942
3424 | 1729.544 | 295.8474 | 295.8474 | 287.9958 | 287.9958 | 1836.15 | 551361.1452 | 103678.4907 | 47029.7153 | 2642357.837 | 46189.9704
3425 | 1610.063 | 1036.0852 | 1036.0852 | 1008.588 | 1008.588 | 1864.2 | 1960727.5491 | 363091.688 | 164702.424 | 1102503.6342 | 134068.9574
3426 | 1527.327 | 198.285 | 198.285 | 193.0226 | 193.0226 | 1826.6 | 368678.8703 | 69488.1352 | 31520.5902 | 2445779.9695 | 32762.0226
3427 | 1637.6 | 0 | 0 | 0 | 0 | 1768.2 | 0 | 0 | 0 | 5564564.8 | 0
3428 | 1442.4 | 0 | 0 | 0 | 0 | 1790.7 | 0 | 0 | 0 | 4901275.2 | 0
3429 | 1472.8 | 0 | 0 | 0 | 0 | 1822.7 | 0 | 0 | 0 | 5004574.4 | 0
3430 | 1553.6 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1873.6 | 604098.5732 | 111351.8261 | 50510.4255 | 4228095.2863 | 38662.4736
3431 | 1444 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1781.25 | 1111553.5147 | 215514.4963 | 97759.7701 | 2872494.6159 | 129500
3432 | 0 | 0 | 0 | 0 | 0 | 1697.6 | 0 | 0 | 0 | 0 | 0
3433 | 0 | 0 | 0 | 0 | 0 | 1475.95 | 0 | 0 | 0 | 0 | 0
3434 | 0 | 0 | 0 | 0 | 0 | 1570.65 | 0 | 0 | 0 | 0 | 0
3435 | 0 | 0 | 0 | 0 | 0 | 1583.4 | 0 | 0 | 0 | 0 | 0
3436 | 0 | 0 | 0 | 0 | 0 | 1598.3 | 0 | 0 | 0 | 0 | 0
3437 | 0 | 0 | 0 | 0 | 0 | 1594.95 | 0 | 0 | 0 | 0 | 0
3438 | 0 | 0 | 0 | 0 | 0 | 1574.9 | 0 | 0 | 0 | 0 | 0
3439 | 1362.282 | 465.9704 | 465.9704 | 453.6038 | 453.6038 | 1579.45 | 751957.1881 | 163297.3725 | 74073.5026 | 1665607.1179 | 186727.5644
3440 | 1064.339 | 1105.6404 | 1105.6404 | 1076.2973 | 1064.339 | 1227.55 | 1374024.9168 | 383162.04 | 173806.5587 | 0 | 822148.6606
3441 | 1658.966 | 2013.7365 | 1723.3418 | 1960.293 | 1658.966 | 1511.75 | 2630164.3457 | 597227.76 | 270909.1478 | 0 | 809990.1495
3442 | 1820.422 | 3321.1076 | 1891.063 | 3232.9672 | 1820.422 | 1584.8 | 3031752.9123 | 655351.92 | 297274.9126 | 0 | 755839.2144
3443 | 1766.438 | 3772.4994 | 1834.9842 | 3672.3794 | 1766.438 | 1085.35 | 2025174.0074 | 635917.68 | 288459.3254 | 0 | 1615672.5167
3444 | 1632.862 | 3988.2592 | 1696.2248 | 3882.413 | 1632.862 | 381.65 | 656025.3364 | 587830.32 | 266646.3646 | 0 | 2642542.2177
3445 | 1633.953 | 3006.9138 | 1697.3581 | 2927.112 | 1633.953 | 378.9 | 649726.9505 | 588223.08 | 266824.5249 | 0 | 2648801.2083
3446 | 1730.896 | 2815.0757 | 1798.063 | 2740.3651 | 1730.896 | 1311.6 | 2392257.9754 | 623122.56 | 282655.3168 | 0 | 1191548.8064
3447 | 1836.767 | 2656.8585 | 1908.0423 | 2586.3469 | 1836.767 | 1690.15 | 3271858.4746 | 661236.12 | 299944.0511 | 0 | 569122.2549
3448 | 1998.015 | 1593.113 | 1593.113 | 1550.8327 | 1550.8327 | 1807.8 | 2950133.1821 | 558299.7677 | 253250.978 | 819685.1778 | 291764.9816
3449 | 1627.268 | 124.2587 | 124.2587 | 120.9609 | 120.9609 | 1906.2 | 242320.2176 | 43545.9417 | 19752.923 | 2761060.8241 | 11106.2014
3450 | 1652.685 | 236.4538 | 236.4538 | 230.1784 | 230.1784 | 1826.6 | 441950.0116 | 82864.2317 | 37588.1362 | 2607454.5587 | 39068.5806
3451 | 1494.002 | 0 | 0 | 0 | 0 | 1776.55 | 0 | 0 | 0 | 5076618.796 | 0
3452 | 1398.4 | 0 | 0 | 0 | 0 | 1832.7 | 0 | 0 | 0 | 4751763.2 | 0
3453 | 1210.4 | 0 | 0 | 0 | 0 | 1752.6 | 0 | 0 | 0 | 4112939.2 | 0
3454 | 1628 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1832.8 | 593663.5514 | 111351.8261 | 50510.4255 | 4480906.4863 | 51142.1328
3455 | 1786.4 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1772.9 | 1112712.1504 | 215514.4963 | 97759.7701 | 4035969.8159 | 134443.2
3456 | 0 | 0 | 0 | 0 | 0 | 1697.6 | 0 | 0 | 0 | 0 | 0
3457 | 0 | 0 | 0 | 0 | 0 | 1624.8 | 0 | 0 | 0 | 0 | 0
3458 | 0 | 0 | 0 | 0 | 0 | 1560.8 | 0 | 0 | 0 | 0 | 0
3459 | 0 | 0 | 0 | 0 | 0 | 1391.25 | 0 | 0 | 0 | 0 | 0
3460 | 0 | 0 | 0 | 0 | 0 | 1537.9 | 0 | 0 | 0 | 0 | 0
3461 | 0 | 0 | 0 | 0 | 0 | 1554.25 | 0 | 0 | 0 | 0 | 0
3462 | 0 | 0 | 0 | 0 | 0 | 1554.55 | 0 | 0 | 0 | 0 | 0
3463 | 1177.554 | 439.0321 | 439.0321 | 427.3805 | 427.3805 | 1310.65 | 587079.3093 | 153856.9638 | 69791.2283 | 1375068.1079 | 288382.679
3464 | 1356.489 | 1265.9217 | 1265.9217 | 1232.3249 | 1232.3249 | 318.1 | 410433.7529 | 443636.9546 | 201238.6519 | 227592.8433 | 2028803.6483
3465 | 1166.426 | 1397.0823 | 1211.6889 | 1360.0045 | 1166.426 | 363.7 | 445393.1824 | 419913.36 | 190477.3658 | 0 | 1908622.8638
3466 | 975.268 | 2266.3053 | 1013.113 | 2206.1588 | 975.268 | 380.4 | 390066.4279 | 351096.48 | 159261.2644 | 0 | 1579544.0528
3467 | 1314.143 | 2946.7452 | 1365.138 | 2868.5402 | 1314.143 | 385.8 | 534046.2344 | 473091.48 | 214599.5519 | 0 | 2121289.6306
3468 | 1169.049 | 3330.032 | 1214.4137 | 3241.6547 | 1169.049 | 381.65 | 468857.9882 | 420857.64 | 190905.7017 | 0 | 1891930.4492
3469 | 1078.088 | 3915.9376 | 1119.9229 | 3812.0107 | 1078.088 | 378.9 | 428416.4437 | 388111.68 | 176051.7704 | 0 | 1747688.4568
3470 | 944.397 | 2791.2954 | 981.0441 | 2717.2159 | 944.397 | 401.05 | 398871.3527 | 339982.92 | 154220.0301 | 0 | 1510043.5832
3471 | 1126.43 | 2376.5058 | 1170.1408 | 2313.4347 | 1126.43 | 412.85 | 489194.9286 | 405514.8 | 183946.019 | 0 | 1787813.3745
3472 | 898.155 | 925.9023 | 925.9023 | 901.3293 | 898.155 | 863.15 | 813746.047 | 323335.8 | 146668.7115 | 0 | 1003000.6915
3473 | 1152.652 | 352.8415 | 352.8415 | 343.4772 | 343.4772 | 1724.3 | 621171.9432 | 123651.8063 | 56089.8332 | 1483217.3357 | 92693.3727
3474 | 869.487 | 23.2952 | 23.2952 | 22.677 | 22.677 | 1765.8 | 42083.3977 | 8163.7037 | 3703.1467 | 1552202.8131 | 5198.5374
3475 | 1185.808 | 0 | 0 | 0 | 0 | 1706.15 | 0 | 0 | 0 | 2173586.064 | 0
3476 | 980.8 | 0 | 0 | 0 | 0 | 1774 | 0 | 0 | 0 | 1797806.4 | 0
3477 | 808.8 | 0 | 0 | 0 | 0 | 1773.55 | 0 | 0 | 0 | 1482530.4 | 0
3478 | 850.4 | 0 | 0 | 0 | 0 | 1874.8 | 0 | 0 | 0 | 1558783.2 | 0
3479 | 840 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1813.7 | 589666.3348 | 111351.8261 | 50510.4255 | 972753.619 | 56984.3262
3480 | 0 | 0 | 0 | 0 | 0 | 1748 | 0 | 0 | 0 | 0 | 0
3481 | 0 | 0 | 0 | 0 | 0 | 1611 | 0 | 0 | 0 | 0 | 0
3482 | 0 | 0 | 0 | 0 | 0 | 1591.95 | 0 | 0 | 0 | 0 | 0
3483 | 0 | 0 | 0 | 0 | 0 | 1554.15 | 0 | 0 | 0 | 0 | 0
3484 | 0 | 0 | 0 | 0 | 0 | 1516.1 | 0 | 0 | 0 | 0 | 0
3485 | 0 | 0 | 0 | 0 | 0 | 1513.85 | 0 | 0 | 0 | 0 | 0
3486 | 0 | 0 | 0 | 0 | 0 | 1538.45 | 0 | 0 | 0 | 0 | 0
3487 | 1097.92 | 1084.3667 | 1084.3667 | 1055.5882 | 1055.5882 | 1236.85 | 1366627.4535 | 380011.7602 | 172377.5568 | 77594.1475 | 793119.6637
3488 | 961.001 | 998.2924 | 998.2924 | 971.7983 | 961.001 | 312.9 | 315245.6661 | 345960.36 | 156931.4633 | 0 | 1621304.7871
3489 | 988.449 | 2033.8301 | 1026.8066 | 1979.8534 | 988.449 | 353.45 | 365696.1192 | 355841.64 | 161413.7217 | 0 | 1627530.7009
3490 | 1114.766 | 3244.7991 | 1158.0242 | 3158.6839 | 1114.766 | 369.4 | 432587.0528 | 401315.76 | 182041.2878 | 0 | 1817737.4396
3491 | 1334.239 | 3710.0351 | 1386.0138 | 3611.5728 | 1334.239 | 375.6 | 528921.4842 | 480326.04 | 217881.2287 | 0 | 2167337.8316
3492 | 1375.817 | 3933.5609 | 1429.2052 | 3829.1664 | 1375.817 | 371.35 | 538506.8106 | 495294.12 | 224670.9161 | 0 | 2240724.3571
3493 | 1313.727 | 3892.3349 | 1364.7058 | 3789.0345 | 1313.727 | 371.45 | 512105.5047 | 472941.72 | 214531.6191 | 0 | 2139470.1058
3494 | 1220.12 | 3028.1574 | 1267.4664 | 2947.7917 | 1220.12 | 395.1 | 505597.7648 | 439243.2 | 199245.596 | 0 | 1958170.588
3495 | 1436.12 | 3055.9766 | 1491.8483 | 2974.8726 | 1436.12 | 403.35 | 608056.805 | 517003.2 | 234518.396 | 0 | 2292980.998
3496 | 1317.272 | 1884.8094 | 1368.3884 | 1834.7876 | 1317.272 | 399 | 551394.5568 | 474217.92 | 215110.5176 | 0 | 2108952.472
3497 | 1561.218 | 1177.0697 | 1177.0697 | 1145.8309 | 1145.8309 | 1347.15 | 1617640.0331 | 412499.1144 | 187114.1816 | 761404.6034 | 732231.3372
3498 | 1522.874 | 218.6165 | 218.6165 | 212.8145 | 212.8145 | 732.85 | 163783.7429 | 76613.2191 | 34752.6075 | 2401339.0678 | 263963.8179
3499 | 1531.013 | 0 | 0 | 0 | 0 | 907.25 | 0 | 0 | 0 | 5202382.174 | 0
3500 | 820.8 | 0 | 0 | 0 | 0 | 1366.9 | 0 | 0 | 0 | 2789078.4 | 0
3501 | 1276 | 0 | 0 | 0 | 0 | 1389.35 | 0 | 0 | 0 | 4335848 | 0
3502 | 1128 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1761.5 | 573653.9395 | 111351.8261 | 50510.4255 | 2781906.4863 | 72950.949
3503 | 905.6 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1753.6 | 1106538.4909 | 215514.4963 | 97759.7701 | 1043011.4159 | 145868.8
3504 | 0 | 0 | 0 | 0 | 0 | 1660.95 | 0 | 0 | 0 | 0 | 0
3505 | 0 | 0 | 0 | 0 | 0 | 1325.4 | 0 | 0 | 0 | 0 | 0
3506 | 0 | 0 | 0 | 0 | 0 | 1502.7 | 0 | 0 | 0 | 0 | 0
3507 | 0 | 0 | 0 | 0 | 0 | 791.75 | 0 | 0 | 0 | 0 | 0
3508 | 0 | 0 | 0 | 0 | 0 | 286.55 | 0 | 0 | 0 | 0 | 0
3509 | 0 | 0 | 0 | 0 | 0 | 282.5 | 0 | 0 | 0 | 0 | 0
3510 | 0 | 0 | 0 | 0 | 0 | 278.25 | 0 | 0 | 0 | 0 | 0
3511 | 803.82 | 461.4693 | 461.4693 | 449.2221 | 449.2221 | 270.4 | 127373.8708 | 161719.9665 | 73357.9737 | 649977.8971 | 760539.712
3512 | 740.237 | 970.0442 | 768.9617 | 944.2997 | 740.237 | 274.45 | 212847.9537 | 266485.32 | 120880.7021 | 0 | 1277315.9553
3513 | 558.473 | 2174.2485 | 580.1444 | 2116.5451 | 558.473 | 291.95 | 171085.9343 | 201050.28 | 91198.6409 | 0 | 953899.8077
3514 | 1199.225 | 3316.0092 | 1245.7606 | 3228.0041 | 1199.225 | 305.15 | 385282.3379 | 431721 | 195833.4425 | 0 | 2032506.4912
3515 | 1228.803 | 3798.2078 | 1276.4864 | 3697.4054 | 1228.803 | 317.05 | 409279.0906 | 442369.08 | 200663.5299 | 0 | 2068014.0089
3516 | 1419.01 | 3999.5084 | 1474.0743 | 3893.3636 | 1419.01 | 319.85 | 477768.6089 | 510843.6 | 231724.333 | 0 | 2384149.6515
3517 | 1282.017 | 3947.0446 | 1331.7653 | 3842.2922 | 1282.017 | 321.45 | 434085.3037 | 461526.12 | 209353.3761 | 0 | 2151929.6354
3518 | 1153.519 | 3620.4143 | 1198.281 | 3524.3304 | 1153.519 | 333.85 | 404796.7759 | 415266.84 | 188369.6527 | 0 | 1921935.6819
3519 | 1350.247 | 3052.5049 | 1402.643 | 2971.4931 | 1350.247 | 338.05 | 477680.3571 | 486088.92 | 220495.3351 | 0 | 2244043.0016
3520 | 1241.158 | 2250.2537 | 1289.3208 | 2190.5331 | 1241.158 | 334.5 | 434123.0927 | 446816.88 | 202681.1014 | 0 | 2067148.649
3521 | 1171.973 | 797.2723 | 797.2723 | 776.1131 | 776.1131 | 324.95 | 264537.5597 | 279400.7107 | 126739.2668 | 725611.2237 | 1272528.7848
3522 | 1371.137 | 194.3936 | 194.3936 | 189.2345 | 189.2345 | 315.85 | 62556.3775 | 68124.4235 | 30901.9954 | 2166427.2647 | 311956.7887
3523 | 1506.995 | 0 | 0 | 0 | 0 | 318.4 | 0 | 0 | 0 | 5120769.01 | 0
3524 | 1457.6 | 0 | 0 | 0 | 0 | 1431.35 | 0 | 0 | 0 | 4952924.8 | 0
3525 | 1496 | 0 | 0 | 0 | 0 | 1433.35 | 0 | 0 | 0 | 5083408 | 0
3526 | 1008.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1688.65 | 548645.7644 | 111351.8261 | 50510.4255 | 2376864.8863 | 95233.8699
3527 | 940.8 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1738.95 | 1092072.2938 | 215514.4963 | 97759.7701 | 1162621.0159 | 154541.6
3528 | 0 | 0 | 0 | 0 | 0 | 1672.4 | 0 | 0 | 0 | 0 | 0
3529 | 0 | 0 | 0 | 0 | 0 | 1411.4 | 0 | 0 | 0 | 0 | 0
3530 | 0 | 0 | 0 | 0 | 0 | 303.85 | 0 | 0 | 0 | 0 | 0
3531 | 0 | 0 | 0 | 0 | 0 | 296.25 | 0 | 0 | 0 | 0 | 0
3532 | 0 | 0 | 0 | 0 | 0 | 290.8 | 0 | 0 | 0 | 0 | 0
3533 | 0 | 0 | 0 | 0 | 0 | 287.45 | 0 | 0 | 0 | 0 | 0
3534 | 0 | 0 | 0 | 0 | 0 | 287.75 | 0 | 0 | 0 | 0 | 0
3535 | 1415.654 | 461.0849 | 461.0849 | 448.848 | 448.848 | 292.3 | 137607.4881 | 161585.27 | 73296.8738 | 1772155.4491 | 750283.1181
3536 | 996.848 | 1035.5304 | 1035.5304 | 1008.048 | 996.848 | 318.1 | 331012.0672 | 358865.28 | 162785.2784 | 0 | 1676598.6512
3537 | 1420.083 | 2005.0479 | 1475.189 | 1951.8351 | 1420.083 | 363.7 | 541014.4627 | 511229.88 | 231899.5539 | 0 | 2323681.8129
3538 | 1718.45 | 3240.3395 | 1785.134 | 3154.3427 | 1718.45 | 380.4 | 687374.9935 | 618642 | 280622.885 | 0 | 2783201.62
3539 | 1514.737 | 2754.5934 | 1573.516 | 2681.488 | 1514.737 | 385.8 | 614901.9701 | 545305.32 | 247356.5521 | 0 | 2445088.4654
3540 | 1481.469 | 3254.3976 | 1538.957 | 3168.0277 | 1481.469 | 381.65 | 594754.8623 | 533328.84 | 241923.8877 | 0 | 2397535.3561
3541 | 1629.559 | 3285.2688 | 1692.7936 | 3198.0796 | 1629.559 | 378.9 | 647385.9191 | 586641.24 | 266106.9847 | 0 | 2641678.0949
3542 | 1581.445 | 3039.2757 | 1642.8126 | 2958.615 | 1581.445 | 1054.8 | 1749632.2051 | 569320.2 | 258249.9685 | 0 | 1494781.814
3543 | 1376.542 | 1669.085 | 1429.9584 | 1624.7884 | 1376.542 | 1666.1 | 2404219.8222 | 495555.12 | 224789.3086 | 0 | 459627.3738
3544 | 1606.679 | 981.0555 | 981.0555 | 955.0188 | 955.0188 | 1798.5 | 1803428.1068 | 343806.781 | 155954.576 | 1194493.0802 | 188365.6255
3545 | 1530.064 | 372.7481 | 372.7481 | 362.8555 | 362.8555 | 1864.2 | 710235.9266 | 130627.996 | 59254.3104 | 2139493.0993 | 48233.3082
3546 | 1776.413 | 98.4382 | 98.4382 | 95.8257 | 95.8257 | 1821.95 | 183658.2823 | 34497.2452 | 15648.3337 | 3080516.5553 | 16700.9119
3547 | 1785.434 | 0 | 0 | 0 | 0 | 1584.65 | 0 | 0 | 0 | 6066904.732 | 0
3548 | 1460 | 0 | 0 | 0 | 0 | 1672.45 | 0 | 0 | 0 | 4961080 | 0
3549 | 1711.2 | 0 | 0 | 0 | 0 | 1823.9 | 0 | 0 | 0 | 5814657.6 | 0
3550 | 1587.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1876 | 608303.2508 | 111351.8261 | 50510.4255 | 4342268.0863 | 37928.376
3551 | 1569.6 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1865.25 | 1172495.9191 | 215514.4963 | 97759.7701 | 3299283.4159 | 79772
3552 | 0 | 0 | 0 | 0 | 0 | 1848.7 | 0 | 0 | 0 | 0 | 0
3553 | 0 | 0 | 0 | 0 | 0 | 1824.65 | 0 | 0 | 0 | 0 | 0
3554 | 0 | 0 | 0 | 0 | 0 | 1769.65 | 0 | 0 | 0 | 0 | 0
3555 | 0 | 0 | 0 | 0 | 0 | 1699.9 | 0 | 0 | 0 | 0 | 0
3556 | 0 | 0 | 0 | 0 | 0 | 1689.8 | 0 | 0 | 0 | 0 | 0
3557 | 0 | 0 | 0 | 0 | 0 | 1640.7 | 0 | 0 | 0 | 0 | 0
3558 | 0 | 0 | 0 | 0 | 0 | 1670.45 | 0 | 0 | 0 | 0 | 0
3559 | 1421.245 | 367.6029 | 367.6029 | 357.8469 | 357.8469 | 1562.3 | 585997.8393 | 128824.8823 | 58436.398 | 1949208.7261 | 153316.2429
3560 | 1472.409 | 1370.8774 | 1370.8774 | 1334.495 | 1334.495 | 1060.1 | 1479976.0018 | 480418.2166 | 217923.041 | 252796.2774 | 1227759.4134
3561 | 1472.679 | 1529.8259 | 1529.8259 | 1489.2252 | 1472.679 | 1402.95 | 2163310.7474 | 530164.44 | 240488.4807 | 0 | 879262.9969
3562 | 1255.664 | 2026.4234 | 1304.3887 | 1972.6433 | 1255.664 | 1679.4 | 2216166.4831 | 452039.04 | 205049.9312 | 0 | 402565.8784
3563 | 1306.374 | 2990.6628 | 1357.0675 | 2911.2922 | 1306.374 | 1326 | 1829170.7848 | 470294.64 | 213330.8742 | 0 | 880496.076
3564 | 1147.369 | 3090.2488 | 1191.8924 | 3008.2353 | 1147.369 | 752.65 | 910519.2606 | 413052.84 | 187365.3577 | 0 | 1431170.7222
3565 | 1451.78 | 2963.3931 | 1508.116 | 2884.7463 | 1451.78 | 378.9 | 577324.1731 | 522640.8 | 237075.674 | 0 | 2353480.558
3566 | 1625.359 | 619.2315 | 619.2315 | 602.7974 | 602.7974 | 1387.25 | 880340.4793 | 217007.0798 | 98436.8226 | 1874355.3326 | 361550.6865
3567 | 1496.668 | 246.3827 | 246.3827 | 239.8438 | 239.8438 | 1583.35 | 398519.7379 | 86343.7715 | 39166.4941 | 2303758.741 | 97817.3372
3568 | 1406.455 | 89.8691 | 89.8691 | 87.484 | 87.484 | 1777.4 | 162697.9694 | 31494.24 | 14286.1372 | 2417673.8428 | 19061.9058
3569 | 1189.61 | 419.4507 | 419.4507 | 408.3187 | 408.3187 | 1864.2 | 795457.0253 | 146994.7201 | 66678.4383 | 1432107.0133 | 54276.6798
3570 | 1307.693 | 198.1603 | 198.1603 | 192.9012 | 192.9012 | 1764.85 | 356649.3284 | 69444.4498 | 31500.774 | 2043413.2788 | 44401.2582
3571 | 1408 | 0 | 0 | 0 | 0 | 1797.4 | 0 | 0 | 0 | 4784384 | 0
3572 | 1389.6 | 0 | 0 | 0 | 0 | 1872.3 | 0 | 0 | 0 | 4721860.8 | 0
3573 | 1545.6 | 0 | 0 | 0 | 0 | 1832.25 | 0 | 0 | 0 | 5251948.8 | 0
3574 | 1364 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1876 | 602627.9184 | 111351.8261 | 50510.4255 | 3583834.4863 | 37928.376
3575 | 1421.6 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1865.25 | 1163199.2692 | 215514.4963 | 97759.7701 | 2796379.4159 | 79772
3576 | 0 | 0 | 0 | 0 | 0 | 1848.7 | 0 | 0 | 0 | 0 | 0
3577 | 0 | 0 | 0 | 0 | 0 | 1813.85 | 0 | 0 | 0 | 0 | 0
3578 | 0 | 0 | 0 | 0 | 0 | 1707.5 | 0 | 0 | 0 | 0 | 0
3579 | 0 | 0 | 0 | 0 | 0 | 1649.5 | 0 | 0 | 0 | 0 | 0
3580 | 0 | 0 | 0 | 0 | 0 | 1511.3 | 0 | 0 | 0 | 0 | 0
3581 | 0 | 0 | 0 | 0 | 0 | 1594.95 | 0 | 0 | 0 | 0 | 0
3582 | 0 | 0 | 0 | 0 | 0 | 1586.75 | 0 | 0 | 0 | 0 | 0
3583 | 1709.965 | 402.9804 | 402.9804 | 392.2855 | 392.2855 | 1595.55 | 654617.6723 | 141222.7905 | 64060.2269 | 2415306.4699 | 155303.5421
3584 | 1408.436 | 1157.1454 | 1157.1454 | 1126.4354 | 1126.4354 | 1339.6 | 1577152.7424 | 405516.7359 | 183946.8972 | 516907.1409 | 728161.6628
3585 | 1450.739 | 1507.0346 | 1507.0346 | 1467.0387 | 1450.739 | 1751.05 | 2652545.3576 | 522266.04 | 236905.6787 | 0 | 361161.474
3586 | 1655.173 | 1869.4808 | 1719.4016 | 1819.8658 | 1655.173 | 1788.7 | 3102660.4228 | 595862.28 | 270289.7509 | 0 | 349738.0549
3587 | 1645.765 | 2399.4478 | 1709.6285 | 2335.7678 | 1645.765 | 1784.8 | 3097591.8205 | 592475.4 | 268753.4245 | 0 | 354168.628
3588 | 1950.329 | 2939.8673 | 2026.011 | 2861.8448 | 1950.329 | 1564.35 | 3216192.0189 | 702118.44 | 318488.7257 | 0 | 849660.8289
3589 | 1604.172 | 2396.8321 | 1666.4215 | 2333.2215 | 1604.172 | 1166.6 | 1970565.9894 | 577501.92 | 261961.2876 | 0 | 1336916.9448
3590 | 1638.537 | 299.8042 | 299.8042 | 291.8476 | 291.8476 | 1853.85 | 566190.5044 | 105065.1371 | 47658.7136 | 2468481.6644 | 41751.2551
3591 | 1750.351 | 864.8133 | 864.8133 | 841.8616 | 841.8616 | 1920.65 | 1697037.274 | 303070.1727 | 137475.9978 | 1665261.0869 | 64211.9244
3592 | 1625.121 | 1688.1834 | 1688.1834 | 1643.3799 | 1625.121 | 1920.15 | 3271204.6997 | 585043.56 | 265382.2593 | 0 | 129765.9118
3593 | 1456.088 | 956.146 | 956.146 | 930.7704 | 930.7704 | 1907.4 | 1863039.3448 | 335077.3518 | 151994.8099 | 962907.121 | 84366.1006
3594 | 1657.048 | 235.7619 | 235.7619 | 229.5049 | 229.5049 | 1826.6 | 439955.3666 | 82621.7779 | 37478.1565 | 2616686.4317 | 38954.31
3595 | 1497.593 | 0 | 0 | 0 | 0 | 1776.55 | 0 | 0 | 0 | 5088821.014 | 0
3596 | 1270.4 | 0 | 0 | 0 | 0 | 1861.5 | 0 | 0 | 0 | 4316819.2 | 0
3597 | 1587.2 | 0 | 0 | 0 | 0 | 1873.05 | 0 | 0 | 0 | 5393305.6 | 0
3598 | 1514.4 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1876 | 606434.0194 | 111351.8261 | 50510.4255 | 4094893.6863 | 37928.376
3599 | 1600.8 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1865.25 | 1171581.5904 | 215514.4963 | 97759.7701 | 3405301.0159 | 79772
3600 | 0 | 0 | 0 | 0 | 0 | 1848.7 | 0 | 0 | 0 | 0 | 0
3601 | 0 | 0 | 0 | 0 | 0 | 1710.55 | 0 | 0 | 0 | 0 | 0
3602 | 0 | 0 | 0 | 0 | 0 | 1720.5 | 0 | 0 | 0 | 0 | 0
3603 | 0 | 0 | 0 | 0 | 0 | 1704.55 | 0 | 0 | 0 | 0 | 0
3604 | 0 | 0 | 0 | 0 | 0 | 1699.1 | 0 | 0 | 0 | 0 | 0
3605 | 0 | 0 | 0 | 0 | 0 | 1695.75 | 0 | 0 | 0 | 0 | 0
3606 | 0 | 0 | 0 | 0 | 0 | 1696.05 | 0 | 0 | 0 | 0 | 0
3607 | 1586.458 | 455.0173 | 455.0173 | 442.9413 | 442.9413 | 1361.75 | 632121.6094 | 159458.8845 | 72332.3218 | 2096066.0269 | 276727.329
3608 | 1339.324 | 1391.2961 | 1391.2961 | 1354.3719 | 1339.324 | 1062.1 | 1486981.4053 | 482156.64 | 218711.6092 | 0 | 1256151.9796
3609 | 1167.329 | 1873.3317 | 1212.6269 | 1823.6145 | 1167.329 | 1541.95 | 1883361.4969 | 420238.44 | 190624.8257 | 0 | 534695.0485
3610 | 1838.145 | 2850.6049 | 1909.4738 | 2774.9514 | 1838.145 | 1738.3 | 3359346.4401 | 661732.2 | 300169.0785 | 0 | 481042.5465
3611 | 1601.039 | 3563.2977 | 1663.1669 | 3468.7297 | 1601.039 | 1527.8 | 2582411.6764 | 576374.04 | 261449.6687 | 0 | 756010.6158
3612 | 1499.82 | 3782.8844 | 1558.0201 | 3682.4887 | 1499.82 | 1278.15 | 2017490.0045 | 539935.2 | 244920.606 | 0 | 1082645.067
3613 | 1916.994 | 3309.1842 | 1991.3825 | 3221.3603 | 1916.994 | 1166.6 | 2349022.0713 | 690117.84 | 313045.1202 | 0 | 1597622.7996
3614 | 1203.199 | 3190.3719 | 1249.8888 | 3105.7012 | 1203.199 | 1754.7 | 2223003.2393 | 433151.64 | 196482.3967 | 0 | 295144.7147
3615 | 1339.569 | 764.4554 | 764.4554 | 744.1671 | 744.1671 | 1821.15 | 1433488.5513 | 267900.1728 | 121522.495 | 1091371.5973 | 130278.9901
3616 | 1487.923 | 99.1248 | 99.1248 | 96.4941 | 96.4941 | 1819.45 | 185546.7678 | 34737.8788 | 15757.4878 | 2550489.1593 | 17053.4891
3617 | 1570.841 | 466.8929 | 466.8929 | 454.5018 | 454.5018 | 1874.75 | 897255.4004 | 163620.6442 | 74220.1422 | 2046249.7729 | 55722.0968
3618 | 1493.196 | 166.1714 | 166.1714 | 161.7613 | 161.7613 | 1727.05 | 293825.6028 | 58234.0555 | 26415.6146 | 2440519.8686 | 43218.903
3619 | 1175.793 | 0 | 0 | 0 | 0 | 1713.55 | 0 | 0 | 0 | 3995344.614 | 0
3620 | 1504 | 0 | 0 | 0 | 0 | 1790.7 | 0 | 0 | 0 | 5110592 | 0
3621 | 1400 | 0 | 0 | 0 | 0 | 1822.7 | 0 | 0 | 0 | 4757200 | 0
3622 | 1072 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1874.8 | 605831.9237 | 111351.8261 | 50510.4255 | 2591618.4863 | 38295.4248
3623 | 1568.8 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1859.05 | 1167890.5235 | 215514.4963 | 97759.7701 | 3296565.0159 | 83442.4
3624 | 0 | 0 | 0 | 0 | 0 | 1756.35 | 0 | 0 | 0 | 0 | 0
3625 | 1048.116 | 0 | 0 | 0 | 0 | 1017.55 | 0 | 0 | 0 | 1921196.6445 | 0
3626 | 1148.1467 | 0 | 0 | 0 | 0 | 1524.35 | 0 | 0 | 0 | 2104552.9561 | 0
3627 | 1165.0637 | 0 | 0 | 0 | 0 | 1437.25 | 0 | 0 | 0 | 2135561.7438 | 0
3628 | 1257.0037 | 0 | 0 | 0 | 0 | 1231 | 0 | 0 | 0 | 2304087.7656 | 0
3629 | 1164.3282 | 0 | 0 | 0 | 0 | 1227.65 | 0 | 0 | 0 | 2134213.5356 | 0
3630 | 1084.892 | 0 | 0 | 0 | 0 | 1075.45 | 0 | 0 | 0 | 1988607.0525 | 0
3631 | 1136.1375 | 457.2413 | 457.2413 | 445.1064 | 445.1064 | 1023.8 | 475741.4169 | 160238.3044 | 72685.8753 | 1266660.0539 | 425320.578
3632 | 857.2624 | 910.3846 | 890.5289 | 886.2235 | 857.2624 | 318.2 | 284867.4837 | 308614.4491 | 139990.9431 | 0 | 1441743.8345
3633 | 1126.9766 | 2087.3483 | 1170.7091 | 2031.9512 | 1126.9766 | 1106.7 | 1303100.5133 | 405711.585 | 184035.2829 | 0 | 1006728.2191
3634 | 1088.1963 | 2065.3464 | 1130.4242 | 2010.5332 | 1088.1963 | 1076.9 | 1234181.3875 | 391750.6799 | 177702.4612 | 0 | 1004514.035
3635 | 1073.6523 | 2767.6511 | 1115.3148 | 2694.1992 | 1073.6523 | 385.8 | 437542.1797 | 386514.8438 | 175327.4278 | 0 | 1733089.6137
3636 | 1056.4835 | 2432.4818 | 1097.4806 | 2367.9251 | 1056.4835 | 381.65 | 423973.5793 | 380334.0488 | 172523.7505 | 0 | 1709760.0221
3637 | 976.002 | 1756.8723 | 1013.8755 | 1710.2459 | 976.002 | 378.9 | 387262.3549 | 351360.702 | 159381.1185 | 0 | 1582196.7613
3638 | 1109.748 | 1140.726 | 1140.726 | 1110.4518 | 1109.748 | 401.05 | 467167.8325 | 399509.276 | 181221.8466 | 0 | 1746635.4178
3639 | 1130.2855 | 1787.8744 | 1174.1465 | 1740.4252 | 1130.2855 | 412.85 | 490751.646 | 406902.7966 | 184575.6297 | 0 | 1793932.7043
3640 | 1121.2717 | 1115.3865 | 1115.3865 | 1085.7847 | 1085.7847 | 411.15 | 469642.3647 | 390882.5007 | 177308.6455 | 65047.7146 | 1688656.7904
3641 | 781.8035 | 353.8346 | 353.8346 | 344.444 | 344.444 | 969.15 | 349627.8276 | 123999.8331 | 56247.7021 | 801680.0395 | 347559.3243
3642 | 946.9489 | 112.5431 | 112.5431 | 109.5562 | 109.5562 | 940.4 | 108100.1318 | 39440.2449 | 17890.5333 | 1534940.7713 | 113630.4444
3643 | 1087.8341 | 0 | 0 | 0 | 0 | 359.9 | 0 | 0 | 0 | 1993999.8851 | 0
3644 | 1190.0714 | 0 | 0 | 0 | 0 | 365.8 | 0 | 0 | 0 | 2181400.8212 | 0
3645 | 939.259 | 0 | 0 | 0 | 0 | 365.25 | 0 | 0 | 0 | 1721661.8354 | 0
3646 | 1095.1893 | 151.9418 | 151.9418 | 147.9094 | 147.9094 | 367 | 56861.6453 | 53247.3705 | 24153.5989 | 1736364.1073 | 238852.378
3647 | 1081.2144 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 356.25 | 224833.4781 | 215514.4963 | 97759.7701 | 884538.0349 | 973100
3648 | 159.6078 | 165.8015 | 165.8015 | 161.4013 | 159.6078 | 339.7 | 56909.9271 | 57458.8229 | 26063.9605 | 0 | 264996.8991
3649 | 82.3782 | 0 | 0 | 0 | 0 | 1072.9 | 0 | 0 | 0 | 98030.1065 | 0
3650 | 157.4013 | 0 | 0 | 0 | 0 | 349.15 | 0 | 0 | 0 | 187307.5249 | 0
3651 | 100.7662 | 0 | 0 | 0 | 0 | 337.6 | 0 | 0 | 0 | 119911.8267 | 0
3652 | 105.1794 | 0 | 0 | 0 | 0 | 327.35 | 0 | 0 | 0 | 125163.4395 | 0
3653 | 78.7006 | 0 | 0 | 0 | 0 | 320.65 | 0 | 0 | 0 | 93653.7624 | 0
3654 | 81.6427 | 0 | 0 | 0 | 0 | 315.7 | 0 | 0 | 0 | 97154.8376 | 0
3655 | 78.8376 | 81.8973 | 81.8973 | 79.7238 | 78.8376 | 314.55 | 25916.7467 | 28381.5473 | 12874.1852 | 0 | 132875.8216
3656 | 193.0078 | 913.661 | 200.4976 | 889.4129 | 193.0078 | 339.6 | 68421.1252 | 69482.8098 | 31518.1745 | 0 | 320470.1593
3657 | 787.8808 | 818.4535 | 818.4535 | 796.7322 | 787.8808 | 384.4 | 316191.2611 | 283637.0723 | 128660.9275 | 0 | 1272900.1499
3658 | 1235.6617 | 1961.9905 | 1283.6105 | 1909.9204 | 1235.6617 | 401.7 | 519998.5935 | 444838.1972 | 201783.5489 | 0 | 1974958.0296
3659 | 1134.1783 | 1612.0858 | 1178.1905 | 1569.3019 | 1134.1783 | 408.5 | 488314.7652 | 408304.183 | 185211.3141 | 0 | 1805044.7422
3660 | 928.5379 | 3950.777 | 964.5697 | 3845.9256 | 928.5379 | 407.55 | 398206.9479 | 334273.6529 | 151630.2431 | 0 | 1478650.2182
3661 | 1150.8718 | 3307.813 | 1195.5313 | 3220.0254 | 1150.8718 | 412.3 | 497510.7891 | 414313.8595 | 187937.3702 | 0 | 1827239.2077
3662 | 1024.287 | 2768.5206 | 1064.0342 | 2695.0456 | 1024.287 | 440.25 | 473820.3966 | 368743.32 | 167266.0671 | 0 | 1597631.6483
3663 | 1039.8662 | 2743.7056 | 1080.2177 | 2670.8892 | 1039.8662 | 451.75 | 494659.9459 | 374351.8439 | 169810.1558 | 0 | 1609972.8952
3664 | 1200.7723 | 839.1963 | 839.1963 | 816.9245 | 816.9245 | 442.4 | 379574.0887 | 294092.829 | 133403.7749 | 703592.9111 | 1245525.4944
3665 | 1211.6653 | 626.3577 | 626.3577 | 609.7345 | 609.7345 | 1408 | 897076.2953 | 219504.4268 | 99569.6469 | 1103339.1548 | 353327.504
3666 | 1362.6896 | 189.5195 | 189.5195 | 184.4898 | 184.4898 | 1756.7 | 340406.8827 | 66416.3255 | 30127.1832 | 2159640.3213 | 43937.0604
3667 | 1236.4091 | 0 | 0 | 0 | 0 | 1770.65 | 0 | 0 | 0 | 4201318.2271 | 0
3668 | 1330.5557 | 0 | 0 | 0 | 0 | 1800.95 | 0 | 0 | 0 | 4521228.2414 | 0
3669 | 1363.6541 | 0 | 0 | 0 | 0 | 1844.25 | 0 | 0 | 0 | 4633696.6046 | 0
3670 | 988.5389 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1903.6 | 615701.0643 | 111351.8261 | 50510.4255 | 2308017.6297 | 29486.2536
3671 | 1133.4363 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1902.5 | 1196365.7005 | 215514.4963 | 97759.7701 | 1817199.2653 | 57720
3672 | 1025.3149 | 0 | 0 | 0 | 0 | 1835.3 | 0 | 0 | 0 | 1879402.1915 | 0
3673 | 1040.0253 | 0 | 0 | 0 | 0 | 1692.8 | 0 | 0 | 0 | 1237630.0939 | 0
3674 | 1289.3666 | 0 | 0 | 0 | 0 | 1658.85 | 0 | 0 | 0 | 1534346.2195 | 0
3675 | 807.601 | 0 | 0 | 0 | 0 | 1379.95 | 0 | 0 | 0 | 961045.1507 | 0
3676 | 906.1606 | 0 | 0 | 0 | 0 | 1078.35 | 0 | 0 | 0 | 1078331.171 | 0
3677 | 1054.7357 | 0 | 0 | 0 | 0 | 1069.6 | 0 | 0 | 0 | 1255135.4699 | 0
3678 | 1198.1621 | 0 | 0 | 0 | 0 | 1005.55 | 0 | 0 | 0 | 1425812.8871 | 0
3679 | 1087.0664 | 447.1577 | 447.1577 | 435.2903 | 435.2903 | 293.2 | 133799.4639 | 156704.5219 | 71082.9123 | 1194705.5022 | 727236.7576
3680 | 1228.1419 | 1275.7997 | 1275.7997 | 1241.9407 | 1228.1419 | 299.9 | 386975.8038 | 442131.079 | 200555.57 | 0 | 2087962.5141
3681 | 1131.3953 | 1903.1796 | 1175.2995 | 1852.6703 | 1131.3953 | 318.8 | 379466.2397 | 407302.2943 | 184756.8463 | 0 | 1902101.7145
3682 | 1253.8934 | 3063.6585 | 1302.551 | 2982.3507 | 1253.8934 | 332.85 | 439680.842 | 451401.61 | 204760.7859 | 0 | 2090428.3168
3683 | 1272.5121 | 3688.7448 | 1321.8915 | 3590.8475 | 1272.5121 | 345.9 | 463999.8273 | 458104.3668 | 207801.2308 | 0 | 2104862.3142
3684 | 1338.8744 | 3910.6148 | 1390.8287 | 3806.8292 | 1338.8744 | 348.15 | 492596.7422 | 481994.7923 | 218638.1933 | 0 | 2211619.7156
3685 | 1355.3308 | 3288.2429 | 1407.9243 | 3200.9748 | 1355.3308 | 355.15 | 508934.6675 | 487919.075 | 221325.5138 | 0 | 2229315.8072
3686 | 1295.2535 | 1037.3743 | 1037.3743 | 1009.843 | 1009.843 | 371.1 | 396064.8377 | 363543.4676 | 164907.3563 | 523157.4916 | 1610138.3298
3687 | 1302.0681 | 1127.3504 | 1127.3504 | 1097.4311 | 1097.4311 | 375.7 | 436256.5391 | 395075.2042 | 179210.5023 | 375099.5463 | 1744850.6731
3688 | 1469.4209 | 823.1281 | 823.1281 | 801.2827 | 801.2827 | 366.25 | 309988.6398 | 288461.7847 | 130849.4707 | 1224697.3458 | 1281404.0388
3689 | 1487.386 | 500.5377 | 500.5377 | 487.2537 | 487.2537 | 348.95 | 178739.3642 | 175411.3258 | 79568.5264 | 1833242.5851 | 787461.6933
3690 | 1238.9154 | 183.4405 | 183.4405 | 178.572 | 178.572 | 334.85 | 62640.9739 | 64285.9356 | 29160.8147 | 1943609.4004 | 291059.8943
3691 | 1209.1949 | 0 | 0 | 0 | 0 | 1291.45 | 0 | 0 | 0 | 4108844.2396 | 0
3692 | 1137.1139 | 0 | 0 | 0 | 0 | 1675.35 | 0 | 0 | 0 | 3863913.1341 | 0
3693 | 1054.7357 | 0 | 0 | 0 | 0 | 1766.25 | 0 | 0 | 0 | 3583991.8712 | 0
3694 | 1102.5445 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1787.75 | 578099.0748 | 111351.8261 | 50510.4255 | 2695408.6633 | 64921.7565
3695 | 1087.8341 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1795.15 | 1123732.611 | 215514.4963 | 97759.7701 | 1662242.8504 | 121271.2
3696 | 1305.548 | 0 | 0 | 0 | 0 | 1773.9 | 0 | 0 | 0 | 2393069.5042 | 0
3697 | 1315.1098 | 0 | 0 | 0 | 0 | 1637.5 | 0 | 0 | 0 | 1564980.6275 | 0
3698 | 1071.6526 | 0 | 0 | 0 | 0 | 1103 | 0 | 0 | 0 | 1275266.6523 | 0
3699 | 1255.5327 | 0 | 0 | 0 | 0 | 1038.05 | 0 | 0 | 0 | 1494083.8547 | 0
3700 | 806.1299 | 0 | 0 | 0 | 0 | 968.4 | 0 | 0 | 0 | 959294.6131 | 0
3701 | 750.2304 | 0 | 0 | 0 | 0 | 977.5 | 0 | 0 | 0 | 892774.1837 | 0
3702 | 706.0992 | 0 | 0 | 0 | 0 | 990.4 | 0 | 0 | 0 | 840258.0554 | 0
3703 | 1144.1924 | 125.5074 | 125.5074 | 122.1765 | 122.1765 | 668.95 | 85843.9963 | 43983.5235 | 19951.415 | 1873355.2121 | 159182.9316
3704 | 1174.6209 | 395.8594 | 395.8594 | 385.3535 | 385.3535 | 344.9 | 139297.3898 | 138727.2637 | 62928.2282 | 1446727.0392 | 624307.0302
3705 | 1421.8944 | 1040.8813 | 1040.8813 | 1013.2569 | 1013.2569 | 399.9 | 424824.7468 | 364772.4827 | 165464.8512 | 749032.5535 | 1587015.9823
3706 | 1445.488 | 1707.6922 | 1501.5798 | 1662.3709 | 1445.488 | 421.4 | 641213.5848 | 520375.6973 | 236048.1982 | 0 | 2281847.4326
3707 | 1314.3991 | 2612.1795 | 1365.4039 | 2542.8536 | 1314.3991 | 427.1 | 593102.9522 | 473183.667 | 214641.3689 | 0 | 2067418.3051
3708 | 1630.578 | 2768.3845 | 1693.8522 | 2694.9131 | 1630.578 | 420.5 | 723922.0748 | 587008.0728 | 266273.3841 | 0 | 2575497.9194
3709 | 1339.1925 | 3957.2166 | 1391.159 | 3852.1942 | 1339.1925 | 422.45 | 595155.3077 | 482109.3126 | 218690.141 | 0 | 2112643.1836
3710 | 1441.9686 | 3654.4621 | 1497.9242 | 3557.4747 | 1441.9686 | 811.15 | 1231773.0132 | 519108.6906 | 235473.4699 | 0 | 1714284.3523
3711 | 1484.2371 | 3088.5099 | 1541.8324 | 3006.5425 | 1484.2371 | 1692.6 | 2641276.7106 | 534325.3492 | 242375.9153 | 0 | 456254.4787
3712 | 1687.8042 | 2283.5079 | 1753.2988 | 2222.9048 | 1687.8042 | 1872.1 | 3318882.5838 | 607609.5102 | 275618.425 | 0 | 215870.1565
3713 | 1368.332 | 1206.9945 | 1206.9945 | 1174.9615 | 1174.9615 | 1904.75 | 2345144.426 | 422986.1517 | 191871.2182 | 354448.0652 | 109547.6918
3714 | 1435.4445 | 278.8869 | 278.8869 | 271.4854 | 271.4854 | 1814.05 | 516970.3442 | 97734.7319 | 44333.5603 | 2133537.1322 | 49414.7249
3715 | 1408.5208 | 0 | 0 | 0 | 0 | 1707.3 | 0 | 0 | 0 | 4786153.7192 | 0
3716 | 1324.6715 | 0 | 0 | 0 | 0 | 1775.5 | 0 | 0 | 0 | 4501233.8657 | 0
3717 | 1376.1579 | 0 | 0 | 0 | 0 | 1797.4 | 0 | 0 | 0 | 4676184.6529 | 0
3718 | 889.2437 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1874.55 | 608048.9961 | 111351.8261 | 50510.4255 | 1970612.5374 | 38371.8933
3719 | 1277.5983 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1819.75 | 1146419.2366 | 215514.4963 | 97759.7701 | 2307061.4728 | 106708
3720 | 914.2514 | 0 | 0 | 0 | 0 | 1821.85 | 0 | 0 | 0 | 1675822.7575 | 0
3721 | 1040.0253 | 0 | 0 | 0 | 0 | 1684.55 | 0 | 0 | 0 | 1237630.0939 | 0
3722 | 1225.3763 | 0 | 0 | 0 | 0 | 1314 | 0 | 0 | 0 | 1458197.8339 | 0
3723 | 1041.4963 | 0 | 0 | 0 | 0 | 1042.1 | 0 | 0 | 0 | 1239380.6315 | 0
3724 | 1069.4461 | 0 | 0 | 0 | 0 | 319.7 | 0 | 0 | 0 | 1272640.8459 | 0
3725 | 1206.9883 | 0 | 0 | 0 | 0 | 313.5 | 0 | 0 | 0 | 1436316.1139 | 0
3726 | 1139.3205 | 0 | 0 | 0 | 0 | 310.6 | 0 | 0 | 0 | 1355791.3831 | 0
3727 | 968.3737 | 448.3938 | 448.3938 | 436.4937 | 436.4937 | 313.5 | 142431.142 | 157137.7352 | 71279.4226 | 974936.0022 | 720573.99
3728 | 1216.8397 | 1264.0592 | 1264.0592 | 1230.5117 | 1216.8397 | 344.9 | 438396.7694 | 438062.2927 | 198709.9233 | 0 | 2013990.2289
3729 | 1270.5584 | 1891.6001 | 1319.8627 | 1841.398 | 1270.5584 | 399.75 | 532756.6718 | 457401.0258 | 207482.1875 | 0 | 2033211.0876
3730 | 1288.7009 | 2836.2195 | 1338.7087 | 2760.9478 | 1288.7009 | 421.4 | 572358.6516 | 463932.3334 | 210444.8612 | 0 | 2034343.2818
3731 | 1265.5835 | 3048.466 | 1314.6947 | 2967.5614 | 1265.5835 | 427.1 | 572305.9614 | 455610.0715 | 206669.7908 | 0 | 1990636.3375
3732 | 1527.2199 | 3167.3074 | 1586.4834 | 3083.2488 | 1527.2199 | 420.5 | 679596.4681 | 549799.182 | 249395.0178 | 0 | 2412243.911
3733 | 1609.8915 | 2789.9709 | 1672.3624 | 2715.9266 | 1609.8915 | 422.45 | 717046.4544 | 579560.9328 | 262895.2787 | 0 | 2539684.3043
3734 | 1684.8217 | 3164.5691 | 1750.2001 | 3080.5831 | 1684.8217 | 776.2 | 1378753.1192 | 606535.798 | 275131.3772 | 0 | 2061884.7487
3735 | 1461.4939 | 2816.7378 | 1518.2069 | 2741.9831 | 1461.4939 | 463.9 | 714705.3908 | 526137.7979 | 238661.9511 | 0 | 2245000.7537
3736 | 1490.238 | 2236.7398 | 1548.0663 | 2177.378 | 1490.238 | 862.6 | 1351321.7118 | 536485.6814 | 243355.8661 | 0 | 1694996.7057
3737 | 1239.2694 | 1136.7298 | 1136.7298 | 1106.5616 | 1106.5616 | 1860.8 | 2147942.5253 | 398362.1643 | 180701.504 | 243253.4276 | 150775.0368
3738 | 1422.6934 | 207.895 | 207.895 | 202.3775 | 202.3775 | 1737.85 | 366534.0263 | 72855.9132 | 33048.2517 | 2236838.9096 | 51930.8664
3739 | 1531.3527 | 0 | 0 | 0 | 0 | 1718.85 | 0 | 0 | 0 | 5203536.3149 | 0
3740 | 1093.7182 | 0 | 0 | 0 | 0 | 1804.65 | 0 | 0 | 0 | 3716454.6135 | 0
3741 | 818.6338 | 0 | 0 | 0 | 0 | 1847.9 | 0 | 0 | 0 | 2781717.5406 | 0
3742 | 913.5158 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1913.55 | 618605.4255 | 111351.8261 | 50510.4255 | 2053089.3378 | 26442.8073
3743 | 1149.6178 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1824.7 | 1148667.1335 | 215514.4963 | 97759.7701 | 1872183.7984 | 103777.6
3744 | 1036.3477 | 0 | 0 | 0 | 0 | 1722 | 0 | 0 | 0 | 1899625.3139 | 0
3745 | 967.2088 | 0 | 0 | 0 | 0 | 1121.35 | 0 | 0 | 0 | 1150978.482 | 0
3746 | 1274.6562 | 0 | 0 | 0 | 0 | 1053.05 | 0 | 0 | 0 | 1516840.8435 | 0
3747 | 962.0602 | 0 | 0 | 0 | 0 | 651.8 | 0 | 0 | 0 | 1144851.6004 | 0
3748 | 1158.444 | 0 | 0 | 0 | 0 | 319.7 | 0 | 0 | 0 | 1378548.3719 | 0
3749 | 1215.0791 | 0 | 0 | 0 | 0 | 313.8 | 0 | 0 | 0 | 1445944.0707 | 0
3750 | 663.439 | 0 | 0 | 0 | 0 | 310.75 | 0 | 0 | 0 | 789492.4645 | 0
3751 | 831.19 | 425.1277 | 425.1277 | 413.8451 | 413.8451 | 313.65 | 135974.3091 | 148984.2247 | 67580.8997 | 764993.283 | 683125.2079
3752 | 900.2029 | 935.1352 | 935.1352 | 910.3172 | 900.2029 | 344.9 | 324993.8601 | 324073.0569 | 147003.1394 | 0 | 1489925.8792
3753 | 1016.1898 | 1408.0946 | 1055.623 | 1370.7246 | 1016.1898 | 399.75 | 426680.5829 | 365828.3438 | 165943.8015 | 0 | 1626157.7979
3754 | 1501.8804 | 1880.8651 | 1560.1611 | 1830.9479 | 1501.8804 | 421.25 | 664258.0261 | 540676.9321 | 245257.0639 | 0 | 2371093.6294
3755 | 1433.3713 | 3664.2726 | 1488.9926 | 3567.0248 | 1433.3713 | 427.1 | 644454.7096 | 516013.659 | 234069.5292 | 0 | 2254549.6784
3756 | 1371.731 | 2235.995 | 1424.9607 | 2176.6529 | 1371.731 | 420.5 | 606084.2452 | 493823.1676 | 224003.6757 | 0 | 2166649.1477
3757 | 1529.9046 | 1084.5267 | 1084.5267 | 1055.744 | 1055.744 | 422.45 | 466670.4445 | 380067.8231 | 172402.9875 | 869136.4621 | 1630259.1006
3758 | 1387.7571 | 355.3128 | 355.3128 | 345.883 | 345.883 | 451.55 | 164427.2483 | 124517.8687 | 56482.6888 | 1909755.2514 | 524254.0711
3759 | 1085.9861 | 606.1966 | 606.1966 | 590.1085 | 590.1085 | 463.6 | 288402.2325 | 212439.0461 | 96364.7118 | 908943.7022 | 887464.5864
3760 | 1513.4915 | 505.9727 | 505.9727 | 492.5445 | 492.5445 | 816.55 | 424201.4997 | 177316.008 | 80432.5114 | 1871395.8554 | 570570.8313
3761 | 1215.0892 | 325.4887 | 325.4887 | 316.8504 | 316.8504 | 1243.75 | 414653.3488 | 114066.1438 | 51741.6702 | 1646471.6556 | 234549.425
3762 | 1339.0123 | 57.1883 | 57.1883 | 55.6705 | 55.6705 | 1111.8 | 65141.1156 | 20041.392 | 9090.9981 | 2352365.5189 | 48400.6826
3763 | 1233.4671 | 0 | 0 | 0 | 0 | 1100 | 0 | 0 | 0 | 4191321.0393 | 0
3764 | 1164.3282 | 0 | 0 | 0 | 0 | 1108.6 | 0 | 0 | 0 | 3956387.1217 | 0
3765 | 1034.1411 | 0 | 0 | 0 | 0 | 1386.75 | 0 | 0 | 0 | 3514011.5563 | 0
3766 | 1329.8202 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1819.6 | 593561.3861 | 111351.8261 | 50510.4255 | 3467691.4307 | 55179.6696
3767 | 1057.6778 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1752.65 | 1108952.4901 | 215514.4963 | 97759.7701 | 1559771.675 | 146431.2
3768 | 1348.9437 | 0 | 0 | 0 | 0 | 1313.5 | 0 | 0 | 0 | 2472613.7874 | 0
3769 | 972.3574 | 0 | 0 | 0 | 0 | 1075.45 | 0 | 0 | 0 | 1157105.3637 | 0
3770 | 1018.6952 | 0 | 0 | 0 | 0 | 1037.1 | 0 | 0 | 0 | 1212247.2987 | 0
3771 | 1329.8202 | 0 | 0 | 0 | 0 | 991.15 | 0 | 0 | 0 | 1582486.0047 | 0
3772 | 1226.8474 | 0 | 0 | 0 | 0 | 968.4 | 0 | 0 | 0 | 1459948.3715 | 0
3773 | 759.7922 | 0 | 0 | 0 | 0 | 993.45 | 0 | 0 | 0 | 904152.6783 | 0
3774 | 961.3246 | 0 | 0 | 0 | 0 | 1029.45 | 0 | 0 | 0 | 1143976.3316 | 0
3775 | 883.3154 | 223.7918 | 223.7918 | 217.8525 | 217.8525 | 993.45 | 227707.0977 | 78426.8901 | 35575.3088 | 1219793.5395 | 214640.7482
3776 | 819.4309 | 869.9148 | 851.2288 | 846.8278 | 819.4309 | 345.2 | 296739.0468 | 294995.1193 | 133813.0638 | 0 | 1355994.2316
3777 | 938.7295 | 1455.0112 | 975.1572 | 1416.396 | 938.7295 | 399.9 | 394139.4236 | 337942.6106 | 153294.5231 | 0 | 1502061.031
3778 | 1175.0134 | 3061.394 | 1220.6091 | 2980.1462 | 1175.0134 | 421.25 | 520047.7448 | 423004.8373 | 191879.6943 | 0 | 1855052.4637
3779 | 1296.981 | 2108.9856 | 1347.31 | 2053.0142 | 1296.981 | 427.1 | 583278.8007 | 466913.1751 | 211797.0042 | 0 | 2040021.481
3780 | 1264.4646 | 3681.0389 | 1313.5312 | 3583.3461 | 1264.4646 | 420.5 | 558432.0439 | 455207.2639 | 206487.0728 | 0 | 1997221.8704
3781 | 1379.1589 | 3695.0908 | 1432.6769 | 3597.0251 | 1379.1589 | 422.45 | 609794.624 | 496497.1874 | 225216.6409 | 0 | 2175692.0501
3782 | 1238.6166 | 1973.6324 | 1286.6812 | 1921.2533 | 1238.6166 | 451.55 | 590795.674 | 445901.9796 | 202266.0924 | 0 | 1917935.8898
3783 | 1071.4449 | 2616.289 | 1113.0222 | 2546.8541 | 1071.4449 | 463.6 | 525935.8287 | 385720.1514 | 174966.9465 | 0 | 1646167.8906
3784 | 1163.5669 | 2073.419 | 1208.7189 | 2018.3915 | 1163.5669 | 457.05 | 562818.6389 | 418884.0865 | 190010.4759 | 0 | 1795325.5592
3785 | 930.6139 | 872.9533 | 872.9533 | 849.7856 | 849.7856 | 1153.75 | 1036240.6734 | 305922.8274 | 138769.9937 | 148158.2705 | 703919.2125
3786 | 930.0798 | 230.4921 | 230.4921 | 224.3749 | 224.3749 | 752.45 | 178646.6643 | 80774.9788 | 36640.4279 | 1293556.9302 | 273998.159
3787 | 892.9213 | 0 | 0 | 0 | 0 | 1369.8 | 0 | 0 | 0 | 3034146.5359 | 0
3788 | 1206.2528 | 0 | 0 | 0 | 0 | 1727.45 | 0 | 0 | 0 | 4098847.0518 | 0
3789 | 1006.9269 | 0 | 0 | 0 | 0 | 1722 | 0 | 0 | 0 | 3421537.5688 | 0
3790 | 984.8613 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1819.6 | 593728.6058 | 111351.8261 | 50510.4255 | 2295521.1449 | 55179.6696
3791 | 1077.5368 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1742.75 | 1106243.2611 | 215514.4963 | 97759.7701 | 1627252.6929 | 152292
3792 | 956.176 | 0 | 0 | 0 | 0 | 1515.85 | 0 | 0 | 0 | 1752670.6232 | 0
3793 | 959.8536 | 0 | 0 | 0 | 0 | 880.95 | 0 | 0 | 0 | 1759411.6642 | 0
3794 | 1045.1739 | 0 | 0 | 0 | 0 | 687.7 | 0 | 0 | 0 | 1915803.8119 | 0
3795 | 993.6875 | 0 | 0 | 0 | 0 | 327.25 | 0 | 0 | 0 | 1821429.2401 | 0
3796 | 951.0274 | 0 | 0 | 0 | 0 | 319.4 | 0 | 0 | 0 | 1743233.1661 | 0
3797 | 970.1509 | 0 | 0 | 0 | 0 | 313.5 | 0 | 0 | 0 | 1778286.5786 | 0
3798 | 989.2744 | 0 | 0 | 0 | 0 | 310.45 | 0 | 0 | 0 | 1813339.991 | 0
3799 | 814.7659 | 433.3841 | 433.3841 | 421.8824 | 421.8824 | 313.5 | 139264.2802 | 151877.6525 | 68893.3907 | 720155.4249 | 696453.667
3800 | 269.8053 | 699.0948 | 280.2747 | 680.5412 | 269.8053 | 344.9 | 97740.7871 | 97129.9035 | 44059.2035 | 0 | 446554.7315
3801 | 129.9866 | 2027.8528 | 135.0311 | 1974.0347 | 129.9866 | 399.75 | 54566.5356 | 46795.1803 | 21226.8137 | 0 | 208011.0757
3802 | 207.7449 | 3146.6975 | 215.8065 | 3063.1858 | 207.7449 | 421.25 | 91922.9441 | 74788.1523 | 33924.7369 | 0 | 327977.2097
3803 | 159.9664 | 2762.6545 | 166.1745 | 2689.3351 | 159.9664 | 427.1 | 72016.4171 | 57587.9067 | 26122.5143 | 0 | 251611.1622
3804 | 171.8487 | 3227.7139 | 178.5176 | 3142.0521 | 171.8487 | 420.5 | 76009.0715 | 61865.5439 | 28062.8981 | 0 | 271435.0739
3805 | 132.4947 | 3104.9323 | 137.6354 | 3022.5291 | 132.4947 | 422.45 | 58623.6964 | 47698.1047 | 21636.3903 | 0 | 209017.0695
3806 | 124.5833 | 3361.6657 | 129.4174 | 3272.4489 | 124.5833 | 451.55 | 59240.3606 | 44849.9873 | 20344.4526 | 0 | 192911.0079
3807 | 178.8941 | 2515.715 | 185.8359 | 2448.9493 | 178.8941 | 463.6 | 87459.9796 | 64401.8743 | 29213.4058 | 0 | 274852.8882
3808 | 197.9358 | 1931.1692 | 205.6169 | 1879.917 | 197.9358 | 1605.15 | 335552.8059 | 71256.884 | 32322.9143 | 0 | 78154.9462
3809 | 169.2818 | 705.9665 | 175.8509 | 687.2305 | 169.2818 | 1647.35 | 292832.8938 | 60941.4366 | 27643.7128 | 0 | 59697.2156
3810 | 186.6658 | 209.6692 | 193.9095 | 204.1047 | 186.6658 | 952.4 | 186964.3358 | 67199.6821 | 30482.5225 | 0 | 195551.0749
3811 | 128.716 | 133.7108 | 133.7108 | 130.1622 | 128.716 | 880.6 | 119068.6966 | 46337.7604 | 21019.323 | 0 | 144084.6904
3812 | 181.6734 | 188.7228 | 188.7228 | 183.7142 | 181.6734 | 1398.1 | 266775.8342 | 65402.439 | 29667.273 | 0 | 109348.9787
3813 | 183.1445 | 190.2509 | 190.2509 | 185.2017 | 183.1445 | 1611.4 | 309634.2805 | 65932.0134 | 29907.4938 | 0 | 71169.7584
3814 | 100.0307 | 103.9127 | 103.9127 | 101.1549 | 100.0307 | 1753.55 | 184463.1562 | 36011.0595 | 16335.0167 | 0 | 24652.5712
3815 | 90.469 | 93.9796 | 93.9796 | 91.4855 | 90.469 | 966.75 | 92398.6542 | 32568.8259 | 14773.5813 | 0 | 93477.0537
3816 | 94.1466 | 97.8004 | 97.8004 | 95.2048 | 94.1466 | 383.2 | 38102.2382 | 33892.7619 | 15374.1334 | 0 | 152216.1595
3817 | 85.3203 | 0 | 0 | 0 | 0 | 721.75 | 0 | 0 | 0 | 101531.1817 | 0
3818 | 91.2045 | 0 | 0 | 0 | 0 | 998.15 | 0 | 0 | 0 | 108533.3322 | 0
3819 | 86.7914 | 0 | 0 | 0 | 0 | 986.6 | 0 | 0 | 0 | 103281.7193 | 0
3820 | 90.469 | 0 | 0 | 0 | 0 | 976.35 | 0 | 0 | 0 | 107658.0633 | 0
3821 | 85.3203 | 34.9433 | 34.9433 | 34.0159 | 34.0159 | 969.65 | 34789.5663 | 12245.7375 | 5554.8026 | 61052.2159 | 34658.9133
3822 | 86.0558 | 89.3954 | 89.3954 | 87.0229 | 86.0558 | 964.7 | 87490.2317 | 30980.1027 | 14052.9188 | 0 | 89093.6119
3823 | 73.9979 | 76.8695 | 76.8695 | 74.8294 | 73.9979 | 978.55 | 76036.8099 | 26639.2475 | 12083.8586 | 0 | 75584.2357
3824 | 92.8447 | 96.4468 | 96.4468 | 93.8871 | 92.8447 | 1013.6 | 98822.413 | 33424.0885 | 15161.5379 | 0 | 91582.0026
3825 | 624.5034 | 648.7367 | 648.7367 | 631.5196 | 624.5034 | 1103.1 | 724464.2937 | 224821.2149 | 101981.4011 | 0 | 560116.7407
3826 | 1169.1854 | 1214.5549 | 1214.5549 | 1182.3213 | 1169.1854 | 726.2 | 893239.646 | 420906.7296 | 190927.9693 | 0 | 1489307.853
3827 | 1182.7428 | 2586.4015 | 1228.638 | 2517.7598 | 1182.7428 | 408.5 | 510004.703 | 425787.4199 | 193141.9046 | 0 | 1882335.2187
3828 | 1218.137 | 2871.8921 | 1265.4065 | 2795.6736 | 1218.137 | 407.55 | 523162.1746 | 438529.311 | 198921.768 | 0 | 1939822.2258
3829 | 1041.8558 | 2856.3734 | 1082.285 | 2780.5668 | 1041.8558 | 412.3 | 450643.2604 | 375068.093 | 170135.0544 | 0 | 1654154.4759
3830 | 1119.2978 | 1457.8596 | 1162.731 | 1419.1688 | 1119.2978 | 440.25 | 520307.8128 | 402947.2069 | 182781.3303 | 0 | 1745824.7389
3831 | 1117.0011 | 2204.3665 | 1160.3459 | 2145.8638 | 1117.0011 | 1508.45 | 1784230.9381 | 402120.4086 | 182406.2853 | 0 | 549061.9079
3832 | 1182.9589 | 1616.1901 | 1228.8634 | 1573.2973 | 1182.9589 | 1576.8 | 1967799.1533 | 425865.2011 | 193177.1871 | 0 | 500628.2031
3833 | 1307.3767 | 854.5488 | 854.5488 | 831.8696 | 831.8696 | 1549.2 | 1358449.4045 | 299473.0465 | 135844.3014 | 871604.5592 | 367074.2684
3834 | 1228.2872 | 235.9749 | 235.9749 | 229.7122 | 229.7122 | 1504.8 | 365326.4543 | 82696.407 | 37512.0091 | 1830387.8086 | 111347.2056
3835 | 1151.8243 | 0 | 0 | 0 | 0 | 1494.6 | 0 | 0 | 0 | 3913899.0733 | 0
3836 | 1090.7762 | 0 | 0 | 0 | 0 | 1504.35 | 0 | 0 | 0 | 3706457.4257 | 0
3837 | 1351.8858 | 0 | 0 | 0 | 0 | 1570 | 0 | 0 | 0 | 4593707.8533 | 0
3838 | 1092.9827 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1532.3 | 500428.5861 | 111351.8261 | 50510.4255 | 2662917.8028 | 143057.2698
3839 | 716.3965 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1284 | 815844.2953 | 215514.4963 | 97759.7701 | 400097.8764 | 423872
3840 | 1042.2318 | 0 | 0 | 0 | 0 | 718.05 | 0 | 0 | 0 | 1910410.9792 | 0
3841 | 806.8654 | 0 | 0 | 0 | 0 | 726.65 | 0 | 0 | 0 | 960169.8819 | 0
3842 | 816.4272 | 0 | 0 | 0 | 0 | 591.9 | 0 | 0 | 0 | 971548.3764 | 0
3843 | 912.0448 | 0 | 0 | 0 | 0 | 331 | 0 | 0 | 0 | 1085333.3215 | 0
3844 | 945.1432 | 0 | 0 | 0 | 0 | 571.95 | 0 | 0 | 0 | 1124720.4178 | 0
3845 | 937.788 | 0 | 0 | 0 | 0 | 313.8 | 0 | 0 | 0 | 1115967.7298 | 0
3846 | 909.1027 | 0 | 0 | 0 | 0 | 303.2 | 0 | 0 | 0 | 1081832.2462 | 0
3847 | 944.3424 | 425.1579 | 425.1579 | 413.8744 | 413.8744 | 292.7 | 127773.2775 | 148994.782 | 67585.6886 | 972347.8738 | 691659.6687
3848 | 881.4527 | 915.6576 | 915.6576 | 891.3565 | 881.4527 | 299.9 | 278138.5156 | 317322.9692 | 143941.2246 | 0 | 1498556.5452
3849 | 933.853 | 1401.3112 | 970.0909 | 1364.1212 | 933.853 | 318.8 | 313389.2396 | 336187.0714 | 152498.191 | 0 | 1569993.6234
3850 | 994.1031 | 2646.1037 | 1032.6789 | 2575.8776 | 994.1031 | 332.85 | 347262.7648 | 357877.1151 | 162337.0358 | 0 | 1657318.979
3851 | 1339.2413 | 2974.6714 | 1391.2109 | 2895.7253 | 1339.2413 | 345.9 | 486803.9702 | 482126.8547 | 218698.0982 | 0 | 2215238.9731
3852 | 1246.3699 | 3250.2455 | 1294.7351 | 3163.9858 | 1246.3699 | 348.15 | 457088.5182 | 448693.1676 | 203532.2063 | 0 | 2058816.1358
3853 | 1003.5325 | 3205.6839 | 1042.4748 | 3120.6068 | 1003.5325 | 355.15 | 377406.5713 | 361271.687 | 163876.8514 | 0 | 1650660.3734
3854 | 1101.4945 | 3025.7266 | 1144.2382 | 2945.4255 | 1101.4945 | 371.1 | 432071.822 | 396538.0326 | 179874.0576 | 0 | 1794224.4481
3855 | 1463.9441 | 2389.9957 | 1520.753 | 2326.5666 | 1463.9441 | 375.7 | 581996.8488 | 527019.8702 | 239062.0689 | 0 | 2377884.3756
3856 | 1017.2747 | 1631.8615 | 1056.7491 | 1588.5528 | 1017.2747 | 366.25 | 394655.8156 | 366218.905 | 166120.9644 | 0 | 1661972.5999
3857 | 1145.9282 | 236.6667 | 236.6667 | 230.3857 | 230.3857 | 348.95 | 84918.7162 | 82938.8608 | 37621.9888 | 1678189.3904 | 372331.5876
3858 | 1215.9093 | 27.6956 | 27.6956 | 26.9605 | 26.9605 | 334.35 | 9537.2126 | 9705.7973 | 4402.6575 | 2179343.0056 | 43956.5035
3859 | 1031.199 | 0 | 0 | 0 | 0 | 334.5 | 0 | 0 | 0 | 3504014.3685 | 0
3860 | 1098.8669 | 0 | 0 | 0 | 0 | 598.65 | 0 | 0 | 0 | 3733949.6922 | 0
3861 | 1268.772 | 0 | 0 | 0 | 0 | 357.25 | 0 | 0 | 0 | 4311287.2934 | 0
3862 | 1276.1272 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 372.75 | 122339.8714 | 111351.8261 | 50510.4255 | 3285242.7492 | 497733.4665
3863 | 1315.8453 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 374.15 | 237810.2956 | 215514.4963 | 97759.7701 | 2437024.9148 | 962503.2
3864 | 1015.0176 | 0 | 0 | 0 | 0 | 359 | 0 | 0 | 0 | 1860527.2773 | 0
3865 | 1181.9806 | 0 | 0 | 0 | 0 | 356.45 | 0 | 0 | 0 | 1406556.9735 | 0
3866 | 934.1104 | 0 | 0 | 0 | 0 | 338.1 | 0 | 0 | 0 | 1111591.3856 | 0
3867 | 1097.3959 | 0 | 0 | 0 | 0 | 327.15 | 0 | 0 | 0 | 1305901.0615 | 0
3868 | 1369.5383 | 0 | 0 | 0 | 0 | 319.4 | 0 | 0 | 0 | 1629750.5199 | 0
3869 | 1001.0427 | 0 | 0 | 0 | 0 | 313.5 | 0 | 0 | 0 | 1191240.8475 | 0
3870 | 1035.6122 | 0 | 0 | 0 | 0 | 310.45 | 0 | 0 | 0 | 1232378.4811 | 0
3871 | 734.6806 | 404.6124 | 404.6124 | 393.8742 | 393.8742 | 313.5 | 130672.3278 | 141794.7048 | 64319.6536 | 624698.1571 | 650216.583
3872 | 858.4429 | 891.7547 | 891.7547 | 868.088 | 858.4429 | 344.9 | 312556.3309 | 309039.4325 | 140183.7204 | 0 | 1420808.791
3873 | 945.9468 | 1203.6828 | 982.6532 | 1171.7377 | 945.9468 | 399.75 | 399875.6976 | 340540.835 | 154473.1065 | 0 | 1513751.3089
3874 | 1313.9909 | 2222.7482 | 1364.9801 | 2163.7577 | 1313.9909 | 421.25 | 585176.5568 | 473036.7103 | 214574.7078 | 0 | 2074463.0734
3875 | 1203.8265 | 2782.3419 | 1250.5412 | 2708.5001 | 1203.8265 | 427.1 | 545237.2765 | 433377.545 | 196584.8697 | 0 | 1893498.7239
3876 | 1170.5985 | 3218.6648 | 1216.0228 | 3133.2432 | 1170.5985 | 420.5 | 522399.1744 | 421415.4521 | 191158.7315 | 0 | 1848960.296
3877 | 1180.2871 | 3153.564 | 1226.0877 | 3069.8701 | 1180.2871 | 422.45 | 525365.1954 | 424903.3614 | 192740.8859 | 0 | 1861961.9383
3878 | 935.0749 | 2901.5032 | 971.3604 | 2824.4989 | 935.0749 | 451.55 | 445232.2207 | 336626.9492 | 152697.7244 | 0 | 1447916.6651
3879 | 1443.3311 | 2538.0223 | 1499.3391 | 2470.6646 | 1443.3311 | 463.6 | 708064.2459 | 519599.2086 | 235695.9743 | 0 | 2217533.9558
3880 | 1115.1485 | 665.8873 | 665.8873 | 648.2151 | 648.2151 | 457.15 | 314071.5616 | 233357.4219 | 105853.5195 | 855889.0745 | 978942.9535
3881 | 1294.3433 | 380.4892 | 380.4892 | 370.3913 | 370.3913 | 1289.7 | 504850.4693 | 133340.8575 | 60484.8945 | 1693604.0384 | 257523.5268
3882 | 1231.2495 | 211.3074 | 211.3074 | 205.6994 | 205.6994 | 717.4 | 155888.3867 | 74051.8002 | 33590.7194 | 1879833.1736 | 258248.9448
3883 | 1327.6136 | 0 | 0 | 0 | 0 | 1439.5 | 0 | 0 | 0 | 4511231.0536 | 0
3884 | 1377.629 | 0 | 0 | 0 | 0 | 1378.4 | 0 | 0 | 0 | 4681183.2469 | 0
3885 | 1547.5341 | 0 | 0 | 0 | 0 | 1395.35 | 0 | 0 | 0 | 5258520.8514 | 0
3886 | 1445.2968 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1700.05 | 556008.9721 | 111351.8261 | 50510.4255 | 3860081.0568 | 91746.9063
3887 | 1164.3282 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1604.15 | 1017318.5648 | 215514.4963 | 97759.7701 | 1922169.7376 | 234343.2
3888 | 1151.8243 | 0 | 0 | 0 | 0 | 383.1 | 0 | 0 | 0 | 2111293.9969 | 0
3889 | 1028.257 | 0 | 0 | 0 | 0 | 881.05 | 0 | 0 | 0 | 1223625.7931 | 0
3890 | 1179.7741 | 0 | 0 | 0 | 0 | 338.2 | 0 | 0 | 0 | 1403931.1671 | 0
3891 | 1259.2103 | 0 | 0 | 0 | 0 | 327.25 | 0 | 0 | 0 | 1498460.1987 | 0
3892 | 1282.0114 | 0 | 0 | 0 | 0 | 319.5 | 0 | 0 | 0 | 1525593.5315 | 0
3893 | 1181.9806 | 0 | 0 | 0 | 0 | 313.6 | 0 | 0 | 0 | 1406556.9735 | 0
3894 | 970.8864 | 0 | 0 | 0 | 0 | 310.6 | 0 | 0 | 0 | 1155354.8261 | 0
3895 | 956.4739 | 436.3531 | 436.3531 | 424.7725 | 424.7725 | 313.7 | 140316.1151 | 152918.0924 | 69365.3458 | 974608.6938 | 701141.6181
3896 | 799.5406 | 830.5659 | 830.5659 | 808.5232 | 799.5406 | 345.1 | 289755.2258 | 287834.6114 | 130564.9779 | 0 | 1323159.7178
3897 | 1009.7099 | 1048.8915 | 1048.8915 | 1021.0545 | 1009.7099 | 649.35 | 689098.2955 | 363495.5687 | 164885.6288 | 0 | 1363764.694
3898 | 1208.6635 | 2164.4775 | 1255.5649 | 2107.0334 | 1208.6635 | 670.85 | 851998.3913 | 435118.8517 | 197374.7458 | 0 | 1606495.0605
3899 | 1010.5833 | 1715.8707 | 1049.7995 | 1670.3324 | 1010.5833 | 427.1 | 454783.2828 | 363810.0035 | 165028.2599 | 0 | 1589546.5402
3900 | 1237.7156 | 1498.1704 | 1285.7453 | 1458.4098 | 1237.7156 | 420.5 | 547190.3754 | 445577.6153 | 202118.9572 | 0 | 1954971.787
3901 | 1291.5998 | 2901.5094 | 1341.7202 | 2824.505 | 1291.5998 | 422.45 | 571607.3898 | 464975.9258 | 210918.2464 | 0 | 2037563.255
3902 | 1072.2006 | 272.3341 | 272.3341 | 265.1065 | 265.1065 | 451.55 | 125910.5898 | 95438.3376 | 43291.8904 | 1479403.5196 | 401819.6781
3903 | 1315.8048 | 193.4701 | 193.4701 | 188.3355 | 188.3355 | 463.8 | 92032.4479 | 67800.7877 | 30755.1906 | 2066651.2573 | 283201.5424
3904 | 1295.1505 | 235.6082 | 235.6082 | 229.3553 | 229.3553 | 956.65 | 230630.9193 | 82567.8992 | 37453.7165 | 1953602.6774 | 234235.205
3905 | 1370.3069 | 120.172 | 120.172 | 116.9827 | 116.9827 | 1561.75 | 191712.6372 | 42113.7896 | 19103.2829 | 2297343.1138 | 50183.5693
3906 | 1281.582 | 79.1413 | 79.1413 | 77.041 | 77.041 | 1488.7 | 120613.6868 | 27734.7498 | 12580.7907 | 2207923.725 | 38557.6443
3907 | 1545.3275 | 0 | 0 | 0 | 0 | 1496.95 | 0 | 0 | 0 | 5251022.9571 | 0
3908 | 1218.0211 | 0 | 0 | 0 | 0 | 1555.55 | 0 | 0 | 0 | 4138835.8031 | 0
3909 | 1410.7274 | 0 | 0 | 0 | 0 | 1637.85 | 0 | 0 | 0 | 4793651.6101 | 0
3910 | 1444.5613 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1825.65 | 595177.7485 | 111351.8261 | 50510.4255 | 3857581.7599 | 53329.1319
3911 | 1081.9499 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1813.7 | 1146393.289 | 215514.4963 | 97759.7701 | 1642248.4747 | 110289.6
3912 | 1302.6059 | 0 | 0 | 0 | 0 | 1630.45 | 0 | 0 | 0 | 2387676.6715 | 0
3913 | 1140.056 | 0 | 0 | 0 | 0 | 1340.45 | 0 | 0 | 0 | 1356666.6519 | 0
3914 | 1240.0867 | 0 | 0 | 0 | 0 | 338.15 | 0 | 0 | 0 | 1475703.2099 | 0
3915 | 1393.0749 | 0 | 0 | 0 | 0 | 327.2 | 0 | 0 | 0 | 1657759.1215 | 0
3916 | 1256.2682 | 0 | 0 | 0 | 0 | 319.4 | 0 | 0 | 0 | 1494959.1235 | 0
3917 | 1270.2431 | 0 | 0 | 0 | 0 | 313.5 | 0 | 0 | 0 | 1511589.2307 | 0
3918 | 1252.5906 | 0 | 0 | 0 | 0 | 310.55 | 0 | 0 | 0 | 1490582.7795 | 0
3919 | 624.6762 | 233.3072 | 233.3072 | 227.1154 | 227.1154 | 313.65 | 74815.9731 | 81761.5401 | 37087.9431 | 728729.0067 | 374894.1548
3920 | 1045.7035 | 712.9857 | 712.9857 | 694.0635 | 694.0635 | 344.9 | 250655.2194 | 249862.8472 | 113340.5637 | 644556.1926 | 1124445.1482
3921 | 811.5093 | 962.7352 | 843.0004 | 937.1847 | 811.5093 | 674.25 | 574125.4258 | 292143.3611 | 132519.4747 | 0 | 1075858.5029
3922 | 397.7894 | 1611.9092 | 413.2251 | 1569.13 | 397.7894 | 1010.25 | 421640.1482 | 143204.2007 | 64959.0166 | 0 | 393712.1045
3923 | 357.9482 | 2137.4675 | 371.8381 | 2080.7403 | 357.9482 | 427.25 | 161661.1226 | 128861.3399 | 58452.9356 | 0 | 562962.9785
3924 | 364.5053 | 2646.621 | 378.6495 | 2576.3812 | 364.5053 | 420.55 | 161500.837 | 131221.9178 | 59523.7199 | 0 | 575717.939
3925 | 782.6071 | 2742.8601 | 812.9759 | 2670.066 | 782.6071 | 422.45 | 347292.9093 | 281738.548 | 127799.7358 | 0 | 1234601.7956
3926 | 1248.8063 | 1068.873 | 1068.873 | 1040.5056 | 1040.5056 | 451.75 | 495267.4406 | 374582.0327 | 169914.572 | 381815.1348 | 1576884.8838
3927 | 1519.8933 | 791.2223 | 791.2223 | 770.2237 | 770.2237 | 463.8 | 375826.702 | 277280.514 | 125777.5221 | 1374144.3803 | 1158188.8022
3928 | 1361.4245 | 340.8059 | 340.8059 | 331.7611 | 331.7611 | 851.4 | 297227.3787 | 119433.9837 | 54176.5821 | 1887373.1609 | 372999.8098
3929 | 1399.7203 | 702.0627 | 702.0627 | 683.4303 | 683.4303 | 1223.25 | 879247.2417 | 246034.9166 | 111604.1719 | 1312959.5539 | 519625.5545
3930 | 1546.8023 | 294.6352 | 294.6352 | 286.8157 | 286.8157 | 787.1 | 237823.5972 | 103253.6504 | 46837.0031 | 2309555.356 | 340520.4621
3931 | 1616.673 | 0 | 0 | 0 | 0 | 775.35 | 0 | 0 | 0 | 5493454.7657 | 0
3932 | 1468.8335 | 0 | 0 | 0 | 0 | 1488.6 | 0 | 0 | 0 | 4991096.0733 | 0
3933 | 1634.3255 | 0 | 0 | 0 | 0 | 1749.05 | 0 | 0 | 0 | 5553437.8927 | 0
3934 | 1700.5223 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1825.65 | 592822.3554 | 111351.8261 | 50510.4255 | 4727337.1088 | 53329.1319
3935 | 1246.7064 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1819.75 | 1147709.4511 | 215514.4963 | 97759.7701 | 2202091.0005 | 106708
3936 | 1177.5675 | 0 | 0 | 0 | 0 | 1798.05 | 0 | 0 | 0 | 2158481.2825 | 0
3937 | 1148.1467 | 0 | 0 | 0 | 0 | 1755.55 | 0 | 0 | 0 | 1366294.6087 | 0
3938 | 1455.5941 | 0 | 0 | 0 | 0 | 1176.6 | 0 | 0 | 0 | 1732156.9707 | 0
3939 | 1526.204 | 0 | 0 | 0 | 0 | 1115.65 | 0 | 0 | 0 | 1816182.7755 | 0
3940 | 902.483 | 0 | 0 | 0 | 0 | 569 | 0 | 0 | 0 | 1073954.827 | 0
3941 | 1237.1447 | 0 | 0 | 0 | 0 | 563.1 | 0 | 0 | 0 | 1472202.1347 | 0
3942 | 1238.6157 | 0 | 0 | 0 | 0 | 1098.95 | 0 | 0 | 0 | 1473952.6723 | 0
3943 | 993.8319 | 262.3927 | 262.3927 | 255.429 | 255.429 | 982.25 | 265759.3748 | 91954.4293 | 41711.5508 | 1353492.5236 | 254462.9438
3944 | 1094.5292 | 804.3341 | 804.3341 | 782.9875 | 782.9875 | 345.1 | 285888.0511 | 281875.4869 | 127861.8528 | 571055.9292 | 1268355.0776
3945 | 975.5698 | 1013.4267 | 1013.4267 | 986.531 | 975.5698 | 794.1 | 813330.2445 | 351205.1396 | 159310.5536 | 0 | 1176439.6605
3946 | 1525.9328 | 1585.1464 | 1585.1464 | 1543.0775 | 1525.9328 | 1065 | 1707892.6003 | 549335.8044 | 249184.8246 | 0 | 1426747.1587
3947 | 1595.194 | 2234.3142 | 1657.0951 | 2175.0168 | 1595.194 | 1016.1 | 1710178.1885 | 574269.8224 | 260495.1722 | 0 | 1569511.3284
3948 | 1689.2072 | 2335.6341 | 1754.7563 | 2273.6476 | 1689.2072 | 420.6 | 749110.7853 | 608114.5916 | 275847.5356 | 0 | 2667933.8501
3949 | 1412.9376 | 2246.2615 | 1467.7667 | 2186.647 | 1412.9376 | 422.55 | 628345.7834 | 508657.5396 | 230732.7117 | 0 | 2228838.4329
3950 | 1322.0172 | 2585.1747 | 1373.3175 | 2516.5656 | 1322.0172 | 1245.3 | 1734677.7037 | 475926.2006 | 215885.4127 | 0 | 997726.399
3951 | 1567.5485 | 2491.1005 | 1628.3763 | 2424.9881 | 1567.5485 | 1302.1 | 2147446.1666 | 564317.4643 | 255980.672 | 0 | 1093992.1065
3952 | 1329.2253 | 1809.6425 | 1380.8052 | 1761.6156 | 1329.2253 | 1584.55 | 2215936.5111 | 478521.1152 | 217062.4948 | 0 | 552226.6592
3953 | 1391.3492 | 635.6602 | 635.6602 | 618.7901 | 618.7901 | 1849.8 | 1202590.0538 | 222764.4476 | 101048.4286 | 1416100.731 | 90976.2902
3954 | 1660.1588 | 200.6742 | 200.6742 | 195.3484 | 195.3484 | 1813.9 | 372997.9853 | 70325.4381 | 31900.4001 | 2684997.3107 | 35585.2976
3955 | 1308.4901 | 0 | 0 | 0 | 0 | 1820.05 | 0 | 0 | 0 | 4446249.3292 | 0
3956 | 1471.04 | 0 | 0 | 0 | 0 | 1898.6 | 0 | 0 | 0 | 4998593.9642 | 0
3957 | 1597.5495 | 0 | 0 | 0 | 0 | 1902.9 | 0 | 0 | 0 | 5428473.0447 | 0
3958 | 1294.5152 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1913.55 | 622543.3146 | 111351.8261 | 50510.4255 | 3347725.1732 | 26442.8073
3959 | 1450.4455 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1907.65 | 1203642.9833 | 215514.4963 | 97759.7701 | 2894396.2652 | 54671.2
3960 | 1306.2835 | 0 | 0 | 0 | 0 | 1892 | 0 | 0 | 0 | 2394417.7123 | 0
3961 | 956.176 | 0 | 0 | 0 | 0 | 1826.45 | 0 | 0 | 0 | 1752670.6232 | 0
3962 | 976.035 | 0 | 0 | 0 | 0 | 1847.1 | 0 | 0 | 0 | 1789072.2439 | 0
3963 | 779.6512 | 0 | 0 | 0 | 0 | 1783.95 | 0 | 0 | 0 | 1429100.6621 | 0
3964 | 1012.811 | 0 | 0 | 0 | 0 | 1745.45 | 0 | 0 | 0 | 1856482.6528 | 0
3965 | 668.5877 | 0 | 0 | 0 | 0 | 1728.55 | 0 | 0 | 0 | 1225521.2281 | 0
3966 | 831.1376 | 0 | 0 | 0 | 0 | 1725.5 | 0 | 0 | 0 | 1523475.2342 | 0
3967 | 843.9182 | 225.028 | 225.028 | 219.0558 | 219.0558 | 1407.25 | 325249.4713 | 78860.1034 | 35771.8191 | 1145372.6766 | 127098.6405
3968 | 837.4805 | 686.7455 | 686.7455 | 668.5197 | 668.5197 | 1024.85 | 718913.3022 | 240667.0766 | 109169.26 | 309705.3125 | 638116.7067
3969 | 846.0043 | 878.833 | 878.833 | 855.5092 | 846.0043 | 1404.7 | 1246876.4943 | 304561.5499 | 138152.5031 | 0 | 503626.1812
3970 | 975.8383 | 1220.8864 | 1013.7051 | 1188.4848 | 975.8383 | 1565.35 | 1605461.4922 | 351301.7869 | 159354.3939 | 0 | 424148.1157
3971 | 936.9532 | 2728.8622 | 973.3112 | 2656.4396 | 936.9532 | 1138 | 1123814.2076 | 337303.1495 | 153004.4564 | 0 | 807653.6524
3972 | 911.1879 | 2339.1172 | 946.5464 | 2277.0383 | 911.1879 | 1309 | 1262116.4312 | 328027.6538 | 148796.9885 | 0 | 629630.8576
3973 | 1051.1298 | 2102.5928 | 1091.9188 | 2046.7911 | 1051.1298 | 1501.2 | 1658021.9719 | 378406.7287 | 171649.4967 | 0 | 524303.5452
3974 | 1012.9324 | 1890.7649 | 1052.2386 | 1840.585 | 1012.9324 | 1861.6 | 1987506.8922 | 364655.6676 | 165411.8626 | 0 | 140189.8455
3975 | 1027.0912 | 2059.7275 | 1066.947 | 2005.0635 | 1027.0912 | 1889.65 | 2048641.3755 | 369752.8212 | 167723.9881 | 0 | 113339.5106
3976 | 478.6691 | 1054.7088 | 497.2436 | 1026.7175 | 478.6691 | 1913.65 | 966020.1033 | 172320.8634 | 78166.6583 | 0 | 41333.0738
3977 | 176.7969 | 766.6847 | 183.6576 | 746.3373 | 176.7969 | 1943.75 | 360266.127 | 63646.8998 | 28870.9409 | 0 | 9944.8281
3978 | 236.4577 | 245.6337 | 245.6337 | 239.1147 | 236.4577 | 1857.85 | 462323.3863 | 85124.7828 | 38613.5473 | 0 | 33612.4663
3979 | 138.2778 | 143.6438 | 143.6438 | 139.8316 | 138.2778 | 1802.1 | 261984.9935 | 49779.994 | 22580.7584 | 0 | 27365.1689
3980 | 145.633 | 151.2843 | 151.2843 | 147.2693 | 145.633 | 1820.6 | 278342.6543 | 52427.8661 | 23781.8626 | 0 | 26126.5533
3981 | 115.4766 | 119.9581 | 119.9581 | 116.7744 | 115.4766 | 1863.9 | 225645.9393 | 41571.5908 | 18857.3355 | 0 | 15716.3708
3982 | 110.328 | 114.6093 | 114.6093 | 111.5676 | 110.328 | 1913.55 | 221323.6492 | 39718.0804 | 18016.5626 | 0 | 9537.8556
3983 | 105.9149 | 110.025 | 110.025 | 107.105 | 105.9149 | 1907.65 | 212951.2297 | 38129.3571 | 17295.9001 | 0 | 9781.2393
3984 | 106.6504 | 110.7885 | 110.7885 | 107.8483 | 106.6504 | 1865.8 | 210104.4586 | 38394.1443 | 17416.0105 | 0 | 14312.43
3985 | 98.5597 | 0 | 0 | 0 | 0 | 1827.4 | 0 | 0 | 0 | 117286.0202 | 0
3986 | 108.1214 | 0 | 0 | 0 | 0 | 1806.15 | 0 | 0 | 0 | 128664.5147 | 0
3987 | 88.9979 | 0 | 0 | 0 | 0 | 1794.6 | 0 | 0 | 0 | 105907.5257 | 0
3988 | 94.8821 | 0 | 0 | 0 | 0 | 1771.35 | 0 | 0 | 0 | 112909.6762 | 0
3989 | 88.9979 | 0 | 0 | 0 | 0 | 1746.7 | 0 | 0 | 0 | 105907.5257 | 0
3990 | 93.411 | 90.2472 | 90.2472 | 87.8521 | 87.8521 | 1736.8 | 161746.3907 | 31626.7523 | 14346.2463 | 6615.1517 | 22470.9632
3991 | 80.6148 | 83.7422 | 83.7422 | 81.5197 | 80.6148 | 1637.65 | 139904.4667 | 29021.3393 | 13164.402 | 0 | 29210.7842
3992 | 145.6072 | 151.2583 | 151.2583 | 147.244 | 145.6072 | 1228.4 | 189026.1711 | 52418.5985 | 23777.6587 | 0 | 112350.3612
3993 | 662.3137 | 688.0149 | 688.0149 | 669.7554 | 662.3137 | 1665.4 | 1162658.7381 | 238432.9321 | 108155.8272 | 0 | 221610.1641
3994 | 881.3451 | 1949.4168 | 915.5454 | 1897.6804 | 881.3451 | 1695.8 | 1576622.0829 | 317284.244 | 143923.6585 | 0 | 268105.1862
3995 | 1021.1849 | 2102.6696 | 1060.8118 | 2046.8659 | 1021.1849 | 1663.6 | 1796280.2576 | 367626.5798 | 166759.5014 | 0 | 343526.6152
3996 | 1073.9732 | 2815.8205 | 1115.6483 | 2741.0902 | 1073.9732 | 1531.55 | 1736916.5414 | 386630.3574 | 175379.826 | 0 | 503102.7526
3997 | 1076.9171 | 1679.4159 | 1118.7065 | 1634.8451 | 1076.9171 | 1230.9 | 1397131.2671 | 387690.1682 | 175860.568 | 0 | 828256.9678
3998 | 1076.9383 | 258.5959 | 258.5959 | 251.7329 | 251.7329 | 1763.35 | 469038.2643 | 90623.8457 | 41107.9833 | 1512601.453 | 58312.4532
3999 | 1164.3879 | 174.0019 | 174.0019 | 169.384 | 169.384 | 1732.75 | 310119.716 | 60978.2249 | 27660.4004 | 1823842.2823 | 44310.3173
4000 | 1132.1777 | 101.538 | 101.538 | 98.8432 | 98.8432 | 1796.4 | 187361.0138 | 35583.5548 | 16141.0958 | 1894102.0711 | 19698.7072
4001 | 1128.9285 | 463.9593 | 463.9593 | 451.6461 | 451.6461 | 1824.2 | 867849.8721 | 162592.5818 | 73753.8017 | 1241458.7334 | 77719.7736
4002 | 1028.4225 | 201.472 | 201.472 | 196.1251 | 196.1251 | 1779.8 | 369174.8145 | 70605.0245 | 32027.2236 | 1525601.1214 | 42273.3354
4003 | 1248.913 | 0 | 0 | 0 | 0 | 1769.6 | 0 | 0 | 0 | 4243806.2755 | 0
4004 | 980.4482 | 0 | 0 | 0 | 0 | 1791.05 | 0 | 0 | 0 | 3331562.8769 | 0
4005 | 989.2744 | 0 | 0 | 0 | 0 | 1805.25 | 0 | 0 | 0 | 3361554.4404 | 0
4006 | 925.2842 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1851.6 | 604988.2216 | 111351.8261 | 50510.4255 | 2093078.0895 | 45391.7016
4007 | 992.2165 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1876 | 1191905.9544 | 215514.4963 | 97759.7701 | 1337334.2445 | 73408
4008 | 1404.8432 | 0 | 0 | 0 | 0 | 1809.5 | 0 | 0 | 0 | 2575077.6076 | 0
4009 | 1122.4035 | 0 | 0 | 0 | 0 | 1781.9 | 0 | 0 | 0 | 1335660.2007 | 0
4010 | 848.7901 | 0 | 0 | 0 | 0 | 1757.35 | 0 | 0 | 0 | 1010060.204 | 0
4011 | 1120.197 | 0 | 0 | 0 | 0 | 1685.45 | 0 | 0 | 0 | 1333034.3943 | 0
4012 | 1104.0155 | 0 | 0 | 0 | 0 | 1569.55 | 0 | 0 | 0 | 1313778.4807 | 0
4013 | 823.7824 | 0 | 0 | 0 | 0 | 1485.15 | 0 | 0 | 0 | 980301.0646 | 0
4014 | 1180.5096 | 0 | 0 | 0 | 0 | 1450.5 | 0 | 0 | 0 | 1404806.4359 | 0
4015 | 1004.4362 | 171.1929 | 171.1929 | 166.6496 | 166.6496 | 1048.1 | 183765.0985 | 59993.8479 | 27213.876 | 1535662.9414 | 155277.7356
4016 | 1200.8854 | 537.3342 | 537.3342 | 523.0737 | 523.0737 | 300 | 164844.7821 | 188306.5192 | 85417.9294 | 1242428.8252 | 870415.3
4017 | 1296.0874 | 1339.012 | 1339.012 | 1303.4754 | 1296.0874 | 318.8 | 432189.3266 | 466591.4586 | 211651.07 | 0 | 2145048.1236
4018 | 905.5732 | 1246.9501 | 940.7135 | 1213.8567 | 905.5732 | 332.85 | 315821.0769 | 326006.3345 | 147880.0956 | 0 | 1509726.2792
4019 | 1261.7184 | 2401.6948 | 1310.6797 | 2337.9551 | 1261.7184 | 345.9 | 457780.379 | 454218.6146 | 206038.6105 | 0 | 2087008.3624
4020 | 1336.4693 | 3157.7981 | 1388.3303 | 3073.9919 | 1336.4693 | 348.15 | 489984.8874 | 481128.9379 | 218245.4321 | 0 | 2207646.767
4021 | 1087.4829 | 3064.9841 | 1129.6825 | 2983.6411 | 1087.4829 | 355.15 | 409013.0224 | 391493.8364 | 177585.9541 | 0 | 1788746.2135
4022 | 1175.372 | 2043.3404 | 1220.982 | 1989.1112 | 1175.372 | 371.1 | 461611.0745 | 423133.9211 | 191938.2481 | 0 | 1914563.4557
4023 | 1147.4094 | 618.3142 | 618.3142 | 601.9045 | 601.9045 | 375.7 | 238647.5871 | 216685.6282 | 98291.0086 | 999910.3866 | 956993.7039
4024 | 998.7939 | 342.2072 | 342.2072 | 333.1252 | 333.1252 | 366.25 | 128297.9752 | 119925.0801 | 54399.3488 | 1220170.6425 | 532731.5663
4025 | 1349.1184 | 275.758 | 275.758 | 268.4395 | 268.4395 | 348.95 | 98593.9738 | 96638.2291 | 43836.1745 | 1980884.337 | 433831.549
4026 | 1296.8027 | 66.8928 | 66.8928 | 65.1175 | 65.1175 | 1089.75 | 75123.1935 | 23442.2981 | 10633.6869 | 2257678.9428 | 58019.335
4027 | 1050.3226 | 0 | 0 | 0 | 0 | 1506 | 0 | 0 | 0 | 3568996.0895 | 0
4028 | 905.4251 | 0 | 0 | 0 | 0 | 1649.05 | 0 | 0 | 0 | 3076634.5846 | 0
4029 | 1113.5773 | 0 | 0 | 0 | 0 | 1662.25 | 0 | 0 | 0 | 3783935.6314 | 0
4030 | 1034.8766 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1787.75 | 585201.9341 | 111351.8261 | 50510.4255 | 2465473.3396 | 64921.7565
4031 | 1276.8627 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1800.1 | 1138225.2716 | 215514.4963 | 97759.7701 | 2304562.1759 | 118340.8
4032 | 906.1606 | 0 | 0 | 0 | 0 | 1773.9 | 0 | 0 | 0 | 1660992.4676 | 0
4033 | 1189.3358 | 0 | 0 | 0 | 0 | 1700.35 | 0 | 0 | 0 | 1415309.6615 | 0
4034 | 1040.0253 | 0 | 0 | 0 | 0 | 1747.1 | 0 | 0 | 0 | 1237630.0939 | 0
4035 | 1162.8571 | 0 | 0 | 0 | 0 | 1595.35 | 0 | 0 | 0 | 1383799.9847 | 0
4036 | 711.9834 | 0 | 0 | 0 | 0 | 1368.4 | 0 | 0 | 0 | 847260.2058 | 0
4037 | 1019.4307 | 0 | 0 | 0 | 0 | 1243.4 | 0 | 0 | 0 | 1213122.5675 | 0
4038 | 675.2074 | 0 | 0 | 0 | 0 | 1557.65 | 0 | 0 | 0 | 803496.7654 | 0
4039 | 747.1449 | 257.4657 | 257.4657 | 250.6327 | 250.6327 | 1292.55 | 340957.2043 | 90227.765 | 40928.3167 | 910106.8985 | 173559.416
4040 | 1067.6514 | 799.0465 | 799.0465 | 777.8403 | 777.8403 | 594.5 | 485492.8287 | 280022.4991 | 127021.317 | 531223.8299 | 1070128.023
4041 | 1143.193 | 1187.5543 | 1187.5543 | 1156.0373 | 1143.193 | 1110.65 | 1335434.6866 | 411549.4811 | 186683.4174 | 0 | 1016698.6946
4042 | 1219.8369 | 1630.2971 | 1267.1725 | 1587.0299 | 1219.8369 | 670.75 | 859662.781 | 439141.3006 | 199199.3733 | 0 | 1621468.2605
4043 | 1490.4715 | 2231.3349 | 1548.3094 | 2172.1165 | 1490.4715 | 427.1 | 671663.6849 | 536569.7515 | 243394.0012 | 0 | 2344362.6727
4044 | 1150.4507 | 2681.4189 | 1195.0929 | 2610.2555 | 1150.4507 | 420.5 | 509562.6953 | 414162.2686 | 187868.6068 | 0 | 1817136.9533
4045 | 1240.471 | 2959.59 | 1288.6072 | 2881.0441 | 1240.471 | 672 | 874194.7839 | 446569.5744 | 202568.9208 | 0 | 1647345.5411
4046 | 1223.9724 | 2958.6385 | 1271.469 | 2880.1178 | 1223.9724 | 1035.55 | 1335710.4998 | 440630.0665 | 199874.6941 | 0 | 1180460.1879
4047 | 1179.3466 | 2038.2481 | 1225.1102 | 1984.1542 | 1179.3466 | 1174.5 | 1455634.5247 | 424564.7648 | 192587.2947 | 0 | 973550.5927
4048 | 1321.3359 | 1920.1994 | 1372.6101 | 1869.2384 | 1321.3359 | 1167.95 | 1623541.0647 | 475680.9413 | 215774.1603 | 0 | 1099417.5755
4049 | 1489.5089 | 308.5634 | 308.5634 | 300.3743 | 300.3743 | 1783.85 | 561585.8819 | 108134.7625 | 49051.1298 | 2179683.6844 | 63552.423
4050 | 1368.6657 | 53.6636 | 53.6636 | 52.2394 | 52.2394 | 1720.9 | 94709.63 | 18806.1881 | 8530.6959 | 2413009.4621 | 14271.4994
4051 | 1199.6331 | 0 | 0 | 0 | 0 | 1628.2 | 0 | 0 | 0 | 4076353.3757 | 0
4052 | 1119.4615 | 0 | 0 | 0 | 0 | 1738.7 | 0 | 0 | 0 | 3803930.0071 | 0
4053 | 1075.3302 | 0 | 0 | 0 | 0 | 1813.9 | 0 | 0 | 0 | 3653972.1861 | 0
4054 | 1176.832 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1843.6 | 600530.1583 | 111351.8261 | 50510.4255 | 2947837.6562 | 47838.6936
4055 | 1138.585 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1802.15 | 1137298.8335 | 215514.4963 | 97759.7701 | 1834694.344 | 117127.2
4056 | 1338.6464 | 0 | 0 | 0 | 0 | 1660.95 | 0 | 0 | 0 | 2453738.8732 | 0
4057 | 1243.0288 | 0 | 0 | 0 | 0 | 1694.3 | 0 | 0 | 0 | 1479204.2851 | 0
4058 | 1127.5522 | 0 | 0 | 0 | 0 | 1589.2 | 0 | 0 | 0 | 1341787.0823 | 0
4059 | 1088.5696 | 0 | 0 | 0 | 0 | 1577.75 | 0 | 0 | 0 | 1295397.8347 | 0
4060 | 1187.8648 | 0 | 0 | 0 | 0 | 1452.9 | 0 | 0 | 0 | 1413559.1239 | 0
4061 | 1379.1 | 0 | 0 | 0 | 0 | 1312.5 | 0 | 0 | 0 | 1641129.0143 | 0
4062 | 1313.6387 | 0 | 0 | 0 | 0 | 1121.25 | 0 | 0 | 0 | 1563230.0899 | 0
4063 | 1192.7735 | 391.0155 | 391.0155 | 380.6381 | 380.6381 | 1143.45 | 457674.9391 | 137029.723 | 62158.2049 | 1488644.1287 | 319139.3948
4064 | 1204.4444 | 1251.1821 | 1251.1821 | 1217.9765 | 1204.4444 | 933.9 | 1181733.3061 | 433599.9664 | 196685.7625 | 0 | 1284057.7484
4065 | 914.0068 | 949.4748 | 949.4748 | 924.2763 | 914.0068 | 755.4 | 724863.5374 | 329042.4507 | 149257.3117 | 0 | 1137571.8676
4066 | 1054.7081 | 2727.4816 | 1095.6357 | 2655.0957 | 1054.7081 | 776.9 | 860094.7481 | 379694.9185 | 172233.8339 | 0 | 1290013.4857
4067 | 1164.4744 | 3007.7127 | 1209.6611 | 2927.8896 | 1164.4744 | 926.1 | 1133749.4645 | 419210.7678 | 190158.6622 | 0 | 1250529.0098
4068 | 1401.6253 | 3279.4079 | 1456.0157 | 3192.3742 | 1401.6253 | 670.1 | 986042.767 | 504585.1123 | 228885.4134 | 0 | 1864021.5024
4069 | 1428.7283 | 3231.6582 | 1484.1705 | 3145.8918 | 1428.7283 | 672.05 | 1006426.5454 | 514342.1898 | 233311.3322 | 0 | 1897279.7526
4070 | 1276.9675 | 3038.8384 | 1326.5204 | 2958.1893 | 1276.9675 | 1162.45 | 1560785.2355 | 459708.3155 | 208528.7998 | 0 | 1069524.1656
4071 | 1519.5135 | 2671.5492 | 1578.4784 | 2600.6478 | 1519.5135 | 464 | 741591.8643 | 547024.874 | 248136.5609 | 0 | 2333972.7959
4072 | 1443.7099 | 2282.6093 | 1499.7328 | 2222.0301 | 1443.7099 | 1167.95 | 1775917.1088 | 519735.5741 | 235757.8312 | 0 | 1201238.8456
4073 | 1342.0133 | 1111.2759 | 1111.2759 | 1081.7833 | 1081.7833 | 1702.95 | 1933623.5106 | 389441.9756 | 176655.2073 | 477001.5705 | 314546.245
4074 | 1332.7466 | 264.4797 | 264.4797 | 257.4605 | 257.4605 | 1516.9 | 409832.7215 | 92685.7952 | 42043.3065 | 1970999.3843 | 121748.4465
4075 | 1262.1523 | 0 | 0 | 0 | 0 | 1307.5 | 0 | 0 | 0 | 4288793.6207 | 0
4076 | 1451.9165 | 0 | 0 | 0 | 0 | 1646.6 | 0 | 0 | 0 | 4933612.2432 | 0
4077 | 1443.0903 | 0 | 0 | 0 | 0 | 1737.8 | 0 | 0 | 0 | 4903620.6797 | 0
4078 | 1423.9667 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1861.15 | 605146.5878 | 111351.8261 | 50510.4255 | 3787601.4416 | 42470.6049
4079 | 1318.0519 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1842.45 | 1164405.2473 | 215514.4963 | 97759.7701 | 2444522.8056 | 93269.6
4080 | 1204.7818 | 0 | 0 | 0 | 0 | 1804.1 | 0 | 0 | 0 | 2208364.9862 | 0
4081 | 1000.3072 | 0 | 0 | 0 | 0 | 1628.55 | 0 | 0 | 0 | 1190365.5787 | 0
4082 | 1279.8048 | 0 | 0 | 0 | 0 | 1598.95 | 0 | 0 | 0 | 1522967.7251 | 0
4083 | 1320.9939 | 0 | 0 | 0 | 0 | 1574.35 | 0 | 0 | 0 | 1571982.7791 | 0
4084 | 1414.405 | 0 | 0 | 0 | 0 | 1403.4 | 0 | 0 | 0 | 1683141.9167 | 0
4085 | 1349.6792 | 0 | 0 | 0 | 0 | 1124.3 | 0 | 0 | 0 | 1606118.2623 | 0
4086 | 1217.2856 | 0 | 0 | 0 | 0 | 1021.35 | 0 | 0 | 0 | 1448569.8771 | 0
4087 | 842.1704 | 306.2511 | 306.2511 | 298.1233 | 298.1233 | 1018.45 | 318922.2722 | 107324.3989 | 48683.5398 | 997238.2921 | 286432.9764
4088 | 1414.8031 | 934.0153 | 934.0153 | 909.2271 | 909.2271 | 594.4 | 566342.6229 | 327321.7423 | 148476.7792 | 926720.8283 | 1250975.5664
4089 | 1229.2948 | 1857.1388 | 1276.9975 | 1807.8513 | 1229.2948 | 1204.7 | 1550096.5035 | 442546.133 | 200743.8431 | 0 | 977658.1656
4090 | 1233.0561 | 2811.7536 | 1280.9044 | 2737.1312 | 1233.0561 | 1132.15 | 1462162.7822 | 443900.1884 | 201358.0577 | 0 | 1070107.7182
4091 | 1290.0993 | 2850.2351 | 1340.162 | 2774.5914 | 1290.0993 | 926.1 | 1255108.9511 | 464435.7599 | 210673.2211 | 0 | 1385437.6737
4092 | 1374.5232 | 1464.0696 | 1427.861 | 1425.214 | 1374.5232 | 1131.4 | 1635346.4103 | 494828.366 | 224459.6449 | 0 | 1193910.8854
4093 | 1301.6783 | 3121.1491 | 1352.1893 | 3038.3155 | 1301.6783 | 1401.5 | 1913759.5356 | 468604.1725 | 212564.0594 | 0 | 779054.4368
4094 | 1473.8341 | 618.3381 | 618.3381 | 601.9278 | 601.9278 | 1634.65 | 1033510.9026 | 216694.0013 | 98294.8067 | 1598204.2254 | 214132.0003
4095 | 1200.2556 | 1246.8316 | 1246.8316 | 1213.7414 | 1200.2556 | 1707.7 | 2157681.2619 | 432092.003 | 196001.7336 | 0 | 348278.0807
4096 | 1652.6215 | 166.4612 | 166.4612 | 162.0434 | 162.0434 | 1878.15 | 320921.0999 | 58335.624 | 26461.6872 | 2732229.6828 | 19327.3596
4097 | 1554.1529 | 129.5161 | 129.5161 | 126.0788 | 126.0788 | 1865.75 | 247665.108 | 45388.3722 | 20588.67 | 2617659.7194 | 16568.061
4098 | 1601.1342 | 32.6455 | 32.6455 | 31.7791 | 31.7791 | 1747.95 | 58713.5943 | 11440.4705 | 5189.5246 | 2876627.9169 | 7840.5194
4099 | 1579.897 | 0 | 0 | 0 | 0 | 1641.85 | 0 | 0 | 0 | 5368489.9177 | 0
4100 | 1123.8746 | 0 | 0 | 0 | 0 | 1804.65 | 0 | 0 | 0 | 3818925.7889 | 0
4101 | 1184.1872 | 0 | 0 | 0 | 0 | 1837.7 | 0 | 0 | 0 | 4023868.1396 | 0
4102 | 1214.3435 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1861.15 | 606449.1732 | 111351.8261 | 50510.4255 | 3075301.8046 | 42470.6049
4103 | 1265.0944 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1819.75 | 1151435.6397 | 215514.4963 | 97759.7701 | 2264573.4245 | 106708
4104 | 1221.6987 | 0 | 0 | 0 | 0 | 1720.85 | 0 | 0 | 0 | 2239373.7739 | 0
4105 | 1285.689 | 0 | 0 | 0 | 0 | 1603.65 | 0 | 0 | 0 | 1529969.8755 | 0
4106 | 1382.7776 | 0 | 0 | 0 | 0 | 1268 | 0 | 0 | 0 | 1645505.3583 | 0
4107 | 1180.5096 | 0 | 0 | 0 | 0 | 1038.05 | 0 | 0 | 0 | 1404806.4359 | 0
4108 | 1251.1195 | 0 | 0 | 0 | 0 | 1030.3 | 0 | 0 | 0 | 1488832.2419 | 0
4109 | 1314.3743 | 0 | 0 | 0 | 0 | 858.45 | 0 | 0 | 0 | 1564105.3587 | 0
4110 | 1123.8746 | 0 | 0 | 0 | 0 | 1071.3 | 0 | 0 | 0 | 1337410.7383 | 0
4111 | 1094.6009 | 401.3059 | 401.3059 | 390.6554 | 390.6554 | 1227.95 | 504029.545 | 140635.9504 | 63794.0297 | 1290332.0214 | 295225.7436
4112 | 1132.8406 | 1026.8595 | 1026.8595 | 999.6072 | 999.6072 | 1055.8 | 1109346.975 | 359858.6065 | 163235.8623 | 244216.6731 | 923863.8204
4113 | 1145.5301 | 1189.983 | 1189.983 | 1158.4015 | 1145.5301 | 1603.35 | 1929904.0577 | 412390.8425 | 187065.0683 | 0 | 454374.4745
4114 | 1243.3736 | 1849.4392 | 1291.6228 | 1800.356 | 1243.3736 | 1710.45 | 2234097.9848 | 447614.491 | 203042.9066 | 0 | 360018.8218
4115 | 952.8174 | 2558.8503 | 989.7908 | 2490.9398 | 952.8174 | 1684.05 | 1689005.2505 | 343014.2784 | 155595.088 | 0 | 301042.6702
4116 | 1336.7828 | 2568.7398 | 1388.6565 | 2500.5668 | 1336.7828 | 1769.6 | 2485730.6147 | 481241.8037 | 218296.6293 | 0 | 307994.7544
4117 | 1269.4781 | 2871.5254 | 1318.7408 | 2795.3167 | 1269.4781 | 1677.45 | 2231433.122 | 457012.1196 | 207305.7754 | 0 | 409470.1644
4118 | 1515.3156 | 2841.3107 | 1574.1175 | 2765.9039 | 1515.3156 | 1723.65 | 2750607.4673 | 545513.6012 | 247451.0308 | 0 | 418757.4547
4119 | 1178.0217 | 2433.9299 | 1223.7338 | 2369.3347 | 1178.0217 | 1744.1 | 2166633.5772 | 424087.817 | 192370.9459 | 0 | 301455.7566
4120 | 1291.1281 | 834.7554 | 834.7554 | 812.6015 | 812.6015 | 1866.05 | 1605450.6928 | 292536.5377 | 132697.8239 | 877139.3467 | 106545.4374
4121 | 1202.7821 | 950.953 | 950.953 | 925.7153 | 925.7153 | 1860.8 | 1814152.1463 | 333257.4921 | 151169.3013 | 507863.4797 | 126133.8528
4122 | 1153.1952 | 123.5554 | 123.5554 | 120.2763 | 120.2763 | 1730.65 | 219905.8307 | 43299.4834 | 19641.1268 | 1893340.1827 | 31711.1142
4123 | 1228.3184 | 0 | 0 | 0 | 0 | 1647.7 | 0 | 0 | 0 | 4173825.9606 | 0
4124 | 785.5354 | 0 | 0 | 0 | 0 | 1650.45 | 0 | 0 | 0 | 2669249.1767 | 0
4125 | 1207.7239 | 0 | 0 | 0 | 0 | 1657.9 | 0 | 0 | 0 | 4103845.6457 | 0
4126 | 1132.7008 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1825.65 | 593240.8783 | 111351.8261 | 50510.4255 | 2797879.8386 | 53329.1319
4127 | 1078.2723 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1813.7 | 1146179.0376 | 215514.4963 | 97759.7701 | 1629751.9899 | 110289.6
4128 | 1233.4671 | 0 | 0 | 0 | 0 | 1649.7 | 0 | 0 | 0 | 2260945.1045 | 0
4129 | 1003.9848 | 0 | 0 | 0 | 0 | 1229.55 | 0 | 0 | 0 | 1840304.1549 | 0
4130 | 1147.4112 | 0 | 0 | 0 | 0 | 1243 | 0 | 0 | 0 | 2103204.7479 | 0
4131 | 1050.3226 | 0 | 0 | 0 | 0 | 1038.05 | 0 | 0 | 0 | 1925241.269 | 0
4132 | 1001.0427 | 0 | 0 | 0 | 0 | 1030.3 | 0 | 0 | 0 | 1834911.3223 | 0
4133 | 899.541 | 0 | 0 | 0 | 0 | 1074.35 | 0 | 0 | 0 | 1648858.594 | 0
4134 | 956.9115 | 0 | 0 | 0 | 0 | 1021.35 | 0 | 0 | 0 | 1754018.8314 | 0
4135 | 789.213 | 184.5873 | 184.5873 | 179.6884 | 179.6884 | 1024.4 | 194378.3247 | 64687.841 | 29343.1234 | 1117258.4446 | 171596.3328
4136 | 1053.7961 | 584.149 | 584.149 | 568.646 | 568.646 | 949.85 | 569143.059 | 204712.5602 | 92859.8919 | 889280.0625 | 584532.3927
4137 | 1095.8283 | 1138.3524 | 1138.3524 | 1108.1411 | 1095.8283 | 1703.75 | 1962405.7329 | 394498.1783 | 178948.757 | 0 | 324639.045
4138 | 1072.8488 | 1402.6482 | 1114.4806 | 1365.4227 | 1072.8488 | 1842.35 | 2081097.6947 | 386225.564 | 175196.2072 | 0 | 169134.6116
4139 | 1035.489 | 1989.0555 | 1075.6709 | 1936.2671 | 1035.489 | 1836.1 | 2002115.6845 | 372776.0288 | 169095.3486 | 0 | 169716.642
4140 | 1331.4199 | 543.8517 | 543.8517 | 529.4182 | 529.4182 | 1693.6 | 942315.5598 | 190590.536 | 86453.9848 | 1470069.2489 | 158782.3016
4141 | 846.3463 | 853.0052 | 853.0052 | 830.3669 | 830.3669 | 1471.45 | 1284467.1652 | 298932.076 | 135598.9111 | 29290.3218 | 425183.5907
4142 | 916.9976 | 952.5819 | 952.5819 | 927.3009 | 916.9976 | 1684.4 | 1626789.9251 | 330119.1417 | 149745.7107 | 0 | 289404.4475
4143 | 791.3395 | 250.4112 | 250.4112 | 243.7654 | 243.7654 | 1562.6 | 401018.581 | 87755.537 | 39806.8867 | 1003703.4324 | 103479.6546
4144 | 216.0103 | 224.3922 | 224.3922 | 218.437 | 216.0103 | 1262 | 287574.0842 | 77763.6985 | 35274.4777 | 0 | 159415.38
4145 | 168.3081 | 174.8391 | 174.8391 | 170.199 | 168.3081 | 1691.7 | 299429.0495 | 60590.9245 | 27484.7166 | 0 | 51889.3945
4146 | 126.4653 | 131.3735 | 131.3735 | 127.8869 | 126.4653 | 1272.75 | 169843.7195 | 45527.5116 | 20651.7851 | 0 | 91971.6712
4147 | 136.0712 | 141.3512 | 141.3512 | 137.5998 | 136.0712 | 1091.9 | 156743.6167 | 48985.6324 | 22220.4272 | 0 | 123566.0751
4148 | 92.6755 | 96.2723 | 96.2723 | 93.7173 | 92.6755 | 1100.5 | 107647.0863 | 33363.1875 | 15133.9125 | 0 | 83361.631
4149 | 88.2624 | 91.687 | 91.687 | 89.2537 | 88.2624 | 1372.95 | 127513.8928 | 31774.4643 | 14413.25 | 0 | 55344.6871
4150 | 94.1466 | 97.8004 | 97.8004 | 95.2048 | 94.1466 | 1512.65 | 149871.308 | 33892.7619 | 15374.1334 | 0 | 45882.3264
4151 | 83.8493 | 87.1027 | 87.1027 | 84.7911 | 83.8493 | 1457.65 | 128900.7228 | 30185.7411 | 13692.5875 | 0 | 45475.5051
4152 | 91.94 | 95.5077 | 95.5077 | 92.973 | 91.94 | 1143.85 | 110689.599 | 33098.4003 | 15013.8021 | 0 | 78714.431
4153 | 82.3782 | 0 | 0 | 0 | 0 | 771.65 | 0 | 0 | 0 | 98030.1065 | 0
4154 | 88.2624 | 0 | 0 | 0 | 0 | 1067.85 | 0 | 0 | 0 | 105032.2569 | 0
4155 | 82.3782 | 0 | 0 | 0 | 0 | 696.95 | 0 | 0 | 0 | 98030.1065 | 0
4156 | 82.3782 | 0 | 0 | 0 | 0 | 327.35 | 0 | 0 | 0 | 98030.1065 | 0
4157 | 83.8493 | 0 | 0 | 0 | 0 | 320.65 | 0 | 0 | 0 | 99780.6441 | 0
4158 | 84.5848 | 0 | 0 | 0 | 0 | 315.7 | 0 | 0 | 0 | 100655.9129 | 0
4159 | 66.9323 | 69.5293 | 69.5293 | 67.684 | 66.9323 | 314.55 | 22129.157 | 24095.6354 | 10930.048 | 0 | 112810.5394
4160 | 82.3874 | 85.584 | 85.584 | 83.3127 | 82.3874 | 339.6 | 29404.4961 | 29659.4765 | 13453.8681 | 0 | 136795.3748
4161 | 584.9195 | 971.9078 | 607.6177 | 946.1139 | 584.9195 | 1103.1 | 679251.3543 | 210571.0297 | 95517.3587 | 0 | 524614.3237
4162 | 1157.201 | 1596.7977 | 1202.1059 | 1554.4195 | 1157.201 | 1110.55 | 1356015.1483 | 416592.3532 | 188970.9202 | 0 | 1029272.4126
4163 | 1150.5013 | 2350.9211 | 1195.1459 | 2288.5289 | 1150.5013 | 1097.5 | 1334647.3515 | 414180.4727 | 187876.8644 | 0 | 1038327.435
4164 | 990.4614 | 2859.2945 | 1028.8956 | 2783.4104 | 990.4614 | 407.55 | 426530.3584 | 356566.0874 | 161742.3391 | 0 | 1577260.1832
4165 | 1247.0319 | 3337.2943 | 1295.4228 | 3248.7243 | 1247.0319 | 661.8 | 868851.2731 | 448931.4761 | 203640.3057 | 0 | 1668778.0591
4166 | 1015.0755 | 3611.5024 | 1054.4658 | 3515.6551 | 1015.0755 | 1139.25 | 1224926.8863 | 365427.1912 | 165761.8342 | 0 | 873726.2633
4167 | 1035.2371 | 2480.3853 | 1075.4091 | 2414.5572 | 1035.2371 | 980.75 | 1076282.3232 | 372685.3394 | 169054.2109 | 0 | 1055165.3673
4168 | 965.4739 | 1832.0392 | 1002.939 | 1783.4178 | 965.4739 | 631.9 | 647717.6099 | 347570.6042 | 157661.888 | 0 | 1320864.8434
4169 | 874.7245 | 813.9378 | 813.9378 | 792.3363 | 792.3363 | 1183.85 | 991142.2832 | 285241.0807 | 129388.5236 | 151017.5476 | 632986.3524
4170 | 1044.9992 | 179.6789 | 179.6789 | 174.9104 | 174.9104 | 730.15 | 135158.1536 | 62967.7295 | 28562.8617 | 1594872.923 | 217412.2883
4171 | 962.7957 | 0 | 0 | 0 | 0 | 360.6 | 0 | 0 | 0 | 3271579.7492 | 0
4172 | 1037.8187 | 0 | 0 | 0 | 0 | 369.95 | 0 | 0 | 0 | 3526508.0411 | 0
4173 | 715.661 | 0 | 0 | 0 | 0 | 738.55 | 0 | 0 | 0 | 2431815.9631 | 0
4174 | 1001.7782 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 753.95 | 245804.0047 | 111351.8261 | 50510.4255 | 2353004.9764 | 381134.2977
4175 | 876.0043 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 393.5 | 248947.6563 | 215514.4963 | 97759.7701 | 942445.3211 | 951048
4176 | 918.6645 | 0 | 0 | 0 | 0 | 378.5 | 0 | 0 | 0 | 1683912.0065 | 0
4177 | 882.624 | 0 | 0 | 0 | 0 | 726.55 | 0 | 0 | 0 | 1050322.5692 | 0
4178 | 1200.3686 | 0 | 0 | 0 | 0 | 1097.6 | 0 | 0 | 0 | 1428438.6935 | 0
4179 | 1074.5947 | 0 | 0 | 0 | 0 | 1086.25 | 0 | 0 | 0 | 1278767.7275 | 0
4180 | 1248.913 | 0 | 0 | 0 | 0 | 1059 | 0 | 0 | 0 | 1486206.4355 | 0
4181 | 1179.0386 | 0 | 0 | 0 | 0 | 313.6 | 0 | 0 | 0 | 1403055.8983 | 0
4182 | 1068.7106 | 0 | 0 | 0 | 0 | 303.05 | 0 | 0 | 0 | 1271765.5771 | 0
4183 | 955.4405 | 322.8034 | 322.8034 | 314.2364 | 314.2364 | 292.7 | 96477.9349 | 113125.0881 | 51314.7969 | 1175327.175 | 525148.407
4184 | 993.9174 | 991.6243 | 991.6243 | 965.3071 | 965.3071 | 299.9 | 303501.2121 | 347510.5724 | 157634.6569 | 52442.5574 | 1606402.3887
4185 | 746.5353 | 775.5041 | 775.5041 | 754.9226 | 746.5353 | 318.8 | 249079.3211 | 268752.7216 | 121909.2207 | 0 | 1255074.642
4186 | 1054.2475 | 729.3573 | 729.3573 | 710.0005 | 710.0005 | 332.85 | 247374.2424 | 255600.1926 | 115943.0873 | 631004.6651 | 1147280.9483
4187 | 1269.1333 | 1337.3458 | 1318.3824 | 1301.8534 | 1269.1333 | 345.9 | 462657.9913 | 456888.0006 | 207249.4736 | 0 | 2099272.8953
4188 | 1079.2074 | 1544.9218 | 1121.0864 | 1503.9205 | 1079.2074 | 348.15 | 397989.9265 | 388514.6492 | 176234.5617 | 0 | 1782688.676
4189 | 1049.5751 | 1266.6905 | 1090.3035 | 1233.0732 | 1049.5751 | 355.15 | 395087.5742 | 377847.0349 | 171395.6133 | 0 | 1726393.5983
4190 | 1119.0192 | 901.507 | 901.507 | 877.5815 | 877.5815 | 371.1 | 344133.6528 | 315929.3257 | 143309.0524 | 442555.4101 | 1399252.7913
4191 | 1490.9597 | 1327.3889 | 1327.3889 | 1292.1607 | 1292.1607 | 375.7 | 512016.1411 | 465177.8469 | 211009.84 | 364398.6534 | 2046041.3735
4192 | 567.8021 | 589.8354 | 589.8354 | 574.1815 | 567.8021 | 366.25 | 218417.4344 | 204408.7695 | 92722.0891 | 0 | 927646.7423
4193 | 1329.9719 | 1080.3995 | 1080.3995 | 1051.7263 | 1051.7263 | 348.95 | 385772.3166 | 378621.4733 | 171746.9072 | 510024.1083 | 1699719.6519
4194 | 1208.3058 | 262.5995 | 262.5995 | 255.6302 | 255.6302 | 334.35 | 90104.7588 | 92026.8742 | 41744.4126 | 1746254.4206 | 416783.94
4195 | 1031.9346 | 0 | 0 | 0 | 0 | 673.95 | 0 | 0 | 0 | 3506513.6655 | 0
4196 | 898.0699 | 0 | 0 | 0 | 0 | 1085.7 | 0 | 0 | 0 | 3051641.6147 | 0
4197 | 1109.1642 | 0 | 0 | 0 | 0 | 1093.9 | 0 | 0 | 0 | 3768939.8497 | 0
4198 | 1198.8976 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1109.35 | 361827.3149 | 111351.8261 | 50510.4255 | 3022816.565 | 272426.6781
4199 | 1042.9674 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 912.55 | 576681.9588 | 215514.4963 | 97759.7701 | 1509785.7358 | 643770.4
4200 | 873.0622 | 0 | 0 | 0 | 0 | 358.85 | 0 | 0 | 0 | 1600323.0999 | 0
4201 | 1123.8746 | 0 | 0 | 0 | 0 | 356.45 | 0 | 0 | 0 | 1337410.7383 | 0
4202 | 782.5933 | 0 | 0 | 0 | 0 | 338.1 | 0 | 0 | 0 | 931286.0113 | 0
4203 | 1155.5019 | 0 | 0 | 0 | 0 | 327.15 | 0 | 0 | 0 | 1375047.2967 | 0
4204 | 1004.7203 | 0 | 0 | 0 | 0 | 319.4 | 0 | 0 | 0 | 1195617.1915 | 0
4205 | 945.8787 | 0 | 0 | 0 | 0 | 313.5 | 0 | 0 | 0 | 1125595.6867 | 0
4206 | 1001.0427 | 0 | 0 | 0 | 0 | 310.45 | 0 | 0 | 0 | 1191240.8475 | 0
4207 | 1244.4999 | 374.2377 | 374.2377 | 364.3057 | 364.3057 | 313.5 | 120394.4467 | 131150.0361 | 59491.1136 | 1613395.9596 | 601405.9
4208 | 641.0608 | 665.9372 | 665.9372 | 648.2636 | 641.0608 | 344.9 | 233405.9047 | 230781.9059 | 104685.2367 | 0 | 1061019.8122
4209 | 822.6911 | 1758.3516 | 854.6153 | 1711.6859 | 822.6911 | 1314.2 | 1140697.5717 | 296168.7886 | 134345.4533 | 0 | 564201.5423
4210 | 1162.7946 | 3075.6567 | 1207.9159 | 2994.0305 | 1162.7946 | 1226.2 | 1503961.9063 | 418606.06 | 189884.36 | 0 | 899770.47
4211 | 1141.8157 | 2820.3923 | 1186.1239 | 2745.5406 | 1141.8157 | 956.1 | 1153995.4802 | 411053.6671 | 186458.5107 | 0 | 1191941.4531
4212 | 1203.114 | 2914.5849 | 1249.8005 | 2837.2334 | 1203.114 | 420.5 | 532868.1331 | 433121.0324 | 196468.5128 | 0 | 1900318.5298
4213 | 999.0366 | 2847.9809 | 1037.8033 | 2772.397 | 999.0366 | 422.45 | 442714.4337 | 359653.1752 | 163142.6764 | 0 | 1576030.185
4214 | 1206.6721 | 2671.6677 | 1253.4966 | 2600.763 | 1206.6721 | 451.55 | 575262.2081 | 434401.9405 | 197049.5469 | 0 | 1868471.3467
4215 | 1353.2033 | 2106.1174 | 1405.7137 | 2050.2222 | 1353.2033 | 463.6 | 663617.282 | 487153.1779 | 220978.0943 | 0 | 2079061.5071
4216 | 1525.3618 | 2153.8079 | 1584.5533 | 2096.647 | 1525.3618 | 812.5 | 1311063.9627 | 549130.2635 | 249091.589 | 0 | 1811367.1886
4217 | 1270.7349 | 787.5501 | 787.5501 | 766.6489 | 766.6489 | 1239.7 | 1001458.9681 | 275993.6158 | 125193.7707 | 923989.6329 | 570552.6893
4218 | 1248.3052 | 247.6666 | 247.6666 | 241.0937 | 241.0937 | 1103.7 | 280509.0097 | 86793.7308 | 39370.6007 | 1846218.7718 | 211521.4222
4219 | 1187.8648 | 0 | 0 | 0 | 0 | 1091.9 | 0 | 0 | 0 | 4036364.6244 | 0
4220 | 1119.4615 | 0 | 0 | 0 | 0 | 1200.4 | 0 | 0 | 0 | 3803930.0071 | 0
4221 | 1184.1872 | 0 | 0 | 0 | 0 | 1248.85 | 0 | 0 | 0 | 4023868.1396 | 0
4222 | 1246.7064 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1284.5 | 418621.3089 | 111351.8261 | 50510.4255 | 3185270.8708 | 218852.847
4223 | 890.7147 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 754.1 | 478457.9006 | 215514.4963 | 97759.7701 | 992431.261 | 737572.8
4224 | 1162.1216 | 0 | 0 | 0 | 0 | 738.45 | 0 | 0 | 0 | 2130168.9111 | 0
4225 | 1210.6659 | 0 | 0 | 0 | 0 | 1067.35 | 0 | 0 | 0 | 1440692.4579 | 0
4226 | 1075.3302 | 0 | 0 | 0 | 0 | 338.4 | 0 | 0 | 0 | 1279642.9963 | 0
4227 | 1067.2395 | 0 | 0 | 0 | 0 | 327.35 | 0 | 0 | 0 | 1270015.0395 | 0
4228 | 1099.6024 | 0 | 0 | 0 | 0 | 319.6 | 0 | 0 | 0 | 1308526.8679 | 0
4229 | 772.296 | 0 | 0 | 0 | 0 | 643.2 | 0 | 0 | 0 | 919032.248 | 0
4230 | 1059.8843 | 0 | 0 | 0 | 0 | 1021.35 | 0 | 0 | 0 | 1261262.3515 | 0
4231 | 649.4642 | 408.1069 | 408.1069 | 397.276 | 397.276 | 669.15 | 282509.7478 | 143019.3514 | 64875.1669 | 462260.9515 | 517531.6321
4232 | 882.1064 | 916.3359 | 916.3359 | 892.0168 | 882.1064 | 345 | 322336.7628 | 317558.2988 | 144047.9728 | 0 | 1459886.068
4233 | 827.5326 | 1805.667 | 859.6452 | 1757.7456 | 827.5326 | 1179.7 | 1033284.5967 | 297911.7503 | 135136.0801 | 0 | 678825.0244
4234 | 1054.0186 | 3122.4497 | 1094.9189 | 3039.5816 | 1054.0186 | 1026.2 | 1144948.7689 | 379446.6805 | 172121.2304 | 0 | 1026403.2708
4235 | 1307.932 | 3615.9973 | 1358.686 | 3520.0307 | 1307.932 | 427.1 | 592562.4613 | 470855.5258 | 213585.2982 | 0 | 2057246.268
4236 | 1422.7357 | 3837.3936 | 1477.9449 | 3735.5512 | 1422.7357 | 420.5 | 633576.6082 | 512184.8362 | 232332.7326 | 0 | 2247210.9687
4237 | 1374.2539 | 3794.3746 | 1427.5805 | 3693.6739 | 1374.2539 | 422.45 | 613845.2388 | 494731.3878 | 224415.6545 | 0 | 2167954.169
4238 | 1156.3257 | 3471.2575 | 1201.1959 | 3379.1322 | 1156.3257 | 451.55 | 556111.9391 | 416277.2563 | 188827.9888 | 0 | 1790512.5487
4239 | 1129.0885 | 2928.3584 | 1172.902 | 2850.6413 | 1129.0885 | 798.1 | 960092.9088 | 406471.8553 | 184380.1499 | 0 | 1357051.4525
4240 | 1626.5602 | 2179.9006 | 1689.6783 | 2122.0472 | 1626.5602 | 1425.3 | 2465865.2187 | 585561.6727 | 265617.281 | 0 | 934784.1481
4241 | 1795.9293 | 1181.3277 | 1181.3277 | 1149.9759 | 1149.9759 | 1712.7 | 2083477.2646 | 413991.3338 | 187791.0689 | 1184032.556 | 323399.245
4242 | 1420.2091 | 178.4199 | 178.4199 | 173.6847 | 173.6847 | 1571.9 | 288510.8795 | 62526.5073 | 28362.7184 | 2284879.2299 | 72781.281
4243 | 1461.4783 | 0 | 0 | 0 | 0 | 1658.95 | 0 | 0 | 0 | 4966103.1037 | 0
4244 | 1213.608 | 0 | 0 | 0 | 0 | 1646.55 | 0 | 0 | 0 | 4123840.0214 | 0
4245 | 1603.4336 | 0 | 0 | 0 | 0 | 1551.25 | 0 | 0 | 0 | 5448467.4204 | 0
4246 | 1394.5459 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1555.15 | 509686.27 | 111351.8261 | 50510.4255 | 3687629.5632 | 136068.0489
4247 | 1470.3045 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1446.65 | 919673.0283 | 215514.4963 | 97759.7701 | 2961877.2831 | 327583.2
4248 | 1418.0826 | 0 | 0 | 0 | 0 | 1261.95 | 0 | 0 | 0 | 2599345.3545 | 0
4249 | 1318.7874 | 0 | 0 | 0 | 0 | 1236.7 | 0 | 0 | 0 | 1569356.9727 | 0
4250 | 1217.2856 | 0 | 0 | 0 | 0 | 1127.1 | 0 | 0 | 0 | 1448569.8771 | 0
4251 | 1218.7567 | 0 | 0 | 0 | 0 | 1038.65 | 0 | 0 | 0 | 1450320.4147 | 0
4252 | 1394.5459 | 0 | 0 | 0 | 0 | 1030.9 | 0 | 0 | 0 | 1659509.6591 | 0
4253 | 1187.1293 | 0 | 0 | 0 | 0 | 1024.4 | 0 | 0 | 0 | 1412683.8551 | 0
4254 | 1418.0826 | 0 | 0 | 0 | 0 | 1021.35 | 0 | 0 | 0 | 1687518.2607 | 0
4255 | 920.1355 | 423.1997 | 423.1997 | 411.9682 | 411.9682 | 1024.7 | 446798.5616 | 148308.5577 | 67274.4096 | 931470.6833 | 393293.6262
4256 | 761.6585 | 791.215 | 791.215 | 770.2166 | 761.6585 | 345.2 | 278776.0779 | 274197.0775 | 124378.841 | 0 | 1260392.5662
4257 | 976.5554 | 1951.6004 | 1014.451 | 1899.806 | 976.5554 | 1043.75 | 1079433.0488 | 351559.9544 | 159471.5015 | 0 | 933831.1289
4258 | 1245.0055 | 3131.0905 | 1293.3181 | 3047.993 | 1245.0055 | 1132.45 | 1496475.546 | 448201.9876 | 203309.4016 | 0 | 1080104.5397
4259 | 1420.1043 | 3619.2082 | 1475.2108 | 3523.1564 | 1420.1043 | 926.1 | 1399959.3903 | 511237.5599 | 231903.0376 | 0 | 1525050.0432
4260 | 1490.1332 | 3872.5228 | 1547.9572 | 3769.7482 | 1490.1332 | 420.5 | 666033.1415 | 536447.9495 | 243338.7504 | 0 | 2353665.3783
4261 | 860.9694 | 3855.9165 | 894.3797 | 3753.5826 | 860.9694 | 422.45 | 385732.1678 | 309948.9765 | 140596.2996 | 0 | 1358222.2443
4262 | 1268.3941 | 3555.5264 | 1317.6137 | 3461.1646 | 1268.3941 | 451.55 | 611182.7903 | 456621.8897 | 207128.7627 | 0 | 1964044.903
4263 | 1179.3631 | 3017.7964 | 1225.1289 | 2937.7057 | 1179.3631 | 463.6 | 582137.1187 | 424570.7225 | 192589.9972 | 0 | 1811973.4945
4264 | 1177.8001 | 2235.273 | 1223.5042 | 2175.9501 | 1177.8001 | 812.5 | 1017049.3019 | 424008.0497 | 192334.7625 | 0 | 1398637.6639
4265 | 933.8677 | 1204.1492 | 970.1055 | 1172.1918 | 933.8677 | 1602.6 | 1585524.2414 | 336192.3671 | 152500.5932 | 0 | 371119.0186
4266 | 1077.5727 | 101.1474 | 101.1474 | 98.463 | 98.463 | 1540.4 | 160936.8049 | 35446.674 | 16079.0052 | 1794708.0485 | 44296.248
4267 | 1109.8997 | 0 | 0 | 0 | 0 | 1571.35 | 0 | 0 | 0 | 3771439.1466 | 0
4268 | 1127.5522 | 0 | 0 | 0 | 0 | 1678.8 | 0 | 0 | 0 | 3831422.2737 | 0
4269 | 1183.4517 | 0 | 0 | 0 | 0 | 1743 | 0 | 0 | 0 | 4021368.8426 | 0
4270 | 1332.0267 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1753.65 | 576079.8503 | 111351.8261 | 50510.4255 | 3475189.3216 | 75352.0599
4271 | 1148.1467 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1556 | 990091.1932 | 215514.4963 | 97759.7701 | 1867185.2045 | 262848
4272 | 1170.2123 | 0 | 0 | 0 | 0 | 1431 | 0 | 0 | 0 | 2144999.2009 | 0
4273 | 1298.1928 | 0 | 0 | 0 | 0 | 711.9 | 0 | 0 | 0 | 1544849.4451 | 0
4274 | 1256.2682 | 0 | 0 | 0 | 0 | 338.2 | 0 | 0 | 0 | 1494959.1235 | 0
4275 | 1237.1447 | 0 | 0 | 0 | 0 | 327.25 | 0 | 0 | 0 | 1472202.1347 | 0
4276 | 1329.0847 | 0 | 0 | 0 | 0 | 319.4 | 0 | 0 | 0 | 1581610.7359 | 0
4277 | 1320.2584 | 0 | 0 | 0 | 0 | 313.5 | 0 | 0 | 0 | 1571107.5103 | 0
4278 | 1256.2682 | 0 | 0 | 0 | 0 | 310.55 | 0 | 0 | 0 | 1494959.1235 | 0
4279 | 957.647 | 375.5622 | 375.5622 | 365.595 | 365.595 | 313.5 | 121166.1621 | 131614.1932 | 59701.6604 | 1085231.4393 | 603534.263
4280 | 1212.8063 | 1259.8686 | 1259.8686 | 1226.4324 | 1212.8063 | 344.9 | 442506.5153 | 436610.2658 | 198051.2678 | 0 | 2007315.6972
4281 | 817.3512 | 1782.1911 | 849.0691 | 1734.8927 | 817.3512 | 739.25 | 640026.3063 | 294246.4335 | 133473.4516 | 0 | 1030475.5306
4282 | 1350.9121 | 2842.8097 | 1403.3338 | 2767.3631 | 1350.9121 | 670.75 | 963654.3704 | 486328.3657 | 220603.9503 | 0 | 1795699.9448
4283 | 1576.5504 | 3669.9621 | 1637.7276 | 3572.5633 | 1576.5504 | 427.1 | 717789.5371 | 567558.1289 | 257450.6735 | 0 | 2479756.0581
4284 | 1514.752 | 3906.392 | 1573.5316 | 3802.7185 | 1514.752 | 420.5 | 678214.0296 | 545310.7081 | 247358.9962 | 0 | 2392550.7319
4285 | 1347.5913 | 3300.3606 | 1399.8839 | 3212.7708 | 1347.5913 | 422.45 | 604053.3603 | 485132.8514 | 220061.6518 | 0 | 2125892.5827
4286 | 1384.7626 | 3295.6299 | 1438.4984 | 3208.1657 | 1384.7626 | 451.55 | 667008.3283 | 498514.5349 | 226131.7321 | 0 | 2144235.6433
4287 | 1490.5497 | 2623.2905 | 1548.3894 | 2553.6698 | 1490.5497 | 463.6 | 733483.9162 | 536597.8852 | 243406.7629 | 0 | 2290080.5299
4288 | 1528.8197 | 1436.4519 | 1436.4519 | 1398.3293 | 1398.3293 | 812.9 | 1204830.4873 | 503398.5419 | 228347.1719 | 239188.9452 | 1624841.9379
4289 | 1453.0225 | 183.588 | 183.588 | 178.7156 | 178.7156 | 1592.6 | 301091.3694 | 64337.6299 | 29184.2638 | 2335804.5336 | 71268.9264
4290 | 1062.5736 | 0 | 0 | 0 | 0 | 1381.9 | 0 | 0 | 0 | 1947697.3611 | 0
4291 | 1421.0247 | 0 | 0 | 0 | 0 | 1428.5 | 0 | 0 | 0 | 4828641.7675 | 0
4292 | 1195.22 | 0 | 0 | 0 | 0 | 1537.7 | 0 | 0 | 0 | 4061357.594 | 0
4293 | 1395.2815 | 0 | 0 | 0 | 0 | 1551.25 | 0 | 0 | 0 | 4741166.3739 | 0
4294 | 1417.3471 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1372.8 | 449347.6753 | 111351.8261 | 50510.4255 | 3765107.769 | 191844.1728
4295 | 1162.8571 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1109.55 | 705640.1803 | 215514.4963 | 97759.7701 | 1917171.1437 | 527146.4
4296 | 1393.0749 | 0 | 0 | 0 | 0 | 657.5 | 0 | 0 | 0 | 2553506.277 | 0
4297 | 1050.3226 | 0 | 0 | 0 | 0 | 712.2 | 0 | 0 | 0 | 1925241.269 | 0
4298 | 1021.6373 | 0 | 0 | 0 | 0 | 338.1 | 0 | 0 | 0 | 1872661.1507 | 0
4299 | 1457.0651 | 0 | 0 | 0 | 0 | 327.25 | 0 | 0 | 0 | 2670800.3888 | 0
4300 | 1272.4496 | 0 | 0 | 0 | 0 | 319.7 | 0 | 0 | 0 | 2332400.137 | 0
4301 | 1186.3938 | 0 | 0 | 0 | 0 | 313.5 | 0 | 0 | 0 | 2174659.7804 | 0
4302 | 1309.2256 | 0 | 0 | 0 | 0 | 310.45 | 0 | 0 | 0 | 2399810.545 | 0
4303 | 1074.5947 | 134.4722 | 134.4722 | 130.9034 | 130.9034 | 313.5 | 43420.5338 | 47125.2298 | 21376.5278 | 1729786.1767 | 216099.6775
4304 | 998.1356 | 1036.8674 | 1036.8674 | 1009.3495 | 998.1356 | 344.9 | 363429.7587 | 359328.8109 | 162995.5412 | 0 | 1652014.2082
4305 | 975.2784 | 1821.7903 | 1013.1234 | 1773.441 | 975.2784 | 399.75 | 411655.042 | 351100.2176 | 159262.9598 | 0 | 1560689.2313
4306 | 1046.5245 | 3148.1466 | 1087.1351 | 3064.5965 | 1046.5245 | 670.85 | 744467.2581 | 376748.8301 | 170897.4554 | 0 | 1390988.0764
4307 | 950.4987 | 3680.6899 | 987.3818 | 3583.0064 | 950.4987 | 782.55 | 789572.3756 | 342179.5368 | 155216.4399 | 0 | 1157184.6585
4308 | 1002.5404 | 3922.0167 | 1041.4433 | 3817.9285 | 1002.5404 | 420.6 | 446802.6448 | 360914.5552 | 163714.8524 | 0 | 1583412.3567
4309 | 1043.7397 | 3911.9746 | 1084.241 | 3808.1529 | 1043.7397 | 422.45 | 466301.5931 | 375746.2794 | 170442.6873 | 0 | 1646551.5085
4310 | 1077.3961 | 3639.7236 | 1119.2041 | 3543.1273 | 1077.3961 | 451.55 | 517434.9242 | 387862.6108 | 175938.7898 | 0 | 1668294.0545
4311 | 1015.4608 | 3099.1368 | 1054.8657 | 3016.8874 | 1015.4608 | 463.6 | 502157.465 | 365565.8736 | 165824.7421 | 0 | 1560153.9117
4312 | 206.3667 | 2318.5478 | 214.374 | 2257.0148 | 206.3667 | 457.05 | 100345.7815 | 74292.0073 | 33699.68 | 0 | 318413.4797
4313 | 168.6547 | 1068.902 | 175.1996 | 1040.534 | 168.6547 | 1145.95 | 204271.1268 | 60715.7055 | 27541.3186 | 0 | 144039.5786
4314 | 147.1628 | 152.8736 | 152.8736 | 148.8164 | 147.1628 | 877.4 | 136822.1154 | 52978.6234 | 24031.6922 | 0 | 165205.0074
4315 | 189.7642 | 197.1277 | 197.1277 | 191.8961 | 189.7642 | 1092.2 | 219687.875 | 68315.0982 | 30988.4876 | 0 | 172267.7592
4316 | 137.5422 | 142.8793 | 142.8793 | 139.0873 | 137.5422 | 1437.6 | 209046.5005 | 49515.2068 | 22460.648 | 0 | 77353.6208
4317 | 106.6504 | 110.7885 | 110.7885 | 107.8483 | 106.6504 | 1562.5 | 176161.8809 | 38394.1443 | 17416.0105 | 0 | 46659.375
4318 | 100.7662 | 104.6762 | 104.6762 | 101.8982 | 100.7662 | 1742.1 | 185558.3297 | 36275.8467 | 16455.1271 | 0 | 25987.5514
4319 | 91.2045 | 94.7431 | 94.7431 | 92.2287 | 91.2045 | 1589 | 153737.3008 | 32833.6131 | 14893.6917 | 0 | 37484.844
4320 | 100.0307 | 103.9127 | 103.9127 | 101.1549 | 100.0307 | 1430.5 | 151642.7754 | 36011.0595 | 16335.0167 | 0 | 56967.4956
4321 | 92.6755 | 0 | 0 | 0 | 0 | 1621.15 | 0 | 0 | 0 | 110283.8698 | 0
4322 | 100.7662 | 0 | 0 | 0 | 0 | 1499.65 | 0 | 0 | 0 | 119911.8267 | 0
4323 | 91.94 | 0 | 0 | 0 | 0 | 1489.6 | 0 | 0 | 0 | 109408.601 | 0
4324 | 95.6176 | 0 | 0 | 0 | 0 | 1590.1 | 0 | 0 | 0 | 113784.945 | 0
4325 | 86.0558 | 0 | 0 | 0 | 0 | 1729.65 | 0 | 0 | 0 | 102406.4505 | 0
4326 | 93.411 | 25.7135 | 25.7135 | 25.0311 | 25.0311 | 1719.2 | 45489.6517 | 9011.1999 | 4087.5804 | 81372.1168 | 6950.6424
4327 | 86.0558 | 89.3954 | 89.3954 | 87.0229 | 86.0558 | 1505.65 | 136981.3906 | 30980.1027 | 14052.9188 | 0 | 42541.7049
4328 | 91.951 | 792.9737 | 95.5191 | 771.9286 | 91.951 | 1192.25 | 116186.5205 | 33102.3721 | 15015.6038 | 0 | 74273.4474
4329 | 200.9569 | 2290.4232 | 208.7551 | 2229.6366 | 200.9569 | 1431.4 | 304268.4505 | 72344.4975 | 32816.2679 | 0 | 114264.1146
4330 | 878.5446 | 3183.0276 | 912.6367 | 3098.5518 | 878.5446 | 1367.35 | 1268391.8394 | 316276.0668 | 143466.3381 | 0 | 555811.2601
4331 | 1068.5028 | 3686.8406 | 1109.966 | 3588.9939 | 1068.5028 | 1294.8 | 1466866.5654 | 384661.0026 | 174486.5048 | 0 | 753508.164
4332 | 1462.838 | 3926.2519 | 1519.6041 | 3822.0513 | 1462.838 | 1066.55 | 1652886.8574 | 526621.6962 | 238881.4527 | 0 | 1365486.1731
4333 | 1268.6028 | 3911.8572 | 1317.8308 | 3808.0386 | 1268.6028 | 412.3 | 552351.8685 | 456697.0228 | 207162.8439 | 0 | 2014160.7307
4334 | 1480.9778 | 3591.6726 | 1538.447 | 3496.3516 | 1480.9778 | 799.75 | 1256277.687 | 533152.0109 | 241843.676 | 0 | 1777543.6141
4335 | 1662.323 | 2371.1529 | 1726.829 | 2308.2238 | 1662.323 | 1304.4 | 2299237.511 | 598436.2883 | 271457.3497 | 0 | 1156311.8948
4336 | 1889.88 | 1886.5307 | 1886.5307 | 1836.4632 | 1836.4632 | 1295.05 | 2521266.6349 | 661126.7577 | 299894.4431 | 97913.0425 | 1267229.3992
4337 | 1479.2732 | 41.2852 | 41.2852 | 40.1895 | 40.1895 | 1588.7 | 67529.632 | 14468.2308 | 6562.9502 | 2637840.4405 | 16180.542
4338 | 1404.2291 | 105.2808 | 105.2808 | 102.4867 | 102.4867 | 1338.45 | 145434.0739 | 36895.2081 | 16736.0763 | 2386093.7532 | 66366.0345
4339 | 1635.7965 | 0 | 0 | 0 | 0 | 1512.5 | 0 | 0 | 0 | 5558436.4866 | 0
4340 | 1688.7539 | 0 | 0 | 0 | 0 | 1707.5 | 0 | 0 | 0 | 5738385.8711 | 0
4341 | 1451.9165 | 0 | 0 | 0 | 0 | 1789.25 | 0 | 0 | 0 | 4933612.2432 | 0
4342 | 1428.3799 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1825.6 | 594860.3575 | 111351.8261 | 50510.4255 | 3802597.2234 | 53344.4256
4343 | 1283.4824 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1837.3 | 1159852.8679 | 215514.4963 | 97759.7701 | 2327055.8485 | 96318.4
4344 | 1275.3917 | 0 | 0 | 0 | 0 | 1727.6 | 0 | 0 | 0 | 2337792.9696 | 0
4345 | 1141.0098 | 0 | 0 | 0 | 0 | 1540 | 0 | 0 | 0 | 1357801.6775 | 0
4346 | 1317.8249 | 0 | 0 | 0 | 0 | 1522.15 | 0 | 0 | 0 | 1568211.6227 | 0
4347 | 1357.1939 | 0 | 0 | 0 | 0 | 1409.95 | 0 | 0 | 0 | 1615060.7112 | 0
4348 | 1237.7056 | 0 | 0 | 0 | 0 | 1306.8 | 0 | 0 | 0 | 1472869.6152 | 0
4349 | 1136.175 | 0 | 0 | 0 | 0 | 1378.1 | 0 | 0 | 0 | 1352048.2797 | 0
4350 | 1195.5738 | 0 | 0 | 0 | 0 | 1563.9 | 0 | 0 | 0 | 1422732.8708 | 0
4351 | 1022.9029 | 344.4136 | 344.4136 | 335.2731 | 335.2731 | 1458.05 | 517361.5667 | 120698.3112 | 54750.095 | 1260425.3839 | 177857.693
4352 | 1129.8233 | 1010.6137 | 1010.6137 | 983.7925 | 983.7925 | 499.4 | 519193.732 | 354165.3106 | 160653.32 | 267674.4448 | 1445050.7892
4353 | 1224.9167 | 1272.4486 | 1272.4486 | 1238.6785 | 1224.9167 | 318.8 | 411474.1486 | 440970.0062 | 200028.8945 | 0 | 2059329.9291
4354 | 1366.0648 | 1814.5166 | 1419.0748 | 1766.3603 | 1366.0648 | 332.85 | 479799.3086 | 491783.3449 | 223078.3895 | 0 | 2277435.0097
4355 | 1337.9229 | 3738.2355 | 1389.8408 | 3639.0248 | 1337.9229 | 345.9 | 490232.0777 | 481652.2552 | 218482.8146 | 0 | 2213058.3202
4356 | 1315.4265 | 3981.0862 | 1366.4718 | 3875.4304 | 1315.4265 | 348.15 | 486274.7931 | 473553.5375 | 214809.1463 | 0 | 2172887.2525
4357 | 1307.2764 | 3186.3684 | 1358.0045 | 3101.8039 | 1307.2764 | 355.15 | 494243.3001 | 470619.5123 | 213478.2399 | 0 | 2150273.6244
4358 | 1149.254 | 2529.5893 | 1193.8505 | 2462.4554 | 1149.254 | 371.1 | 452599.6484 | 413731.4357 | 187673.1762 | 0 | 1872019.8211
4359 | 1075.5123 | 1182.9181 | 1117.247 | 1151.5241 | 1075.5123 | 375.7 | 428650.2686 | 387184.4129 | 175631.1517 | 0 | 1746954.5607
4360 | 1067.8206 | 1374.3667 | 1109.2575 | 1337.8918 | 1067.8206 | 366.25 | 414223.7069 | 384415.4264 | 174375.1087 | 0 | 1744551.9526
4361 | 1122.6445 | 42.0726 | 42.0726 | 40.956 | 40.956 | 348.95 | 15136.5112 | 14744.1767 | 6688.1224 | 1982734.9867 | 66188.9435
4362 | 1180.3883 | 176.4026 | 176.4026 | 171.7209 | 171.7209 | 334.45 | 60826.3973 | 61819.5324 | 28042.0268 | 1848887.287 | 279960.6339
4363 | 1047.7675 | 0 | 0 | 0 | 0 | 1412.95 | 0 | 0 | 0 | 3560313.914 | 0
4364 | 988.3687 | 0 | 0 | 0 | 0 | 1513.55 | 0 | 0 | 0 | 3358476.7386 | 0
4365 | 1236.3242 | 0 | 0 | 0 | 0 | 1523.1 | 0 | 0 | 0 | 4201029.6044 | 0
4366 | 1285.3627 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1765.15 | 577862.7249 | 111351.8261 | 50510.4255 | 3316625.1074 | 71834.5089
4367 | 1237.0149 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1778.1 | 1125981.9537 | 215514.4963 | 97759.7701 | 2169159.1646 | 131364.8
4368 | 955.9065 | 0 | 0 | 0 | 0 | 1703 | 0 | 0 | 0 | 1752176.6618 | 0
4369 | 1144.4632 | 0 | 0 | 0 | 0 | 1728.9 | 0 | 0 | 0 | 1361911.2461 | 0
4370 | 1100.2595 | 0 | 0 | 0 | 0 | 1548.85 | 0 | 0 | 0 | 1309308.7598 | 0
4371 | 1259.8074 | 0 | 0 | 0 | 0 | 1458.85 | 0 | 0 | 0 | 1499170.8584 | 0
4372 | 1195.5738 | 0 | 0 | 0 | 0 | 1411.55 | 0 | 0 | 0 | 1422732.8708 | 0
4373 | 1084.3737 | 0 | 0 | 0 | 0 | 1406.85 | 0 | 0 | 0 | 1290404.7411 | 0
4374 | 1230.7987 | 0 | 0 | 0 | 0 | 1194.45 | 0 | 0 | 0 | 1464650.4768 | 0
4375 | 855.7574 | 224.2998 | 224.2998 | 218.347 | 218.347 | 1306.6 | 299623.551 | 78604.908 | 35656.0597 | 1168373.2498 | 148199.6886
4376 | 848.1616 | 881.0737 | 881.0737 | 857.6905 | 848.1616 | 1336.3 | 1189649.8635 | 305338.1628 | 138504.7833 | 0 | 559885.3734
4377 | 955.36 | 992.4325 | 992.4325 | 966.0939 | 955.36 | 1531.65 | 1540871.8503 | 343929.608 | 156010.2916 | 0 | 447442.856
4378 | 1003.5499 | 1042.4925 | 1042.4925 | 1014.8253 | 1003.5499 | 1590 | 1682953.1906 | 361277.9647 | 163879.699 | 0 | 411455.4598
4379 | 826.6632 | 1806.8523 | 858.7414 | 1758.8994 | 826.6632 | 1593.35 | 1399647.8698 | 297598.7388 | 134994.0946 | 0 | 336162.5754
4380 | 1123.7505 | 2861.0708 | 1167.3568 | 2785.1396 | 1123.7505 | 1549.4 | 1855164.1667 | 404550.1746 | 183508.4542 | 0 | 506361.9685
4381 | 1103.3684 | 3354.3088 | 1146.185 | 3265.2873 | 1103.3684 | 1203.8 | 1409973.0377 | 397212.6251 | 180180.0602 | 0 | 878501.9225
4382 | 1414.2487 | 2936.5317 | 1469.1286 | 2858.5977 | 1414.2487 | 1340.65 | 2007118.4895 | 509129.5259 | 230946.8099 | 0 | 932484.8691
4383 | 1156.956 | 2108.3768 | 1201.8514 | 2052.4216 | 1156.956 | 1674.15 | 2049880.6864 | 416504.1517 | 188930.911 | 0 | 376994.1051
4384 | 1089.7222 | 1884.3066 | 1132.0084 | 1834.2982 | 1089.7222 | 1866.75 | 2144500.3657 | 392299.9978 | 177951.6379 | 0 | 145205.4853
4385 | 1137.5314 | 180.0456 | 180.0456 | 175.2673 | 175.2673 | 1905.4 | 352020.7992 | 63096.2373 | 28621.1543 | 1763829.9672 | 16229.576
4386 | 926.8434 | 0 | 0 | 0 | 0 | 1865.05 | 0 | 0 | 0 | 1698903.9713 | 0
4387 | 835.7275 | 0 | 0 | 0 | 0 | 1851.7 | 0 | 0 | 0 | 2839802.134 | 0
4388 | 1471.8474 | 0 | 0 | 0 | 0 | 1868.7 | 0 | 0 | 0 | 5001337.4788 | 0
4389 | 1105.0942 | 0 | 0 | 0 | 0 | 1871.3 | 0 | 0 | 0 | 3755110.2581 | 0
4390 | 823.2952 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1887.2 | 612766.6386 | 111351.8261 | 50510.4255 | 1746519.6299 | 34502.5872
4391 | 927.5885 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1882 | 1184867.3646 | 215514.4963 | 97759.7701 | 1117728.2903 | 69856
4392 | 973.8643 | 0 | 0 | 0 | 0 | 1862.45 | 0 | 0 | 0 | 1785093.2755 | 0
4393 | 1145.1539 | 0 | 0 | 0 | 0 | 1641.4 | 0 | 0 | 0 | 1362733.16 | 0
4394 | 1047.7675 | 0 | 0 | 0 | 0 | 1813.95 | 0 | 0 | 0 | 1246843.3072 | 0
4395 | 804.6468 | 0 | 0 | 0 | 0 | 1804.45 | 0 | 0 | 0 | 957529.633 | 0
4396 | 1138.2471 | 0 | 0 | 0 | 0 | 1797.55 | 0 | 0 | 0 | 1354514.0216 | 0
4397 | 993.2035 | 0 | 0 | 0 | 0 | 1792.85 | 0 | 0 | 0 | 1181912.1135 | 0
4398 | 968.3388 | 0 | 0 | 0 | 0 | 1791.35 | 0 | 0 | 0 | 1152323.215 | 0
4399 | 1081.611 | 354.3083 | 354.3083 | 344.9051 | 344.9051 | 1781.35 | 649305.334 | 124165.8375 | 56323.0035 | 1350381.9017 | 73818.2079
4400 | 1051.0551 | 1091.842 | 1091.842 | 1062.8651 | 1051.0551 | 1610.75 | 1785518.3735 | 378379.8508 | 171637.3045 | 0 | 409123.2136
4401 | 1124.1761 | 1167.7994 | 1167.7994 | 1136.8066 | 1124.1761 | 1678.25 | 1985968.9405 | 404703.4028 | 183577.9602 | 0 | 361703.628
4402 | 1099.9253 | 1814.8179 | 1142.6073 | 1766.6536 | 1099.9253 | 1676.3 | 1944736.359 | 395973.1238 | 179617.8087 | 0 | 356045.8339
4403 | 1173.32 | 2678.7575 | 1218.8504 | 2607.6647 | 1173.32 | 1636.35 | 2034138.2416 | 422395.2022 | 191603.157 | 0 | 426677.8202
4404 | 1174.9733 | 3442.1429 | 1220.5675 | 3350.7903 | 1174.9733 | 1431.9 | 1779587.9698 | 422990.3988 | 191873.1448 | 0 | 667502.3488
4405 | 1130.4682 | 2018.1109 | 1174.3355 | 1964.5514 | 1130.4682 | 1104.5 | 1315698.5868 | 406968.5696 | 184605.4651 | 0 | 1012334.317
4406 | 1162.7327 | 3645.277 | 1207.8515 | 3548.5333 | 1162.7327 | 1644.9 | 2016819.8808 | 418583.7666 | 189874.2475 | 0 | 412886.3764
4407 | 1439.1789 | 1838.4143 | 1495.026 | 1789.6238 | 1439.1789 | 1742.85 | 2638637.2922 | 518104.4105 | 235017.9173 | 0 | 370084.8588
4408 | 1406.8437 | 1034.3878 | 1034.3878 | 1006.9357 | 1006.9357 | 1903.45 | 2019094.3291 | 362496.8389 | 164432.5939 | 733031.4088 | 95163.1558
4409 | 1304.5051 | 447.6428 | 447.6428 | 435.7626 | 435.7626 | 1915.4 | 881285.1319 | 156874.5308 | 71160.0302 | 1592404.9428 | 36085.6224
4410 | 1480.7011 | 0 | 0 | 0 | 0 | 1875.05 | 0 | 0 | 0 | 2714125.131 | 0
4411 | 1355.1218 | 0 | 0 | 0 | 0 | 1861.7 | 0 | 0 | 0 | 4604703.9546 | 0
4412 | 982.8432 | 0 | 0 | 0 | 0 | 1868.7 | 0 | 0 | 0 | 3339701.1871 | 0
4413 | 1227.3453 | 0 | 0 | 0 | 0 | 1861.3 | 0 | 0 | 0 | 4170519.3328 | 0
4414 | 1230.108 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1877.2 | 611596.2118 | 111351.8261 | 50510.4255 | 3128869.5926 | 37561.3272
4415 | 1073.3228 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1848.6 | 1168537.4714 | 215514.4963 | 97759.7701 | 1612933.4564 | 89628.8
4416 | 1058.8184 | 0 | 0 | 0 | 0 | 1644.35 | 0 | 0 | 0 | 1940814.1785 | 0
4417 | 752.1548 | 0 | 0 | 0 | 0 | 1337.2 | 0 | 0 | 0 | 895064.1806 | 0
4418 | 1158.2769 | 0 | 0 | 0 | 0 | 1594.05 | 0 | 0 | 0 | 1378349.5229 | 0
4419 | 1156.8955 | 0 | 0 | 0 | 0 | 1580.45 | 0 | 0 | 0 | 1376705.695 | 0
4420 | 1170.7092 | 0 | 0 | 0 | 0 | 1573.55 | 0 | 0 | 0 | 1393143.973 | 0
4421 | 1391.7281 | 0 | 0 | 0 | 0 | 1664.15 | 0 | 0 | 0 | 1656156.4033 | 0
4422 | 1459.4151 | 0 | 0 | 0 | 0 | 1766.15 | 0 | 0 | 0 | 1736703.9607 | 0
4423 | 1333.7106 | 313.9798 | 313.9798 | 305.6469 | 305.6469 | 1716.35 | 550131.6777 | 110032.8919 | 49912.1424 | 1884440.7622 | 84862.9743
4424 | 1049.1048 | 1034.849 | 1034.849 | 1007.3847 | 1007.3847 | 1639.75 | 1732304.9536 | 362658.4747 | 164505.9137 | 76473.0715 | 355233.879
4425 | 1288.2412 | 1842.1582 | 1338.2309 | 1793.2683 | 1288.2412 | 1838.75 | 2489074.9245 | 463766.8226 | 210369.7837 | 0 | 207728.8893
4426 | 1625.402 | 1688.4753 | 1688.4753 | 1643.6641 | 1625.402 | 1814.5 | 3098068.7054 | 585144.7114 | 265428.1427 | 0 | 301512.0665
4427 | 1252.525 | 1301.1289 | 1301.1289 | 1266.5977 | 1252.525 | 1636.35 | 2165050.3562 | 450909.0166 | 204537.34 | 0 | 455480.7163
4428 | 1499.6906 | 1967.3227 | 1557.8861 | 1915.111 | 1499.6906 | 1304.5 | 2063363.2006 | 539888.6153 | 244899.4747 | 0 | 1043034.8109
4429 | 1174.5986 | 1711.5472 | 1220.179 | 1666.1236 | 1174.5986 | 1104.25 | 1361350.6708 | 422855.5082 | 191811.9569 | 0 | 1052146.7264
4430 | 1162.5522 | 3187.9474 | 1207.6645 | 3103.341 | 1162.5522 | 1402.45 | 1716886.6565 | 418518.8078 | 189844.7814 | 0 | 694683.0934
4431 | 1383.5979 | 2849.0404 | 1437.2882 | 2773.4285 | 1383.5979 | 1559.75 | 2275130.3969 | 498095.2289 | 225941.5302 | 0 | 609128.957
4432 | 1184.4607 | 100.7807 | 100.7807 | 98.106 | 98.106 | 1680.95 | 174261.2552 | 35318.1662 | 16020.7126 | 1991288.2015 | 30638.6905
4433 | 1396.2434 | 821.8504 | 821.8504 | 800.0389 | 800.0389 | 1901.9 | 1606352.0563 | 288014.0096 | 130646.3549 | 1092842.8491 | 76823.6796
4434 | 1222.7384 | 93.2223 | 93.2223 | 90.7483 | 90.7483 | 1617.55 | 155009.8544 | 32669.3765 | 14819.1922 | 2074937.9833 | 33972.6511
4435 | 1330.2572 | 0 | 0 | 0 | 0 | 1715 | 0 | 0 | 0 | 4520213.9758 | 0
4436 | 1078.8483 | 0 | 0 | 0 | 0 | 1787 | 0 | 0 | 0 | 3665926.3909 | 0
4437 | 1160.349 | 0 | 0 | 0 | 0 | 1525.7 | 0 | 0 | 0 | 3942865.7729 | 0
4438 | 1320.5876 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1219.7 | 398301.1007 | 111351.8261 | 50510.4255 | 3436319.2462 | 238673.4822
4439 | 1039.4793 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1246.25 | 788408.5508 | 215514.4963 | 97759.7701 | 1497933.2026 | 446220
4440 | 1082.9924 | 0 | 0 | 0 | 0 | 1231.1 | 0 | 0 | 0 | 1985125.0032 | 0
4441 | 1015.996 | 0 | 0 | 0 | 0 | 703.55 | 0 | 0 | 0 | 1209035.2709 | 0
4442 | 1259.1168 | 0 | 0 | 0 | 0 | 1040.6 | 0 | 0 | 0 | 1498348.9456 | 0
4443 | 955.2158 | 0 | 0 | 0 | 0 | 1194.55 | 0 | 0 | 0 | 1136706.8519 | 0
4444 | 1254.9727 | 0 | 0 | 0 | 0 | 1232.7 | 0 | 0 | 0 | 1493417.4618 | 0
4445 | 1275.6932 | 0 | 0 | 0 | 0 | 1228.4 | 0 | 0 | 0 | 1518074.8771 | 0
4446 | 932.4233 | 0 | 0 | 0 | 0 | 1301.45 | 0 | 0 | 0 | 1109583.6949 | 0
4447 | 1058.1277 | 390.6903 | 390.6903 | 380.3216 | 380.3216 | 1233.2 | 495704.5925 | 136915.777 | 62106.5177 | 1242418.6569 | 285462.0036
4448 | 793.1348 | 823.9114 | 823.9114 | 802.0452 | 793.1348 | 1141.9 | 958688.11 | 285528.5195 | 129518.909 | 0 | 680588.9516
4449 | 1186.5863 | 2003.0763 | 1232.6312 | 1949.9157 | 1186.5863 | 1379.3 | 1734193.7 | 427171.0741 | 193769.5456 | 0 | 736514.127
4450 | 1347.1392 | 3234.2479 | 1399.4144 | 3148.4128 | 1347.1392 | 1281.25 | 1825917.1024 | 484970.1278 | 219987.8385 | 0 | 968256.3316
4451 | 1551.5661 | 3748.0387 | 1611.7741 | 3648.5678 | 1551.5661 | 1123.95 | 1843246.262 | 558563.8104 | 253370.7507 | 0 | 1359249.5169
4452 | 1023.2024 | 4008.0775 | 1062.9071 | 3901.7053 | 1023.2024 | 742.75 | 803629.6271 | 368352.8816 | 167088.9599 | 0 | 1286421.279
4453 | 1250.4936 | 2753.298 | 1299.0181 | 2680.2269 | 1250.4936 | 390.75 | 517093.5148 | 450177.6859 | 204205.6003 | 0 | 2012356.7807
4454 | 1279.245 | 3148.6961 | 1328.8858 | 3065.1315 | 1279.245 | 779.15 | 1053599.6741 | 460528.2058 | 208900.7111 | 0 | 1561766.2778
4455 | 790.3815 | 2350.5669 | 821.0526 | 2288.1841 | 790.3815 | 1149.25 | 960504.5712 | 284537.3536 | 129069.3051 | 0 | 672417.0932
4456 | 1057.9646 | 1899.3402 | 1099.0191 | 1848.9328 | 1057.9646 | 1235.75 | 1385163.4006 | 380867.2452 | 172765.6143 | 0 | 808549.4226
4457 | 1309.8432 | 565.9938 | 565.9938 | 550.9726 | 550.9726 | 1530.4 | 892119.3531 | 198350.15 | 89973.8319 | 1391009.6964 | 253263.2632
4458 | 1349.9434 | 225.1869 | 225.1869 | 219.2106 | 219.2106 | 1377.6 | 319169.444 | 78915.8022 | 35797.0847 | 2072633.331 | 133550.8576
4459 | 1201.79 | 0 | 0 | 0 | 0 | 1251.8 | 0 | 0 | 0 | 4083682.4064 | 0
4460 | 1417.2834 | 0 | 0 | 0 | 0 | 1482.7 | 0 | 0 | 0 | 4815928.9083 | 0
4461 | 1335.092 | 0 | 0 | 0 | 0 | 1261.4 | 0 | 0 | 0 | 4536642.582 | 0
4462 | 1290.1975 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1113.6 | 364779.5886 | 111351.8261 | 50510.4255 | 3333053.7136 | 271126.7136
4463 | 1175.544 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 697.5 | 442136.6838 | 215514.4963 | 97759.7701 | 1960281.1551 | 771080
4464 | 1105.7849 | 0 | 0 | 0 | 0 | 353.45 | 0 | 0 | 0 | 2026903.7822 | 0
4465 | 1215.6037 | 0 | 0 | 0 | 0 | 1038.65 | 0 | 0 | 0 | 2228201.5344 | 0
4466 | 895.1263 | 0 | 0 | 0 | 0 | 1018.7 | 0 | 0 | 0 | 1640766.5851 | 0
4467 | 966.2668 | 0 | 0 | 0 | 0 | 1133.05 | 0 | 0 | 0 | 1771167.0158 | 0
4468 | 1008.3985 | 0 | 0 | 0 | 0 | 1126.15 | 0 | 0 | 0 | 1848394.456 | 0
4469 | 1040.17 | 0 | 0 | 0 | 0 | 1121.45 | 0 | 0 | 0 | 1906631.5403 | 0
4470 | 973.1736 | 0 | 0 | 0 | 0 | 1119.95 | 0 | 0 | 0 | 1783827.2519 | 0
4471 | 1027.7377 | 293.855 | 293.855 | 286.0563 | 286.0563 | 1187.35 | 358710.6918 | 102980.2528 | 46712.9869 | 1359501.9955 | 227546.0633
4472 | 181.6015 | 350.34 | 188.648 | 341.0422 | 181.6015 | 1032.25 | 197759.7304 | 65376.547 | 29655.5281 | 0 | 175744.8704
4473 | 87.356 | 1194.1383 | 90.7458 | 1162.4465 | 87.356 | 1144.05 | 105640.5264 | 31448.1505 | 14265.2305 | 0 | 74772.3457
4474 | 0 | 1904.6454 | 0 | 1854.0971 | 0 | 993.7 | 0 | 0 | 0 | 0 | 0
4475 | 0 | 2650.7794 | 0 | 2580.4291 | 0 | 392.45 | 0 | 0 | 0 | 0 | 0
4476 | 0 | 3144.5098 | 0 | 3061.0562 | 0 | 386 | 0 | 0 | 0 | 0 | 0
4477 | 0 | 3247.4782 | 0 | 3161.2919 | 0 | 390.75 | 0 | 0 | 0 | 0 | 0
4478 | 0 | 3065.492 | 0 | 2984.1355 | 0 | 422.4 | 0 | 0 | 0 | 0 | 0
4479 | 0 | 1995.9989 | 0 | 1943.0262 | 0 | 435.75 | 0 | 0 | 0 | 0 | 0
4480 | 0 | 1767.8192 | 0 | 1720.9023 | 0 | 1032.75 | 0 | 0 | 0 | 0 | 0
4481 | 0 | 1267.0925 | 0 | 1233.4645 | 0 | 1492.9 | 0 | 0 | 0 | 0 | 0
4482 | 0 | 345.2592 | 0 | 336.0962 | 0 | 1141.6 | 0 | 0 | 0 | 0 | 0
4483 | 0 | 0 | 0 | 0 | 0 | 1128.25 | 0 | 0 | 0 | 0 | 0
4484 | 0 | 0 | 0 | 0 | 0 | 1483.7 | 0 | 0 | 0 | 0 | 0
4485 | 118.7976 | 123.4079 | 123.4079 | 120.1327 | 118.7976 | 1525.7 | 191914.4548 | 42767.1474 | 19399.6533 | 0 | 56345.7168
4486 | 193.3915 | 200.8955 | 200.8955 | 195.5638 | 193.3915 | 1541.6 | 315573.545 | 69620.9377 | 31580.8309 | 0 | 88650.4344
4487 | 241.0487 | 250.4028 | 250.4028 | 243.7573 | 241.0487 | 1497 | 381320.7473 | 86777.526 | 39363.25 | 0 | 121247.4876
4488 | 237.5953 | 246.8148 | 246.8148 | 240.2645 | 237.5953 | 1129 | 284005.943 | 85534.2949 | 38799.3065 | 0 | 206945.245
4489 | 234.8325 | 0 | 0 | 0 | 0 | 1462.45 | 0 | 0 | 0 | 279450.7083 | 0
4490 | 251.4089 | 0 | 0 | 0 | 0 | 1299.15 | 0 | 0 | 0 | 299176.6407 | 0
4491 | 171.9803 | 0 | 0 | 0 | 0 | 1313.7 | 0 | 0 | 0 | 204656.5482 | 0
4492 | 178.8871 | 0 | 0 | 0 | 0 | 1421.25 | 0 | 0 | 0 | 212875.6866 | 0
4493 | 246.5742 | 0 | 0 | 0 | 0 | 1412.65 | 0 | 0 | 0 | 293423.2437 | 0
4494 | 227.9257 | 111.1947 | 111.1947 | 108.2437 | 108.2437 | 1360.8 | 155517.3837 | 38967.7149 | 17676.1884 | 142421.6236 | 68420.6072
4495 | 274.8922 | 285.5591 | 285.5591 | 277.9805 | 274.8922 | 1108.4 | 321751.8055 | 98961.1901 | 44889.8954 | 0 | 245093.7072
4496 | 119.5695 | 725.0868 | 124.2088 | 705.8433 | 119.5695 | 1029.4 | 130001.4835 | 43045.0096 | 19525.6946 | 0 | 116054.1286
4497 | 639.3445 | 1514.8173 | 664.1536 | 1474.6149 | 639.3445 | 962.3 | 649236.2554 | 230164.0228 | 104404.9581 | 0 | 663447.7957
4498 | 1147.0671 | 3182.4833 | 1191.5786 | 3098.0219 | 1147.0671 | 372.95 | 450943.3254 | 412944.1596 | 187316.0591 | 0 | 1866335.5413
4499 | 1141.3284 | 3644.4429 | 1185.6169 | 3547.7213 | 1141.3284 | 382.75 | 459980.0494 | 410878.2208 | 186378.9263 | 0 | 1845813.3403
4500 | 1174.7929 | 2861.2755 | 1220.3795 | 2785.3388 | 1174.7929 | 385.35 | 477256.4137 | 422925.44 | 191843.6788 | 0 | 1896879.3382
4501 | 1161.3384 | 3873.4515 | 1206.4045 | 3770.6522 | 1161.3384 | 393.3 | 481427.3549 | 418081.8121 | 189646.5553 | 0 | 1865922.3543
4502 | 906.2351 | 2049.5088 | 941.4012 | 1995.1159 | 906.2351 | 778 | 745345.1771 | 326244.6466 | 147988.1966 | 0 | 1107419.3281
4503 | 844.8066 | 877.5895 | 877.5895 | 854.2988 | 844.8066 | 1228.9 | 1094962.3675 | 304130.3638 | 137956.9122 | 0 | 651429.9066
4504 | 961.5296 | 1465.3723 | 998.8419 | 1426.4821 | 961.5296 | 1128.55 | 1143768.0453 | 346150.6402 | 157017.7765 | 0 | 837924.9318
4505 | 1098.1261 | 37.6785 | 37.6785 | 36.6785 | 36.6785 | 1365.75 | 52846.7008 | 13204.2674 | 5989.6024 | 1945633.4352 | 22770.8435
4506 | 934.1267 | 45.7687 | 45.7687 | 44.554 | 44.554 | 1262.05 | 59504.1468 | 16039.448 | 7275.6718 | 1630586.6676 | 32182.7375
4507 | 1015.996 | 0 | 0 | 0 | 0 | 1113.5 | 0 | 0 | 0 | 3452354.4963 | 0
4508 | 813.6256 | 0 | 0 | 0 | 0 | 1518.35 | 0 | 0 | 0 | 2764699.9288 | 0
4509 | 770.8032 | 0 | 0 | 0 | 0 | 1667.95 | 0 | 0 | 0 | 2619189.4061 | 0
4510 | 861.9735 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1900 | 621629.934 | 111351.8261 | 50510.4255 | 1877948.4889 | 30587.4
4511 | 1115.4545 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1897 | 1199237.9765 | 215514.4963 | 97759.7701 | 1756097.0341 | 60976
4512 | 933.114 | 0 | 0 | 0 | 0 | 1874.35 | 0 | 0 | 0 | 1710397.883 | 0
4513 | 1098.8781 | 0 | 0 | 0 | 0 | 1809.85 | 0 | 0 | 0 | 1307664.9319 | 0
4514 | 1076.0855 | 0 | 0 | 0 | 0 | 1777.2 | 0 | 0 | 0 | 1280541.7748 | 0
4515 | 1114.0731 | 0 | 0 | 0 | 0 | 1612.4 | 0 | 0 | 0 | 1325747.0366 | 0
4516 | 739.0318 | 0 | 0 | 0 | 0 | 1510.85 | 0 | 0 | 0 | 879447.8174 | 0
4517 | 871.6431 | 0 | 0 | 0 | 0 | 1545.35 | 0 | 0 | 0 | 1037255.2763 | 0
4518 | 1126.5055 | 0 | 0 | 0 | 0 | 1580.15 | 0 | 0 | 0 | 1340541.4867 | 0
4519 | 891.6729 | 309.8993 | 309.8993 | 301.6748 | 301.6748 | 1363.4 | 434996.7997 | 108602.9241 | 49263.4931 | 1081466.5786 | 187983.5238
4520 | 1175.0536 | 1010.1524 | 1010.1524 | 983.3435 | 983.3435 | 534.65 | 555248.5782 | 354003.6747 | 160580.0002 | 351404.5788 | 1410462.385
4521 | 977.329 | 1015.254 | 1015.254 | 988.3097 | 977.329 | 302.05 | 311663.6089 | 351838.4222 | 159597.8176 | 0 | 1659455.6915
4522 | 1380.4794 | 1434.0492 | 1434.0492 | 1395.9903 | 1380.4794 | 312.45 | 454061.2957 | 496972.5912 | 225432.2893 | 0 | 2329627.3364
4523 | 1327.1344 | 2570.4382 | 1378.6341 | 2502.2202 | 1327.1344 | 324.8 | 453384.1684 | 477768.4013 | 216721.0554 | 0 | 2223215.6273
4524 | 1231.0111 | 1278.7811 | 1278.7811 | 1244.843 | 1231.0111 | 327.55 | 424305.774 | 443163.9982 | 201024.1136 | 0 | 2058804.3469
4525 | 1202.3589 | 3233.3909 | 1249.0152 | 3147.5785 | 1202.3589 | 331.8 | 420239.0155 | 432849.2209 | 196345.216 | 0 | 2005775.1954
4526 | 1118.7189 | 2727.9033 | 1162.1306 | 2655.5063 | 1118.7189 | 342.7 | 404684.7521 | 402738.7871 | 182686.7887 | 0 | 1854052.7551
4527 | 1397.5799 | 2588.6111 | 1451.8127 | 2519.9107 | 1397.5799 | 342.4 | 505319.4803 | 503128.7604 | 228224.796 | 0 | 2316628.4257
4528 | 1387.754 | 1412.7485 | 1412.7485 | 1375.2549 | 1375.2549 | 327.9 | 475805.5772 | 495091.7686 | 224579.1273 | 22910.9146 | 2250919.1523
4529 | 1404.902 | 54.8821 | 54.8821 | 53.4256 | 53.4256 | 318.5 | 18002.4 | 19233.2126 | 8724.3989 | 2477256.264 | 87934.0425
4530 | 1178.5865 | 141.7522 | 141.7522 | 137.9902 | 137.9902 | 610.15 | 89060.1823 | 49676.4554 | 22533.7921 | 1907413.0473 | 187729.8192
4531 | 1232.8708 | 0 | 0 | 0 | 0 | 1126.45 | 0 | 0 | 0 | 4189294.8833 | 0
4532 | 1013.2333 | 0 | 0 | 0 | 0 | 1447.8 | 0 | 0 | 0 | 3442966.7194 | 0
4533 | 1301.9392 | 0 | 0 | 0 | 0 | 1574 | 0 | 0 | 0 | 4423989.2759 | 0
4534 | 1252.9006 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1709.55 | 559516.6641 | 111351.8261 | 50510.4255 | 3206318.7421 | 88841.1033
4535 | 1488.4238 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1812.35 | 1147493.5399 | 215514.4963 | 97759.7701 | 3023446.7461 | 111088.8
4536 | 1379.9864 | 0 | 0 | 0 | 0 | 1780.3 | 0 | 0 | 0 | 2529515.1519 | 0
4537 | 1263.2609 | 0 | 0 | 0 | 0 | 1451.4 | 0 | 0 | 0 | 1503280.4282 | 0
4538 | 1365.4821 | 0 | 0 | 0 | 0 | 1552.95 | 0 | 0 | 0 | 1624923.6776 | 0
4539 | 1331.6386 | 0 | 0 | 0 | 0 | 1494.45 | 0 | 0 | 0 | 1584649.8995 | 0
4540 | 1141.0098 | 0 | 0 | 0 | 0 | 1412.05 | 0 | 0 | 0 | 1357801.6775 | 0
4541 | 1093.3526 | 0 | 0 | 0 | 0 | 1407.85 | 0 | 0 | 0 | 1301089.6214 | 0
4542 | 949.6904 | 0 | 0 | 0 | 0 | 1485.15 | 0 | 0 | 0 | 1130131.5411 | 0
4543 | 966.9575 | 337.8609 | 337.8609 | 328.8942 | 328.8942 | 1522.45 | 530116.2274 | 118401.9168 | 53708.425 | 1169569.9462 | 153741.0144
4544 | 843.7136 | 876.4531 | 876.4531 | 853.1925 | 843.7136 | 1521.55 | 1361201.9666 | 303736.8812 | 137778.4242 | 0 | 403674.7522
4545 | 1005.3405 | 1361.309 | 1044.352 | 1325.1806 | 1005.3405 | 1874.75 | 1994623.0917 | 361922.58 | 164172.1037 | 0 | 125918.8976
4546 | 1563.6281 | 3052.4187 | 1624.3042 | 2971.4092 | 1563.6281 | 1879.5 | 3106157.5444 | 562906.1056 | 255340.464 | 0 | 188417.1826
4547 | 1371.9495 | 3688.7448 | 1425.1871 | 3590.8475 | 1371.9495 | 1640.85 | 2382248.4456 | 493901.8103 | 224039.3489 | 0 | 492735.6532
4548 | 1263.6571 | 2856.5209 | 1312.6929 | 2780.7104 | 1263.6571 | 1451.8 | 1938905.4323 | 454916.5718 | 206355.2116 | 0 | 692736.8463
4549 | 1241.5078 | 870.7833 | 870.7833 | 847.6732 | 847.6732 | 1107.25 | 990156.0275 | 305162.3379 | 138425.0272 | 721898.8458 | 740752.1705
4550 | 1242.3884 | 391.9857 | 391.9857 | 381.5826 | 381.5826 | 1718.3 | 692397.8346 | 137369.7408 | 62312.4408 | 1577856.9996 | 105218.0487
4551 | 1546.4283 | 394.1797 | 394.1797 | 383.7183 | 383.7183 | 1802.25 | 729301.1996 | 138138.6033 | 62661.2053 | 2131247.3794 | 74275.2955
4552 | 1391.9206 | 212.928 | 212.928 | 207.277 | 207.277 | 1848.45 | 404640.96 | 74619.7101 | 33848.3296 | 2171451.7676 | 30748.2826
4553 | 1102.5551 | 128.8419 | 128.8419 | 125.4225 | 125.4225 | 1898.7 | 251577.7265 | 45152.1072 | 20481.4975 | 1791084.0614 | 12436.601
4554 | 1208.6278 | 119.2267 | 119.2267 | 116.0625 | 116.0625 | 1705.25 | 208929.4063 | 41782.5089 | 18953.0103 | 2002672.089 | 33485.6633
4555 | 1185.9043 | 0 | 0 | 0 | 0 | 1678.6 | 0 | 0 | 0 | 4029702.6959 | 0
4556 | 1010.4706 | 0 | 0 | 0 | 0 | 1863.7 | 0 | 0 | 0 | 3433578.9425 | 0
4557 | 1031.1911 | 0 | 0 | 0 | 0 | 1786.3 | 0 | 0 | 0 | 3503987.2627 | 0
4558 | 1206.6248 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1887.2 | 616665.063 | 111351.8261 | 50510.4255 | 3049073.5023 | 34502.5872
4559 | 1274.3118 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1882 | 1188765.4933 | 215514.4963 | 97759.7701 | 2295894.1327 | 69856
4560 | 1225.2732 | 0 | 0 | 0 | 0 | 1802.45 | 0 | 0 | 0 | 2245925.8654 | 0
4561 | 1292.9603 | 0 | 0 | 0 | 0 | 1283.9 | 0 | 0 | 0 | 1538622.7237 | 0
4562 | 1131.3402 | 0 | 0 | 0 | 0 | 1248.25 | 0 | 0 | 0 | 1346294.8832 | 0
4563 | 1158.2769 | 0 | 0 | 0 | 0 | 1354.35 | 0 | 0 | 0 | 1378349.5229 | 0
4564 | 1222.5105 | 0 | 0 | 0 | 0 | 1302.55 | 0 | 0 | 0 | 1454787.5105 | 0
4565 | 826.7486 | 0 | 0 | 0 | 0 | 1332.75 | 0 | 0 | 0 | 983830.8761 | 0
4566 | 1008.3985 | 0 | 0 | 0 | 0 | 1406.35 | 0 | 0 | 0 | 1199994.2186 | 0
4567 | 964.1947 | 377.8569 | 377.8569 | 367.8288 | 367.8288 | 1375.55 | 535818.5487 | 132418.3681 | 60066.4431 | 1093138.7543 | 224831.9736
4568 | 949.7888 | 986.6453 | 986.6453 | 960.4603 | 949.7888 | 1237.05 | 1242379.2947 | 341923.9655 | 155100.5099 | 0 | 724641.3597
4569 | 1299.4648 | 1349.8894 | 1349.8894 | 1314.064 | 1299.4648 | 1567.25 | 2152075.4194 | 467807.3237 | 212202.5999 | 0 | 562343.387
4570 | 1185.0608 | 1838.0528 | 1231.047 | 1789.2719 | 1185.0608 | 1483.6 | 1855647.2645 | 426621.8768 | 193520.4236 | 0 | 611965.3811
4571 | 1494.3067 | 2712.4854 | 1552.2922 | 2640.4975 | 1494.3067 | 1230.05 | 1944454.6415 | 537950.4181 | 244020.2869 | 0 | 1150541.4568
4572 | 1253.3755 | 3225.7619 | 1302.0129 | 3140.152 | 1253.3755 | 1304.3 | 1728223.086 | 451215.1624 | 204676.2111 | 0 | 871973.3013
4573 | 1225.6264 | 3142.0135 | 1273.1861 | 3058.6262 | 1225.6264 | 1309.05 | 1694300.2225 | 441225.49 | 200144.7848 | 0 | 846846.5341
4574 | 1352.7545 | 2540.4656 | 1405.2483 | 2473.043 | 1352.7545 | 1670.8 | 2387575.1269 | 486991.6214 | 220904.8105 | 0 | 445326.7827
4575 | 1293.0716 | 2581.1535 | 1343.2493 | 2512.6511 | 1293.0716 | 1597.15 | 2181136.6646 | 465505.7922 | 211158.5996 | 0 | 520913.9122
4576 | 998.7617 | 1687.288 | 1037.5187 | 1642.5083 | 998.7617 | 1525.35 | 1607693.1215 | 359554.2248 | 163097.7914 | 0 | 474062.2578
4577 | 1126.9881 | 715.9962 | 715.9962 | 696.994 | 696.994 | 1807.9 | 1331485.7296 | 250917.8489 | 113819.1242 | 788179.0777 | 131060.225
4578 | 1225.8163 | 128.4461 | 128.4461 | 125.0372 | 125.0372 | 1666.95 | 220170.5983 | 45013.4061 | 20418.5812 | 2017728.0165 | 40762.6556
4579 | 1032.5724 | 0 | 0 | 0 | 0 | 1628.6 | 0 | 0 | 0 | 3508681.1477 | 0
4580 | 1021.5215 | 0 | 0 | 0 | 0 | 1833.7 | 0 | 0 | 0 | 3471130.0468 | 0
4581 | 1216.2944 | 0 | 0 | 0 | 0 | 1791.3 | 0 | 0 | 0 | 4132968.2285 | 0
4582 | 1219.0571 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1887.2 | 615880.0774 | 111351.8261 | 50510.4255 | 3091318.4917 | 34502.5872
4583 | 1163.1117 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1882 | 1188282.8359 | 215514.4963 | 97759.7701 | 1918036.1657 | 69856
4584 | 1101.6408 | 0 | 0 | 0 | 0 | 1754.55 | 0 | 0 | 0 | 2019307.6414 | 0
4585 | 1022.2122 | 0 | 0 | 0 | 0 | 1305.2 | 0 | 0 | 0 | 1216432.4954 | 0
4586 | 1254.9727 | 0 | 0 | 0 | 0 | 1243.95 | 0 | 0 | 0 | 1493417.4618 | 0
4587 | 1133.4123 | 0 | 0 | 0 | 0 | 1123.75 | 0 | 0 | 0 | 1348760.6251 | 0
4588 | 973.1736 | 0 | 0 | 0 | 0 | 1002.05 | 0 | 0 | 0 | 1158076.612 | 0
4589 | 1258.4261 | 0 | 0 | 0 | 0 | 1114.6 | 0 | 0 | 0 | 1497527.0316 | 0
4590 | 1203.862 | 0 | 0 | 0 | 0 | 1351.15 | 0 | 0 | 0 | 1432595.8371 | 0
4591 | 1112.6918 | 208.9119 | 208.9119 | 203.3675 | 203.3675 | 1322.95 | 285481.5232 | 73212.313 | 33209.9187 | 1666791.3242 | 134777.6353
4592 | 1002.4448 | 437.0148 | 437.0148 | 425.4166 | 425.4166 | 1237.05 | 557181.4418 | 153149.9889 | 69470.5366 | 1057692.6378 | 317706.1131
4593 | 715.8188 | 743.5951 | 743.5951 | 723.8605 | 715.8188 | 1614.75 | 1220964.8815 | 257694.7524 | 116893.203 | 0 | 275768.8845
4594 | 888.077 | 1456.6899 | 922.5386 | 1418.0302 | 888.077 | 1633.7 | 1532634.71 | 319707.7378 | 145022.9822 | 0 | 325302.6232
4595 | 1386.1353 | 2299.974 | 1439.9236 | 2238.9339 | 1386.1353 | 1591.45 | 2334974.737 | 499008.6929 | 226355.8876 | 0 | 566305.5597
4596 | 1199.0566 | 2669.6389 | 1245.5861 | 2598.7881 | 1199.0566 | 1339.2 | 1700161.5318 | 431660.3814 | 195805.9452 | 0 | 792336.6112
4597 | 1228.0489 | 2041.6315 | 1275.7031 | 1987.4477 | 1228.0489 | 1166.3 | 1515902.2152 | 442097.6166 | 200540.3911 | 0 | 1023824.3971
4598 | 1402.9448 | 2461.2474 | 1457.3859 | 2395.9272 | 1402.9448 | 1573.3 | 2334268.9341 | 505060.1197 | 229100.8821 | 0 | 598636.5363
4599 | 1345.1535 | 1633.2223 | 1397.3524 | 1589.8775 | 1345.1535 | 1167 | 1657197.1854 | 484255.2701 | 219663.5711 | 0 | 1120512.8888
4600 | 1550.7356 | 113.5788 | 113.5788 | 110.5644 | 110.5644 | 1142.95 | 133116.9621 | 39803.1976 | 18055.1727 | 2639833.7277 | 92754.2363
4601 | 1497.0151 | 46.1354 | 46.1354 | 44.911 | 44.911 | 1630.3 | 77316.7769 | 16167.9558 | 7333.9644 | 2661706.7673 | 16252.3817
4602 | 1191.2752 | 16.1451 | 16.1451 | 15.7166 | 15.7166 | 1622.05 | 26912.2128 | 5657.9836 | 2566.5242 | 2154798.8695 | 5814.3828
4603 | 1230.7987 | 0 | 0 | 0 | 0 | 1600.7 | 0 | 0 | 0 | 4182254.0506 | 0
4604 | 1251.5192 | 0 | 0 | 0 | 0 | 1743.7 | 0 | 0 | 0 | 4252662.3707 | 0
4605 | 1339.2361 | 0 | 0 | 0 | 0 | 1663.2 | 0 | 0 | 0 | 4550724.2474 | 0
4606 | 1237.0149 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1879.7 | 614443.1187 | 111351.8261 | 50510.4255 | 3152339.0349 | 36796.6422
4607 | 1361.338 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1882 | 1188853.5001 | 215514.4963 | 97759.7701 | 2591609.0686 | 69856
4608 | 1507.763 | 0 | 0 | 0 | 0 | 1489.25 | 0 | 0 | 0 | 2763729.5185 | 0
4609 | 607.8018 | 0 | 0 | 0 | 0 | 1216.05 | 0 | 0 | 0 | 723284.1863 | 0
4610 | 762.515 | 0 | 0 | 0 | 0 | 1388.85 | 0 | 0 | 0 | 907392.8882 | 0
4611 | 928.2792 | 0 | 0 | 0 | 0 | 1391.85 | 0 | 0 | 0 | 1104652.2118 | 0
4612 | 756.9896 | 0 | 0 | 0 | 0 | 1450.05 | 0 | 0 | 0 | 900817.5775 | 0
4613 | 800.5026 | 0 | 0 | 0 | 0 | 1482.85 | 0 | 0 | 0 | 952598.1499 | 0
4614 | 622.3062 | 0 | 0 | 0 | 0 | 1471.35 | 0 | 0 | 0 | 740544.377 | 0
4615 | 551.1658 | 183.0031 | 183.0031 | 178.1463 | 178.1463 | 1445.05 | 272485.9518 | 64132.6727 | 29091.2929 | 683744.6404 | 96771.0711
4616 | 537.6301 | 793.7777 | 558.4926 | 772.7113 | 537.6301 | 1297.75 | 740038.8699 | 193546.8285 | 87794.9919 | 0 | 377550.723
4617 | 520.8758 | 2037.5937 | 541.0885 | 1983.5171 | 520.8758 | 1524.25 | 841576.0508 | 187515.2931 | 85059.0205 | 0 | 247806.6686
4618 | 948.3591 | 3231.3975 | 985.1598 | 3145.6379 | 948.3591 | 1421.1 | 1427390.8041 | 341409.2679 | 154867.0373 | 0 | 549005.0699
4619 | 845.2702 | 3756.0697 | 878.0705 | 3656.3857 | 845.2702 | 1230.05 | 1100901.6967 | 304297.2676 | 138032.6217 | 0 | 650815.781
4620 | 618.959 | 4018.8946 | 642.9775 | 3912.2353 | 618.959 | 1217.25 | 798156.7064 | 222825.2301 | 101076.0002 | 0 | 484490.1356
4621 | 587.2298 | 2294.62 | 610.0173 | 2233.722 | 587.2298 | 1166.3 | 724701.7555 | 211402.7342 | 95894.6291 | 0 | 489573.4985
4622 | 673.7052 | 3737.713 | 699.848 | 3638.5161 | 673.7052 | 1456.3 | 1036433.0003 | 242533.8608 | 110016.0541 | 0 | 366293.5003
4623 | 761.9789 | 2147.7641 | 791.5474 | 2090.7636 | 761.9789 | 1344.05 | 1083143.5873 | 274312.4 | 124431.1525 | 0 | 499820.0521
4624 | 727.5949 | 100.7921 | 100.7921 | 98.1171 | 98.1171 | 1329.15 | 137944.5333 | 35322.1707 | 16022.5291 | 1153832.7643 | 64429.7757
4625 | 423.3979 | 67.97 | 67.97 | 66.1661 | 66.1661 | 1755.4 | 122650.1543 | 23819.8125 | 10804.9316 | 654805.7465 | 15841.7636
4626 | 585.8407 | 20.3793 | 20.3793 | 19.8384 | 19.8384 | 1721.95 | 36009.3896 | 7141.83 | 3239.6135 | 1037482.1468 | 5399.4529
4627 | 736.9597 | 0 | 0 | 0 | 0 | 1600.7 | 0 | 0 | 0 | 2504189.1544 | 0
4628 | 609.1832 | 0 | 0 | 0 | 0 | 1744.1 | 0 | 0 | 0 | 2070004.5306 | 0
4629 | 715.5485 | 0 | 0 | 0 | 0 | 1485.8 | 0 | 0 | 0 | 2431433.893 | 0
4630 | 707.951 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1734.1 | 566489.737 | 111351.8261 | 50510.4255 | 1354579.9965 | 81331.8966
4631 | 652.0056 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1865.3 | 1179067.9995 | 215514.4963 | 97759.7701 | 181297.6692 | 79742.4
4632 | 602.2764 | 0 | 0 | 0 | 0 | 1404.95 | 0 | 0 | 0 | 1103972.5789 | 0
4633 | 1192.8111 | 0 | 0 | 0 | 0 | 1751.4 | 0 | 0 | 0 | 2186422.7573 | 0
4634 | 1270.8584 | 0 | 0 | 0 | 0 | 1653.95 | 0 | 0 | 0 | 2329483.4234 | 0
4635 | 1317.8249 | 0 | 0 | 0 | 0 | 1614.45 | 0 | 0 | 0 | 2415573.0289 | 0
4636 | 1299.8671 | 0 | 0 | 0 | 0 | 1582.55 | 0 | 0 | 0 | 2382656.4145 | 0
4637 | 1154.1328 | 0 | 0 | 0 | 0 | 1484.75 | 0 | 0 | 0 | 2115525.4352 | 0
4638 | 1298.4857 | 0 | 0 | 0 | 0 | 1528.45 | 0 | 0 | 0 | 2380124.3669 | 0
4639 | 998.7289 | 329.8589 | 329.8589 | 321.1047 | 321.1047 | 1537.45 | 522518.2304 | 115597.6801 | 52436.3921 | 1242085.2707 | 145385.4782
4640 | 130.6101 | 788.4435 | 135.6783 | 767.5186 | 130.6101 | 1354.75 | 186920.5804 | 47019.6192 | 21328.6217 | 0 | 84276.1369
4641 | 175.9232 | 2017.3848 | 182.7496 | 1963.8445 | 175.9232 | 1614.75 | 300807.5705 | 63332.3643 | 28728.2642 | 0 | 67774.426
4642 | 234.3197 | 3202.6911 | 243.4127 | 3117.6935 | 234.3197 | 1588.1 | 393265.2152 | 84355.0903 | 38264.4062 | 0 | 96516.2825
4643 | 194.8402 | 2216.8571 | 202.4007 | 2158.0229 | 194.8402 | 1461.25 | 300806.2176 | 70142.4732 | 31817.4052 | 0 | 104970.1595
4644 | 182.0764 | 1774.4302 | 189.1414 | 1727.3378 | 182.0764 | 1240 | 238760.3818 | 65547.4913 | 29733.0703 | 0 | 138378.0371
4645 | 203.5454 | 1707.1769 | 211.4446 | 1661.8694 | 203.5454 | 1082 | 232777.5234 | 73276.3477 | 33238.9655 | 0 | 186854.6867
4646 | 203.7794 | 2572.4722 | 211.6876 | 2504.2002 | 203.7794 | 1543.4 | 332197.7346 | 73360.5767 | 33277.1727 | 0 | 93045.6647
4647 | 223.5096 | 2618.4476 | 232.1832 | 2548.9554 | 223.5096 | 1558.65 | 368239.2599 | 80463.4663 | 36499.1224 | 0 | 98645.9746
4648 | 227.8445 | 2035.0663 | 236.6854 | 1981.0567 | 227.8445 | 1450.95 | 349505.2382 | 82024.0321 | 37207.0123 | 0 | 125098.0412
4649 | 436.2411 | 63.2684 | 63.2684 | 61.5893 | 61.5893 | 1682.3 | 109478.9768 | 22172.1459 | 10057.5318 | 686736.8242 | 19152.8622
4650 | 395.2318 | 270.0155 | 270.0155 | 262.8494 | 262.8494 | 1667.55 | 463031.7017 | 94625.7897 | 42923.3096 | 242656.8703 | 85535.7281
4651 | 255.553 | 0 | 0 | 0 | 0 | 1628.6 | 0 | 0 | 0 | 468428.7319 | 0
4652 | 228.6164 | 51.6431 | 51.6431 | 50.2726 | 50.2726 | 1848.7 | 98135.4666 | 18098.1211 | 8209.5088 | 326904.2118 | 7521.7282
4653 | 206.5145 | 214.5277 | 214.5277 | 208.8343 | 206.5145 | 1791.3 | 390997.0067 | 74345.2156 | 33723.8159 | 0 | 43099.4718
4654 | 243.8114 | 253.272 | 253.272 | 246.5503 | 243.8114 | 1887.2 | 485800.3581 | 87772.1108 | 39814.4047 | 0 | 27501.8808
4655 | 205.1331 | 213.0931 | 213.0931 | 207.4378 | 205.1331 | 1882 | 407385.8662 | 73847.9232 | 33498.2385 | 0 | 24205.694
4656 | 192.7008 | 200.1787 | 200.1787 | 194.8661 | 192.7008 | 1862.45 | 378566.9248 | 69372.2915 | 31468.0422 | 0 | 26505.9964
4657 | 223.7816 | 0 | 0 | 0 | 0 | 1850.45 | 0 | 0 | 0 | 266300.0867 | 0
4658 | 188.5567 | 0 | 0 | 0 | 0 | 1641.5 | 0 | 0 | 0 | 224382.4805 | 0
4659 | 172.671 | 0 | 0 | 0 | 0 | 1508.2 | 0 | 0 | 0 | 205478.462 | 0
4660 | 181.6499 | 0 | 0 | 0 | 0 | 1449.3 | 0 | 0 | 0 | 216163.3421 | 0
4661 | 106.3653 | 0 | 0 | 0 | 0 | 1491.15 | 0 | 0 | 0 | 126574.7326 | 0
4662 | 155.4039 | 0 | 0 | 0 | 0 | 1487.2 | 0 | 0 | 0 | 184930.6158 | 0
4663 | 132.6113 | 137.7569 | 137.7569 | 134.1009 | 132.6113 | 1344.3 | 188564.2018 | 47740.0716 | 21655.4269 | 0 | 86953.0327
4664 | 210.6517 | 764.8408 | 218.8263 | 744.5423 | 210.6517 | 1327.4 | 295189.0678 | 75834.6064 | 34399.4201 | 0 | 141684.323
4665 | 378.0493 | 2183.8325 | 392.7201 | 2125.8748 | 378.0493 | 1411.1 | 563760.3665 | 136097.7441 | 61735.4489 | 0 | 222633.2265
4666 | 837.0277 | 3156.2898 | 869.5087 | 3072.5236 | 837.0277 | 1273.7 | 1125403.3234 | 301329.9859 | 136686.6297 | 0 | 607933.2465
4667 | 1269.6825 | 2454.5169 | 1318.9517 | 2389.3754 | 1269.6825 | 1048.75 | 1407364.7464 | 457085.6993 | 207339.1519 | 0 | 1207785.4762
4668 | 1312.5904 | 3342.4509 | 1363.5247 | 3253.7441 | 1312.5904 | 804.1 | 1117684.7805 | 472532.5339 | 214346.0077 | 0 | 1569726.8259
4669 | 1239.8562 | 3261.8843 | 1287.9683 | 3175.3157 | 1239.8562 | 750 | 982445.682 | 446348.2234 | 202468.5135 | 0 | 1549820.22
4670 | 1427.338 | 3632.8456 | 1482.7255 | 3536.4319 | 1427.338 | 1667.8 | 2514823.011 | 513841.6822 | 233084.2964 | 0 | 474161.6856
4671 | 1379.6333 | 3112.1416 | 1433.1693 | 3029.5471 | 1379.6333 | 1748.9 | 2547028.909 | 496667.9995 | 225294.1231 | 0 | 346425.9297
4672 | 1408.1145 | 1979.002 | 1462.7565 | 1926.4804 | 1408.1145 | 1690.75 | 2515394.5209 | 506921.2366 | 229945.1054 | 0 | 435459.4234
4673 | 1482.0911 | 1317.6802 | 1317.6802 | 1282.7097 | 1282.7097 | 1735.5 | 2358229.8614 | 461775.4846 | 209466.4907 | 365466.1603 | 332099.852
4674 | 1357.8284 | 322.1354 | 322.1354 | 313.5861 | 313.5861 | 1284.6 | 426954.4617 | 112891.0073 | 51208.6153 | 1914096.1536 | 219594.1762
4675 | 1372.3889 | 0 | 0 | 0 | 0 | 1613.95 | 0 | 0 | 0 | 4663377.5536 | 0
4676 | 1344.7616 | 0 | 0 | 0 | 0 | 1848.75 | 0 | 0 | 0 | 4569499.7979 | 0
4677 | 1383.4399 | 0 | 0 | 0 | 0 | 1798.65 | 0 | 0 | 0 | 4700928.6579 | 0
4678 | 1246.6844 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1900 | 621549.6215 | 111351.8261 | 50510.4255 | 3185196.2474 | 30587.4
4679 | 1187.2856 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1897 | 1199409.6934 | 215514.4963 | 97759.7701 | 2000179.2003 | 60976
4680 | 944.1649 | 0 | 0 | 0 | 0 | 1879.35 | 0 | 0 | 0 | 1730654.2606 | 0
4681 | 1060.1998 | 0 | 0 | 0 | 0 | 1007.05 | 0 | 0 | 0 | 1261637.7572 | 0
4682 | 1112.0011 | 0 | 0 | 0 | 0 | 1654.3 | 0 | 0 | 0 | 1323281.2959 | 0
4683 | 985.6059 | 0 | 0 | 0 | 0 | 1519.3 | 0 | 0 | 0 | 1172871.0612 | 0
4684 | 1117.5266 | 0 | 0 | 0 | 0 | 1327.55 | 0 | 0 | 0 | 1329856.6064 | 0
4685 | 919.991 | 0 | 0 | 0 | 0 | 1341.4 | 0 | 0 | 0 | 1094789.2456 | 0
4686 | 716.2392 | 0 | 0 | 0 | 0 | 1305.15 | 0 | 0 | 0 | 852324.6604 | 0
4687 | 888.9102 | 222.9992 | 222.9992 | 217.0809 | 217.0809 | 829.25 | 190430.0019 | 78149.124 | 35449.311 | 1231463.083 | 248771.4967
4688 | 709.9428 | 737.4922 | 737.4922 | 717.9195 | 709.9428 | 285.05 | 214670.8572 | 255579.3948 | 115933.6532 | 0 | 1217516.3419
4689 | 511.2727 | 1893.1697 | 531.1128 | 1842.926 | 511.2727 | 302.05 | 163586.4779 | 184058.1784 | 83490.8348 | 0 | 868115.5114
4690 | 207.6748 | 3210.9652 | 215.7338 | 3125.7479 | 207.6748 | 312.45 | 68586.1694 | 74762.9412 | 33913.3008 | 0 | 350461.6708
4691 | 138.7688 | 3711.9278 | 144.1539 | 3613.4152 | 138.7688 | 324.8 | 47615.8642 | 49956.7525 | 22660.938 | 0 | 232465.4217
4692 | 202.4179 | 3970.1684 | 210.2728 | 3864.8023 | 202.4179 | 327.55 | 70141.6042 | 72870.4328 | 33054.838 | 0 | 338533.765
4693 | 689.9172 | 3966.195 | 716.6901 | 3860.9343 | 689.9172 | 331.8 | 242369.1921 | 248370.2088 | 112663.4864 | 0 | 1150919.9511
4694 | 1105.1745 | 2808.2393 | 1148.061 | 2733.7102 | 1105.1745 | 342.7 | 400740.5855 | 397862.8348 | 180475.0025 | 0 | 1831605.7668
4695 | 1065.5889 | 2213.3501 | 1106.9389 | 2154.609 | 1065.5889 | 342.4 | 388395.8831 | 383611.9885 | 174010.6603 | 0 | 1766320.0894
4696 | 1205.8909 | 1508.2946 | 1252.6853 | 1468.2653 | 1205.8909 | 327.9 | 419878.5966 | 434120.7355 | 196921.9892 | 0 | 2016370.2274
4697 | 1007.9081 | 601.4835 | 601.4835 | 585.5205 | 585.5205 | 318.5 | 198576.191 | 210787.3751 | 95615.4954 | 774236.527 | 963726.5025
4698 | 1302.5098 | 150.3992 | 150.3992 | 146.4077 | 146.4077 | 310.55 | 48424.1161 | 52706.764 | 23908.3738 | 2119135.2634 | 242115.0795
4699 | 973.1736 | 0 | 0 | 0 | 0 | 804.1 | 0 | 0 | 0 | 3306843.9727 | 0
4700 | 879.9313 | 0 | 0 | 0 | 0 | 1417.8 | 0 | 0 | 0 | 2990006.5445 | 0
4701 | 879.2406 | 0 | 0 | 0 | 0 | 1338.5 | 0 | 0 | 0 | 2987659.6003 | 0
4702 | 925.5164 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1197.05 | 393268.9269 | 111351.8261 | 50510.4255 | 2093867.3287 | 245601.5283
4703 | 1076.0855 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1109 | 705692.9707 | 215514.4963 | 97759.7701 | 1622321.2299 | 527472
4704 | 1077.4669 | 0 | 0 | 0 | 0 | 1121.55 | 0 | 0 | 0 | 1974996.8149 | 0
4705 | 1165.8744 | 0 | 0 | 0 | 0 | 1162.5 | 0 | 0 | 0 | 1387390.5753 | 0
4706 | 1019.4494 | 0 | 0 | 0 | 0 | 1018.45 | 0 | 0 | 0 | 1213144.8395 | 0
4707 | 1090.5899 | 0 | 0 | 0 | 0 | 469.95 | 0 | 0 | 0 | 1297801.9655 | 0
4708 | 797.7399 | 0 | 0 | 0 | 0 | 288.55 | 0 | 0 | 0 | 949310.4944 | 0
4709 | 1000.1103 | 0 | 0 | 0 | 0 | 283.85 | 0 | 0 | 0 | 1190131.2522 | 0
4710 | 815.6977 | 0 | 0 | 0 | 0 | 282.35 | 0 | 0 | 0 | 970680.2546 | 0
4711 | 1003.5637 | 333.8511 | 333.8511 | 324.9908 | 324.9908 | 638.05 | 220260.3016 | 116996.7041 | 53071.0049 | 1243824.0714 | 433258.0862
4712 | 951.6977 | 988.6284 | 988.6284 | 962.3907 | 951.6977 | 675.5 | 683372.1076 | 342611.1615 | 155412.2296 | 0 | 1260523.565
4713 | 1121.6603 | 1272.38 | 1165.1857 | 1238.6117 | 1121.6603 | 1417.3 | 1680226.9033 | 403797.7091 | 183167.1275 | 0 | 653591.4586
4714 | 1083.6407 | 2518.1095 | 1125.6914 | 2451.2802 | 1083.6407 | 1403.2 | 1607831.7242 | 390110.6678 | 176958.5335 | 0 | 646716.796
4715 | 1503.6577 | 2779.8457 | 1562.006 | 2706.0701 | 1503.6577 | 1381.45 | 2198271.513 | 541316.777 | 245547.3047 | 0 | 930087.479
4716 | 1480.6329 | 3195.2813 | 1538.0886 | 3110.4803 | 1480.6329 | 1299.3 | 2034170.384 | 533027.8451 | 241787.3531 | 0 | 1037479.4751
4717 | 1652.4707 | 2999.1841 | 1716.5937 | 2919.5874 | 1652.4707 | 937 | 1640546.9445 | 594889.4671 | 269848.4722 | 0 | 1756576.3987
4718 | 1615.0866 | 3174.5229 | 1677.76 | 3090.2728 | 1615.0866 | 1290.7 | 2207121.1978 | 581431.1803 | 263743.6437 | 0 | 1145580.9339
4719 | 1540.0611 | 3074.6823 | 1599.8227 | 2993.0819 | 1540.0611 | 854.55 | 1392126.1726 | 554421.9863 | 251491.9732 | 0 | 1764062.9561
4720 | 1743.6635 | 1595.6508 | 1595.6508 | 1553.3031 | 1553.3031 | 903.45 | 1486384.546 | 559189.129 | 253654.4021 | 348930.4826 | 1667243.9648
4721 | 1217.598 | 605.3988 | 605.3988 | 589.3318 | 589.3318 | 1657.9 | 1034217.7281 | 212159.4598 | 96237.8883 | 1151611.9287 | 197345.5165
4722 | 1425.4723 | 88.1956 | 88.1956 | 85.8549 | 85.8549 | 1855.05 | 168288.3925 | 30907.7639 | 14020.1051 | 2455518.6872 | 12181.4531
4723 | 1408.9952 | 0 | 0 | 0 | 0 | 1861.7 | 0 | 0 | 0 | 4787765.5809 | 0
4724 | 1178.3067 | 0 | 0 | 0 | 0 | 1868.7 | 0 | 0 | 0 | 4003886.3161 | 0
4725 | 1460.1058 | 0 | 0 | 0 | 0 | 1871.3 | 0 | 0 | 0 | 4961439.4302 | 0
4726 | 1165.1837 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1887.2 | 615801.8493 | 111351.8261 | 50510.4255 | 2908256.8654 | 34502.5872
4727 | 1237.7056 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1882 | 1188493.7745 | 215514.4963 | 97759.7701 | 2171506.1054 | 69856
4728 | 1343.3802 | 0 | 0 | 0 | 0 | 1632.5 | 0 | 0 | 0 | 2462415.9011 | 0
4729 | 1258.4261 | 0 | 0 | 0 | 0 | 926.3 | 0 | 0 | 0 | 1497527.0316 | 0
4730 | 1290.1975 | 0 | 0 | 0 | 0 | 1273.95 | 0 | 0 | 0 | 1535335.0678 | 0
4731 | 1518.8139 | 0 | 0 | 0 | 0 | 1163.75 | 0 | 0 | 0 | 1807388.5517 | 0
4732 | 1493.2586 | 0 | 0 | 0 | 0 | 707.35 | 0 | 0 | 0 | 1776977.74 | 0
4733 | 1221.1291 | 0 | 0 | 0 | 0 | 283.85 | 0 | 0 | 0 | 1453143.6837 | 0
4734 | 1216.2944 | 0 | 0 | 0 | 0 | 1119.95 | 0 | 0 | 0 | 1447390.286 | 0
4735 | 1270.1677 | 330.1789 | 330.1789 | 321.4161 | 321.4161 | 1126.65 | 383438.1589 | 115709.8058 | 52487.2536 | 1739061.6382 | 274770.757
4736 | 1420.868 | 1106.7758 | 1106.7758 | 1077.4026 | 1077.4026 | 1259.05 | 1437027.6704 | 387864.9337 | 175939.8436 | 629572.1337 | 781414.7614
4737 | 1032.7373 | 1225.9433 | 1072.8121 | 1193.4075 | 1032.7373 | 1569.15 | 1714856.5304 | 371785.4424 | 168646.0076 | 0 | 444954.8829
4738 | 983.6487 | 2003.2093 | 1021.8193 | 1950.0452 | 983.6487 | 1376.2 | 1431386.1989 | 354113.535 | 160629.834 | 0 | 613600.0642
4739 | 1036.9712 | 2733.4391 | 1077.2104 | 2660.8952 | 1036.9712 | 1381.45 | 1516096.1146 | 373309.6435 | 169337.4022 | 0 | 641418.5556
4740 | 1264.5447 | 2743.2268 | 1313.6154 | 2670.423 | 1264.5447 | 1223.6 | 1636353.487 | 455236.0823 | 206500.1451 | 0 | 981792.4841
4741 | 1287.5099 | 3184.9494 | 1337.4715 | 3100.4226 | 1287.5099 | 740.25 | 1007426.155 | 463503.5687 | 210250.3688 | 0 | 1621940.6129
4742 | 1054.9635 | 2948.3533 | 1095.9006 | 2870.1056 | 1054.9635 | 1363.2 | 1522437.7503 | 379786.8773 | 172275.5474 | 0 | 671800.7874
4743 | 1243.8855 | 1035.2572 | 1035.2572 | 1007.7821 | 1007.7821 | 1273.35 | 1359009.4088 | 362801.5443 | 164570.8116 | 432777.5073 | 716814.0656
4744 | 986.9251 | 848.878 | 848.878 | 826.3492 | 826.3492 | 1473.45 | 1287664.1269 | 297485.7261 | 134942.8308 | 294335.626 | 425909.9719
4745 | 1104.938 | 1053.3896 | 1053.3896 | 1025.4332 | 1025.4332 | 1798.2 | 1952374.9451 | 369155.9456 | 167453.2386 | 145732.2981 | 202555.1356
4746 | 1034.1178 | 0 | 0 | 0 | 0 | 1875.05 | 0 | 0 | 0 | 1895538.0099 | 0
4747 | 840.5623 | 0 | 0 | 0 | 0 | 1861.7 | 0 | 0 | 0 | 2856230.7413 | 0
4748 | 1201.79 | 0 | 0 | 0 | 0 | 1868.7 | 0 | 0 | 0 | 4083682.4064 | 0
4749 | 714.1672 | 0 | 0 | 0 | 0 | 1871.3 | 0 | 0 | 0 | 2426740.0053 | 0
4750 | 1128.5775 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1824.7 | 598113.3533 | 111351.8261 | 50510.4255 | 2783868.8381 | 53619.7122
4751 | 844.7064 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1495.9 | 949202.1684 | 215514.4963 | 97759.7701 | 836095.0209 | 298427.2
4752 | 1005.6358 | 0 | 0 | 0 | 0 | 827.95 | 0 | 0 | 0 | 1843330.3609 | 0
4753 | 1029.119 | 0 | 0 | 0 | 0 | 324.9 | 0 | 0 | 0 | 1224651.6338 | 0
4754 | 1085.7551 | 0 | 0 | 0 | 0 | 304.95 | 0 | 0 | 0 | 1292048.569 | 0
4755 | 1188.667 | 0 | 0 | 0 | 0 | 644.95 | 0 | 0 | 0 | 1414513.7324 | 0
4756 | 1035.3352 | 0 | 0 | 0 | 0 | 288.55 | 0 | 0 | 0 | 1232048.8583 | 0
4757 | 943.4742 | 0 | 0 | 0 | 0 | 283.85 | 0 | 0 | 0 | 1122734.3164 | 0
4758 | 1012.5426 | 0 | 0 | 0 | 0 | 282.35 | 0 | 0 | 0 | 1204925.7011 | 0
4759 | 1096.806 | 29.2029 | 29.2029 | 28.4279 | 28.4279 | 289.05 | 8680.6186 | 10234.0262 | 4642.268 | 1958337.2267 | 47610.6056
4760 | 934.3477 | 125.7972 | 125.7972 | 122.4586 | 122.4586 | 318.75 | 41260.4675 | 44085.092 | 19997.4876 | 1488192.7241 | 201528.075
4761 | 1094.2419 | 1316.1791 | 1136.7038 | 1281.2484 | 1094.2419 | 1281.55 | 1477290.3133 | 393927.0764 | 178689.6988 | 0 | 786158.078
4762 | 1260.8348 | 2237.2914 | 1309.7614 | 2177.915 | 1260.8348 | 387.2 | 514330.7488 | 453900.5413 | 205894.3289 | 0 | 2033474.4251
4763 | 1083.1262 | 2604.1588 | 1125.1564 | 2535.0459 | 1083.1262 | 392.45 | 447779.2679 | 389925.4266 | 176874.506 | 0 | 1741179.4987
4764 | 1249.8858 | 2993.3834 | 1298.3875 | 2913.9406 | 1249.8858 | 386 | 508131.1205 | 449958.8772 | 204106.3462 | 0 | 2017315.6328
4765 | 1115.5132 | 3153.5931 | 1158.8002 | 3069.8984 | 1115.5132 | 390.75 | 458794.8227 | 401584.7578 | 182163.3082 | 0 | 1795139.6428
4766 | 1150.3401 | 2792.7445 | 1194.9787 | 2718.6266 | 1150.3401 | 422.4 | 512183.3225 | 414122.432 | 187850.5365 | 0 | 1814776.5244
4767 | 1467.4236 | 2371.9579 | 1524.367 | 2309.0075 | 1467.4236 | 435.75 | 676269.3279 | 528272.4863 | 239630.2695 | 0 | 2295417.3241
4768 | 1501.2835 | 2188.9725 | 1559.5399 | 2130.8783 | 1501.2835 | 429.45 | 680712.8422 | 540462.0557 | 245159.5936 | 0 | 2357840.7821
4769 | 1430.4064 | 1226.1137 | 1226.1137 | 1193.5733 | 1193.5733 | 1682.3 | 2117165.6052 | 429686.3954 | 194910.5233 | 434114.9776 | 371177.1702
4770 | 1592.421 | 349.8372 | 349.8372 | 340.5527 | 340.5527 | 1489.45 | 535375.2592 | 122598.9888 | 55612.2635 | 2294674.4275 | 170190.8214
4771 | 1372.3889 | 0 | 0 | 0 | 0 | 1520.8 | 0 | 0 | 0 | 4663377.5536 | 0
4772 | 1328.8758 | 0 | 0 | 0 | 0 | 1708.7 | 0 | 0 | 0 | 4515520.0873 | 0
4773 | 1486.3518 | 0 | 0 | 0 | 0 | 1513.25 | 0 | 0 | 0 | 5050623.3009 | 0
4774 | 1364.1007 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1546.3 | 504157.6 | 111351.8261 | 50510.4255 | 3584176.7124 | 138775.0338
4775 | 1410.3765 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 722.5 | 455663.7514 | 215514.4963 | 97759.7701 | 2758242.0853 | 756280
4776 | 1210.7689 | 0 | 0 | 0 | 0 | 353.45 | 0 | 0 | 0 | 2219339.3699 | 0
4777 | 1007.0171 | 0 | 0 | 0 | 0 | 780.95 | 0 | 0 | 0 | 1198350.3906 | 0
4778 | 820.5325 | 0 | 0 | 0 | 0 | 761 | 0 | 0 | 0 | 976433.6514 | 0
4779 | 1060.8905 | 0 | 0 | 0 | 0 | 295.45 | 0 | 0 | 0 | 1262459.6712 | 0
4780 | 1237.7056 | 0 | 0 | 0 | 0 | 288.55 | 0 | 0 | 0 | 1472869.6152 | 0
4781 | 960.7413 | 0 | 0 | 0 | 0 | 283.85 | 0 | 0 | 0 | 1143282.1626 | 0
4782 | 1200.4086 | 0 | 0 | 0 | 0 | 1087.9 | 0 | 0 | 0 | 1428486.2685 | 0
4783 | 1122.3613 | 323.5669 | 323.5669 | 314.9796 | 314.9796 | 1119.1 | 373338.5814 | 113392.661 | 51436.1709 | 1479930.717 | 271596.4453
4784 | 1070.4651 | 1112.0041 | 1112.0041 | 1082.4921 | 1070.4651 | 318.75 | 360821.6393 | 385367.4306 | 174806.9484 | 0 | 1799719.2812
4785 | 1185.2757 | 1873.3078 | 1231.2703 | 1823.5912 | 1185.2757 | 1191.75 | 1490908.9744 | 426699.2678 | 193555.529 | 0 | 957999.1201
4786 | 1241.5501 | 2200.5292 | 1289.728 | 2142.1283 | 1241.5501 | 387.2 | 507310.8263 | 446958.0284 | 202745.1279 | 0 | 2002371.9674
4787 | 1273.3423 | 2864.6412 | 1322.7537 | 2788.6152 | 1273.3423 | 392.45 | 528209.7275 | 458403.2132 | 207936.7909 | 0 | 2046961.3485
4788 | 1429.0673 | 4065.7623 | 1484.5216 | 3957.8592 | 1429.0673 | 386 | 583125.3094 | 514464.2302 | 233366.6911 | 0 | 2306514.6319
4789 | 1265.5332 | 2871.4423 | 1314.6417 | 2795.2358 | 1265.5332 | 390.75 | 521400.6246 | 455591.957 | 206661.5738 | 0 | 2036559.3246
4790 | 1185.2801 | 2971.1873 | 1231.2745 | 2892.3336 | 1185.2801 | 422.4 | 529324.0198 | 426700.822 | 193556.234 | 0 | 1869897.8242
4791 | 1296.2238 | 2938.8025 | 1346.5236 | 2860.8083 | 1296.2238 | 435.75 | 597260.7565 | 466640.5511 | 211673.3389 | 0 | 2027618.0056
4792 | 1491.7106 | 1733.0743 | 1549.5965 | 1687.0795 | 1491.7106 | 429.45 | 676029.0213 | 537015.8192 | 243596.3424 | 0 | 2342806.097
4793 | 1623.4698 | 741.8406 | 741.8406 | 722.1526 | 722.1526 | 1551.95 | 1182430.4784 | 259974.9184 | 117927.5116 | 1652114.4952 | 316715.7918
4794 | 1365.0331 | 16.1337 | 16.1337 | 15.7055 | 15.7055 | 1461.95 | 24204.6434 | 5653.9791 | 2564.7078 | 2473317.5631 | 8271.4427
4795 | 1483.589 | 0 | 0 | 0 | 0 | 1424.25 | 0 | 0 | 0 | 5041235.5239 | 0
4796 | 1207.3155 | 0 | 0 | 0 | 0 | 1381.2 | 0 | 0 | 0 | 4102457.9603 | 0
4797 | 1394.4908 | 0 | 0 | 0 | 0 | 1351.3 | 0 | 0 | 0 | 4738479.7588 | 0
4798 | 1198.3366 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 834.25 | 272925.1042 | 111351.8261 | 50510.4255 | 3020910.1749 | 356572.6155
4799 | 1087.8272 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 373 | 236452.8538 | 215514.4963 | 97759.7701 | 1662219.2784 | 963184
4800 | 982.8432 | 0 | 0 | 0 | 0 | 353.45 | 0 | 0 | 0 | 1801551.5821 | 0
4801 | 1308.846 | 0 | 0 | 0 | 0 | 324.9 | 0 | 0 | 0 | 2399114.7217 | 0
4802 | 1232.1801 | 0 | 0 | 0 | 0 | 304.95 | 0 | 0 | 0 | 2258586.1013 | 0
4803 | 1165.8744 | 0 | 0 | 0 | 0 | 295.45 | 0 | 0 | 0 | 2137047.8357 | 0
4804 | 1230.108 | 0 | 0 | 0 | 0 | 288.55 | 0 | 0 | 0 | 2254788.03 | 0
4805 | 1178.9974 | 0 | 0 | 0 | 0 | 283.85 | 0 | 0 | 0 | 2161102.2837 | 0
4806 | 1110.6197 | 0 | 0 | 0 | 0 | 282.35 | 0 | 0 | 0 | 2035765.9486 | 0
4807 | 929.6605 | 147.8676 | 147.8676 | 143.9433 | 143.9433 | 289.05 | 43872.9495 | 51819.5869 | 23505.9404 | 1440219.7017 | 241071.1441
4808 | 777.6212 | 807.7974 | 807.7974 | 786.3589 | 777.6212 | 318.75 | 261421.2382 | 279943.6149 | 126985.5342 | 0 | 1307375.3062
4809 | 947.273 | 1343.24 | 984.0317 | 1307.5911 | 947.273 | 368.25 | 368455.9489 | 341018.2717 | 154689.6771 | 0 | 1545712.6802
4810 | 1179.9083 | 1501.8426 | 1225.694 | 1461.9845 | 1179.9083 | 387.2 | 482934.1282 | 424766.9761 | 192679.02 | 0 | 1902956.053
4811 | 1059.5877 | 2605.3358 | 1100.705 | 2536.1916 | 1059.5877 | 392.45 | 440479.8895 | 381451.5637 | 173030.6677 | 0 | 1703340.1702
4812 | 1194.5136 | 2409.517 | 1240.8658 | 2345.5697 | 1194.5136 | 386 | 488886.5207 | 430024.9108 | 195064.0776 | 0 | 1927945.0166
4813 | 1267.6269 | 3020.4276 | 1316.8169 | 2940.2671 | 1267.6269 | 390.75 | 525412.4841 | 456345.666 | 207003.4646 | 0 | 2039928.5084
4814 | 887.0799 | 2887.6466 | 921.5029 | 2811.01 | 887.0799 | 422.4 | 398063.1713 | 319348.7549 | 144860.1435 | 0 | 1399457.2102
4815 | 1241.5596 | 2687.0316 | 1289.7374 | 2615.7192 | 1241.5596 | 435.75 | 574638.3546 | 446961.4474 | 202746.6788 | 0 | 1942109.5668
4816 | 536.721 | 1753.1575 | 557.5483 | 1706.6297 | 536.721 | 429.45 | 244668.1142 | 193219.5479 | 87646.5338 | 0 | 842947.1138
4817 | 511.4393 | 875.2304 | 531.2853 | 852.0023 | 511.4393 | 1357.3 | 734632.8554 | 184118.1643 | 83518.0451 | 0 | 328702.0673
4818 | 220.4508 | 234.7803 | 229.0055 | 228.5493 | 220.4508 | 1747.15 | 407652.6098 | 79362.2745 | 35999.6095 | 0 | 55740.9753
4819 | 219.6375 | 123.3913 | 123.3913 | 120.1166 | 120.1166 | 1786.7 | 227329.8595 | 43241.9643 | 19615.0355 | 182421.8362 | 25336.2006
4820 | 234.8325 | 243.9456 | 243.9456 | 237.4715 | 234.8325 | 1863.7 | 463276.9873 | 84539.7101 | 38348.1518 | 0 | 32007.6736
4821 | 155.4039 | 161.4344 | 161.4344 | 157.15 | 155.4039 | 1743.4 | 286771.3469 | 55945.3964 | 25377.4534 | 0 | 39876.6353
4822 | 212.04 | 220.2682 | 220.2682 | 214.4224 | 212.04 | 1356.25 | 304622.3435 | 76334.3853 | 34626.1253 | 0 | 136500.7237
4823 | 91.1703 | 94.7078 | 94.7078 | 92.1943 | 91.1703 | 373 | 36051.6374 | 32821.2992 | 14888.106 | 0 | 148333.59
4824 | 85.6448 | 88.9684 | 88.9684 | 86.6073 | 85.6448 | 353.45 | 32185.3098 | 30832.1296 | 13985.7965 | 0 | 141018.4526
4825 | 78.738 | 0 | 0 | 0 | 0 | 796.15 | 0 | 0 | 0 | 93698.1787 | 0
4826 | 84.9541 | 0 | 0 | 0 | 0 | 719.9 | 0 | 0 | 0 | 101095.4033 | 0
4827 | 77.3566 | 0 | 0 | 0 | 0 | 1218.6 | 0 | 0 | 0 | 92054.351 | 0
4828 | 82.1914 | 0 | 0 | 0 | 0 | 1209.65 | 0 | 0 | 0 | 97807.7479 | 0
4829 | 78.738 | 0 | 0 | 0 | 0 | 1201.55 | 0 | 0 | 0 | 93698.1787 | 0
4830 | 83.5728 | 0 | 0 | 0 | 0 | 1215.3 | 0 | 0 | 0 | 99451.5756 | 0
4831 | 66.9963 | 69.5968 | 69.5968 | 67.7497 | 66.9963 | 1198.8 | 85054.233 | 24118.682 | 10940.5021 | 0 | 53677.4667
4832 | 81.1985 | 381.4948 | 84.3489 | 371.3701 | 81.1985 | 1225.4 | 105519.8058 | 29231.4696 | 13259.7194 | 0 | 62896.3788
4833 | 713.0577 | 1327.4751 | 740.727 | 1292.2446 | 713.0577 | 1558.9 | 1175118.6793 | 256700.7892 | 116442.3302 | 0 | 314529.7725
4834 | 1109.9109 | 2652.216 | 1152.9808 | 2581.8277 | 1109.9109 | 1331.95 | 1563016.8671 | 399567.9262 | 181248.4509 | 0 | 741475.9808
4835 | 1211.7488 | 3263.8653 | 1258.7696 | 3177.2441 | 1211.7488 | 1236.95 | 1586381.1195 | 436229.5662 | 197878.5782 | 0 | 924624.918
4836 | 1105.1884 | 4069.3524 | 1148.0745 | 3961.354 | 1105.1884 | 684.85 | 801965.871 | 397867.8078 | 180477.2584 | 0 | 1453488.4651
4837 | 969.134 | 3196.5404 | 1006.741 | 3111.7059 | 969.134 | 393.3 | 403062.1804 | 348888.235 | 158259.5799 | 0 | 1557107.5753
4838 | 1192.262 | 2305.6438 | 1238.5274 | 2244.4532 | 1192.262 | 421.3 | 532453.6669 | 429214.3243 | 194696.3866 | 0 | 1882224.0383
4839 | 1204.9136 | 2417.0992 | 1251.6704 | 2352.9507 | 1204.9136 | 427.4 | 545911.4208 | 433768.901 | 196762.3932 | 0 | 1894847.1494
4840 | 1193.8661 | 1938.8283 | 1240.1937 | 1887.3729 | 1193.8661 | 864.7 | 1092392.0895 | 429791.805 | 194958.3382 | 0 | 1355396.2117
4841 | 893.7415 | 722.8149 | 722.8149 | 703.6318 | 703.6318 | 1315.5 | 978556.3274 | 253307.4387 | 114903.0687 | 348471.1659 | 471448.006
4842 | 898.8077 | 84.5764 | 84.5764 | 82.3318 | 82.3318 | 1274.35 | 110970.7601 | 29639.432 | 13444.7757 | 1496600.3829 | 58480.1335
4843 | 882.694 | 0 | 0 | 0 | 0 | 1433.95 | 0 | 0 | 0 | 2999394.3201 | 0
4844 | 1020.8308 | 0 | 0 | 0 | 0 | 1540.45 | 0 | 0 | 0 | 3468783.1026 | 0
4845 | 1455.9617 | 0 | 0 | 0 | 0 | 1279.05 | 0 | 0 | 0 | 4947357.7683 | 0
4846 | 774.9473 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 845.7 | 277453.504 | 111351.8261 | 50510.4255 | 1582233.5561 | 353070.3582
4847 | 1051.2209 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 388 | 246226.3859 | 215514.4963 | 97759.7701 | 1537831.2511 | 954304
4848 | 1114.0731 | 0 | 0 | 0 | 0 | 370.35 | 0 | 0 | 0 | 2042096.0656 | 0
4849 | 966.9575 | 0 | 0 | 0 | 0 | 717.05 | 0 | 0 | 0 | 1150679.3873 | 0
4850 | 895.1263 | 0 | 0 | 0 | 0 | 333.2 | 0 | 0 | 0 | 1065200.3471 | 0
4851 | 941.4022 | 0 | 0 | 0 | 0 | 318.4 | 0 | 0 | 0 | 1120268.5749 | 0
4852 | 939.3301 | 0 | 0 | 0 | 0 | 308.05 | 0 | 0 | 0 | 1117802.8334 | 0
4853 | 1111.3104 | 0 | 0 | 0 | 0 | 297.35 | 0 | 0 | 0 | 1322459.382 | 0
4854 | 1126.5055 | 0 | 0 | 0 | 0 | 286.15 | 0 | 0 | 0 | 1340541.4867 | 0
4855 | 1100.2595 | 333.5914 | 333.5914 | 324.738 | 324.738 | 277.35 | 95940.0512 | 116905.6929 | 53029.7212 | 1421530.7743 | 547575.3102
4856 | 882.8235 | 900.6603 | 900.6603 | 876.7573 | 876.7573 | 285.05 | 265508.3746 | 315632.6292 | 143174.4676 | 11119.4027 | 1471788.9545
4857 | 886.201 | 952.5154 | 920.5898 | 927.2362 | 886.201 | 302.05 | 283478.3692 | 319032.3525 | 144716.6199 | 0 | 1504724.9528
4858 | 1103.5739 | 1408.1185 | 1146.3979 | 1370.7478 | 1103.5739 | 312.45 | 364794.7004 | 397286.5975 | 180213.6149 | 0 | 1862336.1046
4859 | 1112.4017 | 2566.5988 | 1155.5674 | 2498.4827 | 1112.4017 | 324.8 | 382415.4197 | 400464.6066 | 181655.1952 | 0 | 1863495.3027
4860 | 1166.9312 | 2607.2285 | 1212.2135 | 2538.0341 | 1166.9312 | 327.55 | 404678.9449 | 420095.2248 | 190559.8617 | 0 | 1951634.052
4861 | 990.0065 | 3266.6036 | 1028.4229 | 3179.9097 | 990.0065 | 331.8 | 347612.6468 | 356402.3233 | 161668.0539 | 0 | 1651528.7659
4862 | 1284.0444 | 1620.8793 | 1333.871 | 1577.862 | 1284.0444 | 342.7 | 466106.4067 | 462255.9862 | 209684.4515 | 0 | 2128046.7941
4863 | 1002.3878 | 1212.5417 | 1041.2854 | 1180.3615 | 1002.3878 | 342.4 | 363924.2237 | 360859.6174 | 163689.932 | 0 | 1661558.0604
4864 | 1384.9171 | 907.3201 | 907.3201 | 883.2403 | 883.2403 | 327.9 | 307974.7193 | 317966.5201 | 144233.1465 | 919573.4466 | 1445625.7597
4865 | 1471.9052 | 331.5148 | 331.5148 | 322.7166 | 322.7166 | 318.5 | 109867.0509 | 116177.9674 | 52699.6169 | 2106462.8356 | 531169.035
4866 | 1181.0885 | 230.7165 | 230.7165 | 224.5934 | 224.5934 | 310.55 | 74494.2114 | 80853.6125 | 36676.097 | 1753255.5275 | 371413.7563
4867 | 1185.2136 | 0 | 0 | 0 | 0 | 942.85 | 0 | 0 | 0 | 4027355.755 | 0
4868 | 1040.17 | 0 | 0 | 0 | 0 | 1241.55 | 0 | 0 | 0 | 3534497.5309 | 0
4869 | 1251.5192 | 0 | 0 | 0 | 0 | 569 | 0 | 0 | 0 | 4252662.3707 | 0
4870 | 1156.8955 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 789.65 | 259322.7564 | 111351.8261 | 50510.4255 | 2880093.538 | 370214.5959
4871 | 1042.9327 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1134.05 | 722221.7933 | 215514.4963 | 97759.7701 | 1509667.9237 | 512642.4
4872 | 1049.8395 | 0 | 0 | 0 | 0 | 304.7 | 0 | 0 | 0 | 1924355.8713 | 0
4873 | 880.622 | 0 | 0 | 0 | 0 | 324.9 | 0 | 0 | 0 | 1047940.1563 | 0
4874 | 931.0419 | 0 | 0 | 0 | 0 | 304.95 | 0 | 0 | 0 | 1107939.8672 | 0
4875 | 782.5449 | 0 | 0 | 0 | 0 | 295.45 | 0 | 0 | 0 | 931228.3898 | 0
4876 | 743.1759 | 0 | 0 | 0 | 0 | 288.55 | 0 | 0 | 0 | 884379.3005 | 0
4877 | 860.5921 | 0 | 0 | 0 | 0 | 283.85 | 0 | 0 | 0 | 1024104.6547 | 0
4878 | 848.8505 | 0 | 0 | 0 | 0 | 282.35 | 0 | 0 | 0 | 1010132.1193 | 0
4879 | 506.2713 | 291.7494 | 291.7494 | 284.0065 | 284.0065 | 289.05 | 87309.9081 | 102242.3341 | 46378.2588 | 407411.4139 | 475642.389
4880 | 90.0212 | 267.7748 | 93.5142 | 260.6682 | 90.0212 | 675.4 | 64632.4464 | 32407.6141 | 14700.4538 | 0 | 119242.0156
4881 | 76.9871 | 1580.0334 | 79.9755 | 1538.1002 | 76.9871 | 1462.25 | 119680.4774 | 27715.3494 | 12571.9904 | 0 | 41399.8031
4882 | 90.8526 | 2557.1779 | 94.3775 | 2489.3118 | 90.8526 | 1458.75 | 140825.284 | 32706.922 | 14836.2232 | 0 | 49173.9486
4883 | 77.379 | 3033.1603 | 80.3817 | 2952.6619 | 77.379 | 1406.5 | 115508.4305 | 27856.4561 | 12635.998 | 0 | 45924.463
4884 | 103.2926 | 3283.4883 | 107.3013 | 3196.3463 | 103.2926 | 1200 | 131775.4117 | 37185.3509 | 16867.6884 | 0 | 82634.1132
4885 | 71.5652 | 3110.7642 | 74.3421 | 3028.2062 | 71.5652 | 390.75 | 29692.2708 | 25763.4766 | 11686.5993 | 0 | 115166.3189
4886 | 75.749 | 2862.1221 | 78.6884 | 2786.163 | 75.749 | 1342.95 | 107900.1973 | 27269.651 | 12369.8167 | 0 | 49770.9006
4887 | 91.6762 | 2674.7134 | 95.2345 | 2603.728 | 91.6762 | 1529.75 | 148785.8346 | 33003.4326 | 14970.7237 | 0 | 43110.7338
4888 | 85.3392 | 1798.0152 | 88.6506 | 1750.2969 | 85.3392 | 1820.55 | 164702.7888 | 30722.1036 | 13935.8876 | 0 | 15314.1153
4889 | 76.2014 | 1205.4508 | 79.159 | 1173.4588 | 76.2014 | 1915.3 | 154727.143 | 27432.5143 | 12443.6933 | 0 | 6454.261
4890 | 81.8383 | 347.6963 | 85.0147 | 338.4686 | 81.8383 | 1874.95 | 162421.5929 | 29461.7782 | 13364.1899 | 0 | 10233.876
4891 | 78.0473 | 81.0756 | 81.0756 | 78.9239 | 78.0473 | 1858.95 | 153489.1725 | 28097.0213 | 12745.121 | 0 | 11008.5294
4892 | 82.8821 | 86.0982 | 86.0982 | 83.8132 | 82.8821 | 1849.5 | 162086.4102 | 29837.5447 | 13534.6418 | 0 | 12473.741
4893 | 75.2845 | 78.2064 | 78.2064 | 76.1309 | 75.2845 | 1383.95 | 110346.5157 | 27102.4365 | 12293.9663 | 0 | 46379.0444
4894 | 79.4286 | 82.5112 | 82.5112 | 80.3214 | 79.4286 | 1337.2 | 112453.0651 | 28594.3137 | 12970.6984 | 0 | 52645.3087
4895 | 75.9752 | 78.9232 | 78.9232 | 76.8286 | 75.9752 | 1293.55 | 104047.4173 | 27351.0827 | 12406.755 | 0 | 53672.5388
4896 | 78.738 | 81.7934 | 81.7934 | 79.6227 | 78.738 | 353.45 | 29530.6394 | 28345.6675 | 12857.9097 | 0 | 129645.9967
4897 | 74.5939 | 45.1859 | 45.1859 | 43.9867 | 43.9867 | 324.9 | 15210.3583 | 15835.2188 | 7183.0312 | 36422.5 | 72863.4998
4898 | 80.81 | 83.9458 | 83.9458 | 81.7179 | 80.81 | 304.95 | 26310.6687 | 29091.6061 | 13196.2758 | 0 | 136976.9905
4899 | 74.5939 | 77.4886 | 77.4886 | 75.4321 | 74.5939 | 295.45 | 23556.4304 | 26853.7903 | 12181.1776 | 0 | 127148.9672
4900 | 77.3566 | 80.3588 | 80.3588 | 78.2261 | 77.3566 | 288.55 | 23868.8057 | 27848.3751 | 12632.3324 | 0 | 132391.9487
4901 | 71.8311 | 74.6184 | 74.6184 | 72.6381 | 71.8311 | 283.85 | 21786.446 | 25859.2054 | 11730.0229 | 0 | 123272.7707
4902 | 79.4286 | 82.5112 | 82.5112 | 80.3214 | 79.4286 | 282.35 | 23979.4076 | 28594.3137 | 12970.6984 | 0 | 136430.6193
4903 | 66.3057 | 68.879 | 68.879 | 67.051 | 66.3057 | 289.05 | 20457.4115 | 23870.0358 | 10827.7135 | 0 | 113444.5397
4904 | 72.9207 | 75.7496 | 75.7496 | 73.7393 | 72.9207 | 318.75 | 24752.8674 | 26251.4448 | 11907.9471 | 0 | 122597.8934
4905 | 154.285 | 1183.8998 | 160.272 | 1152.4797 | 154.285 | 368.25 | 60399.9554 | 55542.5895 | 25194.7357 | 0 | 251754.5013
4906 | 105.3492 | 2568.9236 | 109.437 | 2500.7458 | 105.3492 | 387.2 | 43314.4036 | 37925.695 | 17203.5167 | 0 | 169907.1136
4907 | 130.5488 | 2926.5488 | 135.6149 | 2848.8798 | 130.5488 | 392.45 | 54344.0859 | 46997.5518 | 21318.6117 | 0 | 209863.6513
4908 | 202.7269 | 2750.4714 | 210.5938 | 2677.4754 | 202.7269 | 386 | 83084.4403 | 72981.702 | 33105.3109 | 0 | 327201.2973
4909 | 354.6912 | 2052.2523 | 368.4547 | 1997.7866 | 354.6912 | 390.75 | 146989.3049 | 127688.8403 | 57921.0767 | 0 | 570786.8506
4910 | 688.6006 | 2437.9813 | 715.3209 | 2373.2786 | 688.6006 | 422.4 | 309339.2356 | 247896.227 | 112448.483 | 0 | 1086336.3548
4911 | 987.823 | 2050.076 | 1026.1552 | 1995.6681 | 987.823 | 435.75 | 457986.1891 | 355616.2905 | 161311.5007 | 0 | 1545202.1733
4912 | 1032.5448 | 1871.3257 | 1072.6126 | 1821.6618 | 1032.5448 | 429.45 | 470829.5636 | 371716.1323 | 168614.5678 | 0 | 1621663.2545
4913 | 1329.4033 | 859.0261 | 859.0261 | 836.228 | 836.228 | 1365.4 | 1211794.2021 | 301042.0794 | 136556.0321 | 903990.4106 | 519444.8494
4914 | 1196.1437 | 54.5217 | 54.5217 | 53.0747 | 53.0747 | 1409.55 | 79360.9956 | 19106.8891 | 8667.0972 | 2095245.4094 | 30675.0584
4915 | 1400.707 | 0 | 0 | 0 | 0 | 1503.65 | 0 | 0 | 0 | 4759602.2535 | 0
4916 | 823.2952 | 0 | 0 | 0 | 0 | 1690.6 | 0 | 0 | 0 | 2797557.1436 | 0
4917 | 1177.6161 | 0 | 0 | 0 | 0 | 1406.3 | 0 | 0 | 0 | 4001539.3719 | 0
4918 | 1352.3591 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1421.7 | 466815.3091 | 111351.8261 | 50510.4255 | 3544278.6673 | 176886.9342
4919 | 1335.092 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1302 | 829679.1439 | 215514.4963 | 97759.7701 | 2502425.198 | 413216
4920 | 1360.6473 | 0 | 0 | 0 | 0 | 353.45 | 0 | 0 | 0 | 2494066.4917 | 0
4921 | 1288.1255 | 0 | 0 | 0 | 0 | 324.9 | 0 | 0 | 0 | 1532869.3272 | 0
4922 | 1518.8139 | 0 | 0 | 0 | 0 | 304.95 | 0 | 0 | 0 | 1807388.5517 | 0
4923 | 1469.7754 | 0 | 0 | 0 | 0 | 295.45 | 0 | 0 | 0 | 1749032.6689 | 0
4924 | 1038.0979 | 0 | 0 | 0 | 0 | 288.55 | 0 | 0 | 0 | 1235336.5141 | 0
4925 | 1302.6298 | 0 | 0 | 0 | 0 | 283.85 | 0 | 0 | 0 | 1550129.5179 | 0
4926 | 1125.8148 | 0 | 0 | 0 | 0 | 478.9 | 0 | 0 | 0 | 1339719.5727 | 0
4927 | 1215.6037 | 4.0804 | 4.0804 | 3.9721 | 3.9721 | 888.05 | 3736.9414 | 1429.9678 | 648.6493 | 2220920.615 | 4323.2616
4928 | 1164.5561 | 51.0676 | 51.0676 | 49.7123 | 49.7123 | 318.75 | 16814.2193 | 17896.4403 | 8118.0242 | 2043508.6046 | 81811.3062
4929 | 1265.2017 | 605.2274 | 605.2274 | 589.165 | 589.165 | 368.25 | 230503.7699 | 212099.3924 | 96210.641 | 1239175.2842 | 941033.4885
4930 | 1521.9772 | 1581.0369 | 1581.0369 | 1539.0771 | 1521.9772 | 387.2 | 625294.9984 | 547911.8068 | 248538.8835 | 0 | 2454644.5056
4931 | 1459.9884 | 2846.7478 | 1516.6435 | 2771.1967 | 1459.9884 | 392.45 | 607469.8723 | 525595.81 | 238416.0994 | 0 | 2347004.2897
4932 | 1450.6684 | 3524.8567 | 1506.9618 | 3431.3089 | 1450.6684 | 386 | 594189.2368 | 522240.6402 | 236894.1571 | 0 | 2341378.8702
4933 | 1401.7369 | 3302.7498 | 1456.1311 | 3215.0967 | 1401.7369 | 390.75 | 581463.8791 | 504625.2998 | 228903.643 | 0 | 2255745.1771
4934 | 1375.3968 | 3754.4315 | 1428.7679 | 3654.7909 | 1375.3968 | 422.4 | 617787.3466 | 495142.8656 | 224602.3054 | 0 | 2169826.069
4935 | 1381.8306 | 3193.9922 | 1435.4526 | 3109.2254 | 1381.8306 | 435.75 | 641462.2615 | 497459.0052 | 225652.9321 | 0 | 2161528.4691
4936 | 1788.7211 | 1966.0502 | 1858.1319 | 1913.8723 | 1788.7211 | 429.45 | 816725.3142 | 643939.5935 | 292098.1545 | 0 | 2809275.9126
4937 | 1525.3581 | 1345.329 | 1345.329 | 1309.6247 | 1309.6247 | 655.9 | 912571.4346 | 471464.8999 | 213861.7171 | 395439.3537 | 1723030.0161
4938 | 1702.6602 | 336.6839 | 336.6839 | 327.7485 | 327.7485 | 366.05 | 127144.9481 | 117989.4541 | 53521.3274 | 2520213.0862 | 524197.3032
4939 | 1469.7754 | 0 | 0 | 0 | 0 | 1378.7 | 0 | 0 | 0 | 4994296.6461 | 0
4940 | 1623.7979 | 0 | 0 | 0 | 0 | 1522.6 | 0 | 0 | 0 | 5517665.1385 | 0
4941 | 1571.3059 | 0 | 0 | 0 | 0 | 1291.3 | 0 | 0 | 0 | 5339297.4006 | 0
4942 | 1333.0199 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1307.2 | 428451.2579 | 111351.8261 | 50510.4255 | 3478564.2356 | 211909.5072
4943 | 1336.4734 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1302 | 827727.0745 | 215514.4963 | 97759.7701 | 2507119.0864 | 413216
4944 | 1509.1443 | 0 | 0 | 0 | 0 | 817.95 | 0 | 0 | 0 | 2766261.5642 | 0
4945 | 1440.7666 | 0 | 0 | 0 | 0 | 324.9 | 0 | 0 | 0 | 1714512.2873 | 0
4946 | 1415.902 | 0 | 0 | 0 | 0 | 304.95 | 0 | 0 | 0 | 1684923.3883 | 0
4947 | 1212.8409 | 0 | 0 | 0 | 0 | 295.45 | 0 | 0 | 0 | 1443280.7174 | 0
4948 | 1147.9167 | 0 | 0 | 0 | 0 | 288.55 | 0 | 0 | 0 | 1366020.8159 | 0
4949 | 1229.4174 | 0 | 0 | 0 | 0 | 283.85 | 0 | 0 | 0 | 1463006.6501 | 0
4950 | 988.3687 | 0 | 0 | 0 | 0 | 282.35 | 0 | 0 | 0 | 1176158.7166 | 0
4951 | 1297.7951 | 323.3238 | 323.3238 | 314.743 | 314.743 | 289.05 | 96287.2258 | 113307.4745 | 51397.5294 | 1801934.4522 | 527119.7417
4952 | 1047.8219 | 1088.4825 | 1088.4825 | 1059.5947 | 1047.8219 | 318.75 | 353991.5106 | 377215.8757 | 171109.3125 | 0 | 1761650.5307
4953 | 1384.7712 | 1866.7134 | 1438.5067 | 1817.1719 | 1384.7712 | 844.3 | 1237952.0606 | 498517.6165 | 226133.1299 | 0 | 1600380.0261
4954 | 1349.7673 | 3160.9114 | 1402.1444 | 3077.0226 | 1349.7673 | 387.2 | 553453.5149 | 485916.2266 | 220416.9994 | 0 | 2176904.695
4955 | 1301.2096 | 3776.2609 | 1351.7031 | 3676.041 | 1301.2096 | 392.45 | 540343.728 | 468435.4661 | 212487.5323 | 0 | 2091759.5375
4956 | 1364.7042 | 4047.3526 | 1417.661 | 3939.9381 | 1364.7042 | 386 | 558167.9105 | 491293.5116 | 222856.1957 | 0 | 2202632.5772
4957 | 1493.1455 | 4050.1377 | 1551.0861 | 3942.6492 | 1493.1455 | 390.75 | 620240.0491 | 537532.3818 | 243830.661 | 0 | 2402844.4039
4958 | 1284.4951 | 3717.8479 | 1334.3395 | 3619.1783 | 1284.4951 | 422.4 | 576697.0788 | 462418.2277 | 209758.0461 | 0 | 2026419.4335
4959 | 1168.1969 | 3174.606 | 1213.5286 | 3090.3537 | 1168.1969 | 435.75 | 540261.0035 | 420550.8689 | 190766.5469 | 0 | 1827351.9351
4960 | 1479.6564 | 2382.7324 | 1537.0737 | 2319.496 | 1479.6564 | 885.5 | 1391651.4438 | 532676.3213 | 241627.898 | 0 | 1649077.1113
4961 | 1510.8356 | 837.0024 | 837.0024 | 814.7888 | 814.7888 | 1450.45 | 1250825.1501 | 293323.9665 | 133055.0103 | 1275853.8783 | 438295.2511
4962 | 1394.1765 | 354.5389 | 354.5389 | 345.1296 | 345.1296 | 830.55 | 303213.274 | 124246.6554 | 56359.6634 | 1922903.0532 | 395072.9546
4963 | 1384.1314 | 0 | 0 | 0 | 0 | 352.7 | 0 | 0 | 0 | 4703278.5346 | 0
4964 | 1029.119 | 0 | 0 | 0 | 0 | 1288.7 | 0 | 0 | 0 | 3496946.43 | 0
4965 | 1141.7005 | 0 | 0 | 0 | 0 | 1176.3 | 0 | 0 | 0 | 3879498.2854 | 0
4966 | 1211.4596 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1307.2 | 427565.9556 | 111351.8261 | 50510.4255 | 3065502.1085 | 211909.5072
4967 | 1361.338 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1285.1 | 814060.5285 | 215514.4963 | 97759.7701 | 2591609.0686 | 423220.8
4968 | 1071.2507 | 0 | 0 | 0 | 0 | 353.45 | 0 | 0 | 0 | 1963602.6028 | 0
4969 | 1274.3118 | 0 | 0 | 0 | 0 | 824.55 | 0 | 0 | 0 | 2335813.5404 | 0
4970 | 875.7872 | 0 | 0 | 0 | 0 | 304.95 | 0 | 0 | 0 | 1605317.9242 | 0
4971 | 1036.7165 | 0 | 0 | 0 | 0 | 295.45 | 0 | 0 | 0 | 1900301.4233 | 0
4972 | 911.7028 | 0 | 0 | 0 | 0 | 288.55 | 0 | 0 | 0 | 1671151.1514 | 0
4973 | 1306.0833 | 0 | 0 | 0 | 0 | 283.85 | 0 | 0 | 0 | 2394050.6266 | 0
4974 | 1031.1911 | 0 | 0 | 0 | 0 | 282.35 | 0 | 0 | 0 | 1890173.235 | 0
4975 | 1167.9465 | 125.3297 | 125.3297 | 122.0035 | 122.0035 | 289.05 | 37338.7783 | 43921.2719 | 19923.1769 | 1917213.4311 | 204326.7818
4976 | 1102.0699 | 466.8337 | 466.8337 | 454.4441 | 454.4441 | 318.75 | 153682.6067 | 163599.8937 | 74210.7295 | 1187098.0327 | 747872.1188
4977 | 1017.1236 | 1056.5922 | 1056.5922 | 1028.5508 | 1017.1236 | 1307.25 | 1407956.6426 | 366164.4841 | 166096.2785 | 0 | 704612.351
4978 | 1192.6799 | 1238.9616 | 1238.9616 | 1206.0803 | 1192.6799 | 1316.2 | 1662665.7953 | 429364.7554 | 194764.6238 | 0 | 815553.9002
4979 | 1048.5359 | 2385.5912 | 1089.2231 | 2322.2789 | 1048.5359 | 1308 | 1451814.9074 | 377472.9136 | 171225.9077 | 0 | 725586.8227
4980 | 1037.4685 | 3242.8357 | 1077.7277 | 3156.7727 | 1037.4685 | 735.5 | 807605.9166 | 373488.669 | 169418.6101 | 0 | 1311878.9499
4981 | 1077.8269 | 3109.3151 | 1119.6518 | 3026.7955 | 1077.8269 | 390.75 | 444843.3132 | 388017.6883 | 176009.1347 | 0 | 1734492.9581
4982 | 1076.3005 | 3114.3418 | 1118.0656 | 3031.6889 | 1076.3005 | 881.9 | 1005617.1519 | 387468.1804 | 175759.8718 | 0 | 1203411.5902
4983 | 852.6441 | 1217.7815 | 885.7306 | 1185.4622 | 852.6441 | 1356.3 | 1228202.1324 | 306951.8766 | 139236.7818 | 0 | 548847.0083
4984 | 422.9472 | 1354.7437 | 439.3594 | 1318.7895 | 422.9472 | 1273.45 | 572049.8414 | 152260.9908 | 69067.2772 | 0 | 307292.2857
4985 | 167.4831 | 387.8751 | 173.9821 | 377.5812 | 167.4831 | 1791.4 | 317953.4193 | 60293.9077 | 27349.9865 | 0 | 34936.9699
4986 | 147.3263 | 283.1979 | 153.0429 | 275.682 | 147.3263 | 1673.15 | 260760.2218 | 53037.479 | 24058.3898 | 0 | 48153.6112
4987 | 102.2212 | 106.1877 | 106.1877 | 103.3695 | 102.2212 | 1659.8 | 179345.4566 | 36799.6385 | 16692.7249 | 0 | 34775.5842
4988 | 109.8187 | 114.0805 | 114.0805 | 111.0529 | 109.8187 | 1773.7 | 205720.6965 | 39534.7468 | 17933.4004 | 0 | 24851.9811
4989 | 87.0262 | 90.403 | 90.403 | 88.0038 | 87.0262 | 1747.3 | 160591.5398 | 31329.422 | 14211.3739 | 0 | 21991.4702
4990 | 81.5007 | 84.6636 | 84.6636 | 82.4167 | 81.5007 | 1872.2 | 161427.05 | 29340.2523 | 13309.0645 | 0 | 10415.7896
4991 | 81.5007 | 84.6636 | 84.6636 | 82.4167 | 81.5007 | 1849.5 | 159840.3825 | 29340.2523 | 13309.0645 | 0 | 12265.8555
4992 | 85.6448 | 88.9684 | 88.9684 | 86.6073 | 85.6448 | 1751.75 | 159032.6024 | 30832.1296 | 13985.7965 | 0 | 21261.3227
4993 | 80.1193 | 0 | 0 | 0 | 0 | 1544.25 | 0 | 0 | 0 | 95342.0064 | 0
4994 | 78.738 | 38.7287 | 38.7287 | 37.7009 | 37.7009 | 1279.4 | 51061.2943 | 13572.3166 | 6156.5536 | 48834.132 | 26865.4092
4995 | 73.9032 | 76.7708 | 76.7708 | 74.7333 | 73.9032 | 1238.2 | 97005.2061 | 26605.1441 | 12068.389 | 0 | 56299.3054
4996 | 80.81 | 83.9458 | 83.9458 | 81.7179 | 80.81 | 1224.25 | 104896.884 | 29091.6061 | 13196.2758 | 0 | 62688.3575
4997 | 77.3566 | 80.3588 | 80.3588 | 78.2261 | 77.3566 | 1201.55 | 98675.9663 | 27848.3751 | 12632.3324 | 0 | 61765.3752
4998 | 80.81 | 83.9458 | 83.9458 | 81.7179 | 80.81 | 635.8 | 54542.7927 | 29091.6061 | 13196.2758 | 0 | 110241.002
4999 | 70.4498 | 73.1838 | 73.1838 | 71.2415 | 70.4498 | 638.9 | 47823.4386 | 25361.913 | 11504.4455 | 0 | 95889.1662
5000 | 82.0705 | 85.2547 | 85.2547 | 82.9921 | 82.0705 | 1235.2 | 107550.4115 | 29545.3854 | 13402.1151 | 0 | 62767.53
5001 | 531.2024 | 1102.9011 | 551.8152 | 1073.6307 | 531.2024 | 1350.1 | 758570.2943 | 191232.8647 | 86745.3522 | 0 | 345228.4411
5002 | 1284.5469 | 2257.4443 | 1334.3925 | 2197.5329 | 1284.5469 | 1311.95 | 1783474.9473 | 462436.8764 | 209766.5053 | 0 | 883832.4801
5003 | 1356.1138 | 1618.4609 | 1408.7377 | 1575.5078 | 1356.1138 | 1311.75 | 1882029.6786 | 488200.9745 | 221453.3865 | 0 | 933345.3352
5004 | 1186.715 | 2727.1409 | 1232.7652 | 2654.764 | 1186.715 | 1189.55 | 1496940.7746 | 427217.3845 | 193790.5525 | 0 | 961773.1369
5005 | 1505.9819 | 2016.1652 | 1564.4213 | 1962.6573 | 1505.9819 | 1197.5 | 1914569.9829 | 542153.4718 | 245926.8387 | 0 | 1208550.4475
5006 | 1112.084 | 500.4608 | 500.4608 | 487.1789 | 487.1789 | 1435.35 | 744836.6729 | 175384.3865 | 79556.3064 | 1145451.0843 | 269266.3395
5007 | 1330.2779 | 322.632 | 322.632 | 314.0695 | 314.0695 | 1547.9 | 517982.5672 | 113065.0207 | 51287.5497 | 1862710.0359 | 138987.2946
5008 | 1190.5629 | 1000.6193 | 1000.6193 | 974.0634 | 974.0634 | 1773.45 | 1837206.711 | 350662.836 | 159064.5586 | 396843.5758 | 216006.1365
5009 | 1041.9355 | 370.8793 | 370.8793 | 361.0363 | 361.0363 | 1870.5 | 715263.609 | 129973.0794 | 58957.233 | 1248088.2175 | 45765.1705
5010 | 1168.6743 | 189.5258 | 189.5258 | 184.4959 | 184.4959 | 1681.45 | 328172.1455 | 66418.5098 | 30128.174 | 1803999.0668 | 57527.9002
5011 | 1443.5337 | 0 | 0 | 0 | 0 | 1656.25 | 0 | 0 | 0 | 4905127.4446 | 0
5012 | 1038.0979 | 0 | 0 | 0 | 0 | 1728.75 | 0 | 0 | 0 | 3527456.7016 | 0
5013 | 1286.7441 | 0 | 0 | 0 | 0 | 1806.15 | 0 | 0 | 0 | 4372356.5096 | 0
5014 | 712.7858 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1900 | 619187.681 | 111351.8261 | 50510.4255 | 1371008.6037 | 30587.4
5015 | 1145.8446 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1897 | 1199153.4062 | 215514.4963 | 97759.7701 | 1859362.5667 | 60976
5016 | 1181.7602 | 0 | 0 | 0 | 0 | 1814.35 | 0 | 0 | 0 | 2166166.3788 | 0
5017 | 911.7028 | 0 | 0 | 0 | 0 | 1564.05 | 0 | 0 | 0 | 1084926.2794 | 0
5018 | 1009.0892 | 0 | 0 | 0 | 0 | 1622.2 | 0 | 0 | 0 | 1200816.1325 | 0
5019 | 973.8643 | 0 | 0 | 0 | 0 | 1607.4 | 0 | 0 | 0 | 1158898.5258 | 0
5020 | 848.1598 | 0 | 0 | 0 | 0 | 1597.05 | 0 | 0 | 0 | 1009310.2054 | 0
5021 | 780.4728 | 0 | 0 | 0 | 0 | 1543.25 | 0 | 0 | 0 | 928762.6483 | 0
5022 | 770.8032 | 0 | 0 | 0 | 0 | 1487.05 | 0 | 0 | 0 | 917255.8544 | 0
5023 | 969.0295 | 183.2753 | 183.2753 | 178.4113 | 178.4113 | 1230.6 | 233748.9196 | 64228.0525 | 29134.5582 | 1449203.2764 | 134365.7078
5024 | 708.5433 | 707.7938 | 707.7938 | 689.0093 | 689.0093 | 285.05 | 208222.9354 | 248043.3515 | 112515.2203 | 35805.7401 | 1156620.5883
5025 | 1101.8299 | 1396.4673 | 1144.5862 | 1359.4058 | 1101.8299 | 302.05 | 351785.3371 | 396658.7658 | 179928.8235 | 0 | 1870852.0872
5026 | 952.1242 | 2151.8934 | 989.0709 | 2094.7833 | 952.1242 | 312.45 | 313632.664 | 342764.7005 | 155481.8767 | 0 | 1606757.1399
5027 | 1203.6531 | 3182.4833 | 1250.3605 | 3098.0219 | 1203.6531 | 324.8 | 411364.9613 | 433315.1218 | 196556.5538 | 0 | 2016359.6999
5028 | 1159.54 | 3275.9061 | 1204.5357 | 3188.9653 | 1159.54 | 327.55 | 400104.9133 | 417434.3993 | 189352.8817 | 0 | 1939272.6697
5029 | 964.4063 | 2967.8704 | 1001.8306 | 2889.1047 | 964.4063 | 331.8 | 337709.9612 | 347186.2517 | 157487.5414 | 0 | 1608822.5139
5030 | 1140.2509 | 1184.4971 | 1184.4971 | 1153.0612 | 1140.2509 | 342.7 | 412667.2732 | 410490.3326 | 186202.9759 | 0 | 1889737.8563
5031 | 833.8618 | 2160.7783 | 866.2188 | 2103.4324 | 833.8618 | 342.4 | 301467.6464 | 300190.2539 | 136169.6346 | 0 | 1382209.3467
5032 | 1036.9885 | 2496.7194 | 1077.2291 | 2430.4579 | 1036.9885 | 327.9 | 359289.8157 | 373315.86 | 169340.2221 | 0 | 1733948.4708
5033 | 1019.831 | 1051.3556 | 1051.3556 | 1023.4532 | 1019.831 | 318.5 | 345691.4787 | 367139.1773 | 166538.4101 | 0 | 1684533.426
5034 | 933.7278 | 340.4693 | 340.4693 | 331.4334 | 331.4334 | 310.55 | 109151.2239 | 119316.0332 | 54123.0784 | 1104005.5923 | 548094.7479
5035 | 870.2617 | 0 | 0 | 0 | 0 | 1238.6 | 0 | 0 | 0 | 2957149.3297 | 0
5036 | 1061.5812 | 0 | 0 | 0 | 0 | 1562.3 | 0 | 0 | 0 | 3607252.7919 | 0
5037 | 730.0529 | 0 | 0 | 0 | 0 | 1611 | 0 | 0 | 0 | 2480719.7155 | 0
5038 | 1020.8308 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1661.15 | 543811.9222 | 111351.8261 | 50510.4255 | 2417745.5888 | 103645.4049
5039 | 954.5252 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1646.45 | 1042448.6055 | 215514.4963 | 97759.7701 | 1209259.1028 | 209301.6
5040 | 756.9896 | 0 | 0 | 0 | 0 | 1596.2 | 0 | 0 | 0 | 1387561.8651 | 0
5041 | 995.2755 | 0 | 0 | 0 | 0 | 1330.5 | 0 | 0 | 0 | 1184377.855 | 0
5042 | 975.9364 | 0 | 0 | 0 | 0 | 1225.5 | 0 | 0 | 0 | 1161364.2673 | 0
5043 | 974.555 | 0 | 0 | 0 | 0 | 841.5 | 0 | 0 | 0 | 1159720.4396 | 0
5044 | 919.3003 | 0 | 0 | 0 | 0 | 288.55 | 0 | 0 | 0 | 1093967.3318 | 0
5045 | 1018.0681 | 0 | 0 | 0 | 0 | 283.85 | 0 | 0 | 0 | 1211501.0116 | 0
5046 | 664.4379 | 0 | 0 | 0 | 0 | 282.35 | 0 | 0 | 0 | 790681.1218 | 0
5047 | 891.6729 | 234.3003 | 234.3003 | 228.0821 | 228.0821 | 485.6 | 117632.5471 | 82109.5669 | 37245.8119 | 1216361.9224 | 338101.9152
5048 | 882.8417 | 882.3389 | 882.3389 | 858.9221 | 858.9221 | 774.8 | 705517.2516 | 309211.9718 | 140261.9861 | 43844.4831 | 1030090.5756
5049 | 1164.6709 | 1913.6643 | 1209.8647 | 1862.8767 | 1164.6709 | 1479.3 | 1821029.5437 | 419281.5301 | 190190.7607 | 0 | 606444.1465
5050 | 1275.9643 | 2919.7612 | 1325.4785 | 2842.2724 | 1275.9643 | 1498.75 | 2027455.3564 | 459347.1365 | 208364.965 | 0 | 639577.0893
5051 | 1281.6469 | 1975.039 | 1331.38 | 1922.6225 | 1281.6469 | 1313 | 1784879.0422 | 461392.8732 | 209292.9339 | 0 | 880491.3997
5052 | 1165.2105 | 4149.2739 | 1210.4257 | 4039.1544 | 1165.2105 | 386 | 476524.1233 | 419475.7847 | 190278.8768 | 0 | 1880649.768
5053 | 1262.2861 | 2157.5985 | 1311.2687 | 2100.337 | 1262.2861 | 390.75 | 521206.7857 | 454423.009 | 206131.326 | 0 | 2031333.9644
5054 | 1118.1698 | 2554.2505 | 1161.5603 | 2486.4621 | 1118.1698 | 422.4 | 500907.4484 | 402541.1132 | 182597.1216 | 0 | 1764024.6118
5055 | 1150.1519 | 2632.085 | 1194.7834 | 2562.2309 | 1150.1519 | 1399.9 | 1707561.9733 | 414054.6757 | 187819.8015 | 0 | 690206.1414
5056 | 1238.5577 | 1683.2366 | 1286.6199 | 1638.5644 | 1238.5577 | 1718.45 | 2250098.5257 | 445880.7688 | 202256.4709 | 0 | 348715.9179
5057 | 954.5088 | 564.0949 | 564.0949 | 549.1241 | 549.1241 | 1700.4 | 987842.8938 | 197684.6762 | 89671.9656 | 743070.0704 | 161037.3968
5058 | 1051.3962 | 159.5178 | 159.5178 | 155.2843 | 155.2843 | 1687.05 | 276824.1474 | 55902.3489 | 25357.9266 | 1642573.046 | 47568.4
5059 | 866.1271 | 0 | 0 | 0 | 0 | 1839.2 | 0 | 0 | 0 | 2943099.9364 | 0
5060 | 1031.8818 | 0 | 0 | 0 | 0 | 1868.7 | 0 | 0 | 0 | 3506334.2035 | 0
5061 | 910.3214 | 0 | 0 | 0 | 0 | 1760.6 | 0 | 0 | 0 | 3093272.0764 | 0
5062 | 1085.7551 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1699.2 | 556440.9754 | 111351.8261 | 50510.4255 | 2638358.3161 | 92006.8992
5063 | 1110.6197 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1694 | 1075660.6198 | 215514.4963 | 97759.7701 | 1739668.4279 | 181152
5064 | 991.1314 | 0 | 0 | 0 | 0 | 1559.45 | 0 | 0 | 0 | 1816743.8654 | 0
5065 | 1030.5004 | 0 | 0 | 0 | 0 | 780.95 | 0 | 0 | 0 | 1226295.4617 | 0
5066 | 809.4815 | 0 | 0 | 0 | 0 | 1003.95 | 0 | 0 | 0 | 963283.0299 | 0
5067 | 1055.365 | 0 | 0 | 0 | 0 | 1044.45 | 0 | 0 | 0 | 1255884.3595 | 0
5068 | 926.8978 | 0 | 0 | 0 | 0 | 1200.65 | 0 | 0 | 0 | 1103008.3841 | 0
5069 | 813.6256 | 0 | 0 | 0 | 0 | 1195.95 | 0 | 0 | 0 | 968214.513 | 0
5070 | 907.5587 | 0 | 0 | 0 | 0 | 1194.45 | 0 | 0 | 0 | 1079994.7964 | 0
5071 | 821.2232 | 319.6226 | 319.6226 | 311.14 | 311.14 | 938.05 | 310126.7472 | 112010.383 | 50809.1543 | 934982.5262 | 323425.3681
5072 | 962.443 | 999.7904 | 999.7904 | 973.2565 | 962.443 | 318.75 | 325655.8805 | 346479.4748 | 157166.9395 | 0 | 1618107.2695
5073 | 1008.2725 | 1865.1282 | 1047.3977 | 1815.6287 | 1008.2725 | 1288.8 | 1375861.6058 | 362978.0831 | 164650.8916 | 0 | 717083.3686
5074 | 1436.7719 | 3039.3194 | 1492.5256 | 2958.6575 | 1436.7719 | 387.2 | 588740.4206 | 517237.8786 | 234624.8488 | 0 | 2317225.6961
5075 | 1155.7145 | 3843.1891 | 1200.5612 | 3741.1929 | 1155.7145 | 392.45 | 479444.2637 | 416057.2103 | 188728.1734 | 0 | 1857868.8011
5076 | 1137.1705 | 916.0128 | 916.0128 | 891.7024 | 891.7024 | 386 | 364965.4812 | 321012.8467 | 145614.9941 | 449943.0661 | 1418467.128
5077 | 1170.2102 | 1215.6197 | 1215.6197 | 1183.3578 | 1170.2102 | 390.75 | 483945.3646 | 421275.6724 | 191095.3258 | 0 | 1883160.766
5078 | 1059.333 | 2919.3779 | 1100.4402 | 2841.8992 | 1059.333 | 422.4 | 474211.4884 | 381359.8753 | 172989.0768 | 0 | 1671203.7203
5079 | 1086.2248 | 2471.0225 | 1128.3746 | 2405.4429 | 1086.2248 | 891.8 | 1027164.1293 | 391040.9154 | 177380.5041 | 0 | 1203754.2846
5080 | 1050.3472 | 273.0966 | 273.0966 | 265.8487 | 265.8487 | 1388.45 | 390796.3362 | 95705.5464 | 43413.0993 | 1437985.6586 | 159140.5988
5081 | 1100.0177 | 499.6152 | 499.6152 | 486.3557 | 486.3557 | 1731.4 | 891358.9309 | 175088.0541 | 79421.8867 | 1124842.4777 | 127871.5962
5082 | 961.4501 | 269.8908 | 269.8908 | 262.7281 | 262.7281 | 1828.05 | 507131.4007 | 94582.1043 | 42903.4934 | 1280757.5359 | 44220.5535
5083 | 1004.2544 | 0 | 0 | 0 | 0 | 1841.7 | 0 | 0 | 0 | 3412456.4478 | 0
5084 | 918.6096 | 0 | 0 | 0 | 0 | 1866.2 | 0 | 0 | 0 | 3121435.4035 | 0
5085 | 1251.5192 | 0 | 0 | 0 | 0 | 1828.8 | 0 | 0 | 0 | 4252662.3707 | 0
5086 | 1076.0855 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1772.2 | 581681.629 | 111351.8261 | 50510.4255 | 2605501.1002 | 69678.0972
5087 | 1287.4348 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1698 | 1080692.1537 | 215514.4963 | 97759.7701 | 2340486.0697 | 178784
5088 | 1154.1328 | 0 | 0 | 0 | 0 | 1419.35 | 0 | 0 | 0 | 2115525.4352 | 0
5089 | 1704.5439 | 0 | 0 | 0 | 0 | 324.9 | 0 | 0 | 0 | 2028407.2636 | 0
5090 | 1118.0342 | 0 | 0 | 0 | 0 | 304.95 | 0 | 0 | 0 | 1330460.6778 | 0
5091 | 1386.5855 | 0 | 0 | 0 | 0 | 295.45 | 0 | 0 | 0 | 1650036.764 | 0
5092 | 1257.4896 | 0 | 0 | 0 | 0 | 288.55 | 0 | 0 | 0 | 1496412.6514 | 0
5093 | 1113.2529 | 0 | 0 | 0 | 0 | 283.85 | 0 | 0 | 0 | 1324770.8963 | 0
5094 | 1508.5094 | 0 | 0 | 0 | 0 | 282.35 | 0 | 0 | 0 | 1795126.2038 | 0
5095 | 1345.1473 | 156.7089 | 156.7089 | 152.5499 | 152.5499 | 289.05 | 46700.8106 | 54917.9718 | 24911.4022 | 2186031.0456 | 255484.1868
5096 | 1347.8468 | 942.3663 | 942.3663 | 917.3564 | 917.3564 | 318.75 | 309884.307 | 330248.2981 | 149804.2974 | 789088.9094 | 1509680.1187
5097 | 1439.8057 | 1495.6773 | 1495.6773 | 1455.9828 | 1439.8057 | 368.25 | 562443.4173 | 518330.0506 | 235120.2702 | 0 | 2349401.8087
5098 | 1331.5524 | 1682.0191 | 1383.2225 | 1637.3793 | 1331.5524 | 387.2 | 546185.5122 | 479358.8694 | 217442.5094 | 0 | 2147527.7349
5099 | 1361.5313 | 2406.0089 | 1414.3649 | 2342.1548 | 1361.5313 | 392.45 | 565108.4209 | 490151.286 | 222338.0695 | 0 | 2188729.7217
5100 | 1417.9132 | 3313.7092 | 1472.9358 | 3225.7652 | 1417.9132 | 386 | 579542.6323 | 510448.7462 | 231545.2229 | 0 | 2288511.879
5101 | 1620.5808 | 3449.4945 | 1683.4672 | 3357.9468 | 1620.5808 | 390.75 | 670863.2026 | 583409.0833 | 264640.8425 | 0 | 2607919.6315
5102 | 1546.263 | 3105.3759 | 1606.2653 | 3022.9609 | 1546.263 | 422.4 | 693515.0533 | 556654.6768 | 252504.7464 | 0 | 2439384.4946
5103 | 1367.5967 | 2506.3595 | 1420.6663 | 2439.8421 | 1367.5967 | 435.75 | 631196.8142 | 492334.7998 | 223328.5356 | 0 | 2139263.0848
5104 | 1582.1499 | 1542.3944 | 1542.3944 | 1501.4601 | 1501.4601 | 429.45 | 682644.3836 | 540525.6465 | 245188.4391 | 147904.2694 | 2308237.335
5105 | 1603.4885 | 587.4732 | 587.4732 | 571.882 | 571.882 | 1535.4 | 929322.129 | 205877.5034 | 93388.3231 | 1890934.8538 | 260076.111
5106 | 1628.2678 | 249.8253 | 249.8253 | 243.195 | 243.195 | 1695.05 | 436999.3744 | 87550.2158 | 39713.7507 | 2538838.307 | 72593.3475
5107 | 1753.1561 | 0 | 0 | 0 | 0 | 1824.2 | 0 | 0 | 0 | 5957224.404 | 0
5108 | 1494.1654 | 0 | 0 | 0 | 0 | 1848.7 | 0 | 0 | 0 | 5077174.1209 | 0
5109 | 1494.1654 | 0 | 0 | 0 | 0 | 1756.3 | 0 | 0 | 0 | 5077174.1209 | 0
5110 | 1460.6961 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1839.7 | 602796.1321 | 111351.8261 | 50510.4255 | 3912407.9054 | 49031.6022
5111 | 1675.8559 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1770 | 1123377.5351 | 215514.4963 | 97759.7701 | 3660341.1069 | 136160
5112 | 1392.1637 | 0 | 0 | 0 | 0 | 1371.5 | 0 | 0 | 0 | 2551836.1226 | 0
5113 | 1467.0712 | 0 | 0 | 0 | 0 | 1228.85 | 0 | 0 | 0 | 1745814.7601 | 0
5114 | 1345.1473 | 0 | 0 | 0 | 0 | 852.4 | 0 | 0 | 0 | 1600725.3203 | 0
5115 | 1282.1932 | 0 | 0 | 0 | 0 | 296.55 | 0 | 0 | 0 | 1525809.858 | 0
5116 | 1174.6132 | 0 | 0 | 0 | 0 | 289.2 | 0 | 0 | 0 | 1397789.7639 | 0
5117 | 1106.8777 | 0 | 0 | 0 | 0 | 283.7 | 0 | 0 | 0 | 1317184.5201 | 0
5118 | 1184.9728 | 0 | 0 | 0 | 0 | 280.8 | 0 | 0 | 0 | 1410117.6249 | 0
5119 | 1051.8925 | 301.0581 | 301.0581 | 293.0682 | 293.0682 | 283.6 | 88241.4076 | 105504.5392 | 47858.0312 | 1390924.9339 | 492381.9516
5120 | 1003.1398 | 1042.0666 | 1042.0666 | 1014.4107 | 1003.1398 | 298.65 | 317728.7998 | 361130.3406 | 163812.7351 | 0 | 1706691.9583
5121 | 1520.4757 | 1248.5218 | 1248.5218 | 1215.3867 | 1215.3867 | 919.35 | 1184484.7232 | 437539.2049 | 198472.6449 | 559228.1512 | 1275732.18
5122 | 1744.6384 | 1812.3393 | 1812.3393 | 1764.2408 | 1744.6384 | 836.15 | 1547526.3693 | 628069.8074 | 284899.4432 | 0 | 2030496.9363
5123 | 1595.175 | 2247.8177 | 1657.0754 | 2188.1618 | 1595.175 | 351.95 | 595948.8081 | 574262.9978 | 260492.0765 | 0 | 2628928.1489
5124 | 1462.4025 | 2895.1769 | 1519.1501 | 2818.3405 | 1462.4025 | 359.3 | 558559.5408 | 526464.8849 | 238810.3214 | 0 | 2399363.7128
5125 | 1607.6891 | 3204.7968 | 1670.075 | 3119.7432 | 1607.6891 | 377.2 | 644632.8082 | 578768.0857 | 262535.6344 | 0 | 2608957.9153
5126 | 1637.0923 | 2702.1722 | 1700.62 | 2630.458 | 1637.0923 | 405.85 | 705209.9764 | 589353.232 | 267337.1744 | 0 | 2609770.7076
5127 | 1664.4276 | 1813.2919 | 1729.0157 | 1765.1681 | 1664.4276 | 411.6 | 726320.2982 | 599193.9248 | 271801.022 | 0 | 2643776.7506
5128 | 1619.2759 | 692.033 | 692.033 | 673.6668 | 673.6668 | 865.1 | 618130.925 | 242520.0644 | 110009.7959 | 1733301.3637 | 748371.2184
5129 | 1609.6674 | 732.5786 | 732.5786 | 713.1364 | 713.1364 | 1766.6 | 1334759.4482 | 256729.0953 | 116455.1702 | 1643341.3707 | 162925.1034
5130 | 1842.5401 | 260.9259 | 260.9259 | 254.0011 | 254.0011 | 1809.2 | 485615.3467 | 91440.3981 | 41478.3806 | 2911791.8977 | 47438.2224
5131 | 1522.0625 | 0 | 0 | 0 | 0 | 1837.65 | 0 | 0 | 0 | 5171968.3444 | 0
5132 | 1333.194 | 0 | 0 | 0 | 0 | 1844.9 | 0 | 0 | 0 | 4530193.229 | 0
5133 | 1353.1162 | 0 | 0 | 0 | 0 | 1753.25 | 0 | 0 | 0 | 4597888.8816 | 0
5134 | 1412.8828 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1823.35 | 597304.6043 | 111351.8261 | 50510.4255 | 3749938.3324 | 54032.6421
5135 | 1341.9598 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1719.3 | 1090099.3381 | 215514.4963 | 97759.7701 | 2525761.9314 | 166174.4
5136 | 1469.4619 | 0 | 0 | 0 | 0 | 1523.05 | 0 | 0 | 0 | 2693523.648 | 0
5137 | 1242.3487 | 0 | 0 | 0 | 0 | 1228.85 | 0 | 0 | 0 | 2277225.2533 | 0
5138 | 1430.4144 | 0 | 0 | 0 | 0 | 1198.05 | 0 | 0 | 0 | 2621949.5365 | 0
5139 | 1263.8647 | 0 | 0 | 0 | 0 | 1085.8 | 0 | 0 | 0 | 2316664.0483 | 0
5140 | 1263.8647 | 0 | 0 | 0 | 0 | 964.6 | 0 | 0 | 0 | 2316664.0483 | 0
5141 | 1340.366 | 0 | 0 | 0 | 0 | 959.1 | 0 | 0 | 0 | 2456890.8762 | 0
5142 | 1114.0497 | 0 | 0 | 0 | 0 | 956.2 | 0 | 0 | 0 | 2042053.1771 | 0
5143 | 1307.6936 | 187.2259 | 187.2259 | 182.257 | 182.257 | 770.3 | 149113.6492 | 65612.5147 | 29762.5657 | 2062925.2801 | 219379.7097
5144 | 1075.8529 | 686.7985 | 686.7985 | 668.5712 | 668.5712 | 298.65 | 212011.1458 | 240685.6429 | 109177.6819 | 746547.2951 | 1113412.7792
5145 | 1014.0104 | 1053.3584 | 1053.3584 | 1025.4028 | 1014.0104 | 1036 | 1113887.8894 | 365043.739 | 165587.896 | 0 | 977505.64
5146 | 1160.599 | 1660.1523 | 1205.6358 | 1616.0928 | 1160.599 | 677.85 | 834063.4756 | 417815.6299 | 189525.8121 | 0 | 1534485.9308
5147 | 1335.6922 | 2614.71 | 1387.5242 | 2545.317 | 1335.6922 | 351.95 | 498792.7625 | 480849.2096 | 218118.5443 | 0 | 2201287.611
5148 | 1416.1869 | 3171.2995 | 1471.1418 | 3087.1349 | 1416.1869 | 359.3 | 539827.7074 | 509827.293 | 231263.3249 | 0 | 2323537.8878
5149 | 1072.5339 | 2922.3084 | 1114.1534 | 2844.7519 | 1072.5339 | 377.2 | 430242.0513 | 386112.1889 | 175144.779 | 0 | 1740507.9448
5150 | 1228.6313 | 555.3242 | 555.3242 | 540.5862 | 540.5862 | 405.85 | 233613.8564 | 194611.0463 | 88277.7329 | 1261186.6175 | 843546.0666
5151 | 962.4338 | 199.7632 | 199.7632 | 194.4616 | 194.4616 | 411.6 | 84986.6872 | 70006.1709 | 31755.5769 | 1407693.0466 | 302348.7632
5152 | 1200.7083 | 317.3102 | 317.3102 | 308.8889 | 308.8889 | 738.3 | 241795.5765 | 111200.0194 | 50441.5644 | 1634704.9698 | 381480.0418
5153 | 1232.7184 | 608.8819 | 608.8819 | 592.7225 | 592.7225 | 1633.75 | 1026416.4496 | 213380.1018 | 96791.5851 | 1173112.3873 | 212492.39
5154 | 856.2803 | 176.9053 | 176.9053 | 172.2104 | 172.2104 | 1674.2 | 305586.2635 | 61995.73 | 28121.952 | 1253900.2109 | 54919.4544
5155 | 1170.6288 | 0 | 0 | 0 | 0 | 1675.15 | 0 | 0 | 0 | 2145762.6014 | 0
5156 | 1184.9728 | 0 | 0 | 0 | 0 | 1822.4 | 0 | 0 | 0 | 2172055.1314 | 0
5157 | 1341.1629 | 0 | 0 | 0 | 0 | 1700.3 | 0 | 0 | 0 | 2458351.5719 | 0
5158 | 1157.0817 | 176.1875 | 176.1875 | 171.5116 | 171.5116 | 1798.3 | 327239.4923 | 61744.1751 | 28007.8439 | 1806550.0089 | 34209.5302
5159 | 1082.1742 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1699.3 | 1079137.4746 | 215514.4963 | 97759.7701 | 886297.3557 | 178014.4
5160 | 136.2679 | 141.5558 | 141.5558 | 137.799 | 136.2679 | 1394.6 | 202087.6216 | 49056.4393 | 22252.5459 | 0 | 82496.5787
5161 | 105.9861 | 0 | 0 | 0 | 0 | 1319.6 | 0 | 0 | 0 | 126123.4998 | 0
5162 | 87.6577 | 0 | 0 | 0 | 0 | 1120.65 | 0 | 0 | 0 | 104312.669 | 0
5163 | 91.6421 | 0 | 0 | 0 | 0 | 1223.5 | 0 | 0 | 0 | 109054.1539 | 0
5164 | 87.6577 | 0 | 0 | 0 | 0 | 1183 | 0 | 0 | 0 | 104312.669 | 0
5165 | 91.6421 | 0 | 0 | 0 | 0 | 1173.65 | 0 | 0 | 0 | 109054.1539 | 0
5166 | 84.4702 | 0 | 0 | 0 | 0 | 1164.55 | 0 | 0 | 0 | 100519.481 | 0
5167 | 82.0795 | 85.2641 | 85.2641 | 83.0012 | 82.0795 | 1176.2 | 102306.9909 | 29548.6155 | 13403.5803 | 0 | 67616.6802
5168 | 81.0455 | 546.5671 | 84.191 | 532.0615 | 81.0455 | 817.65 | 70216.3765 | 29176.389 | 13234.7342 | 0 | 95824.1764
5169 | 801.8299 | 1347.444 | 832.9438 | 1311.6836 | 801.8299 | 1029 | 875947.2972 | 288658.775 | 130938.8277 | 0 | 778576.8626
5170 | 967.4233 | 2241.8674 | 1004.9636 | 2182.3694 | 967.4233 | 665.1 | 682523.9511 | 348272.3895 | 157980.2256 | 0 | 1291413.3689
5171 | 1373.2187 | 2494.3125 | 1426.5064 | 2428.1148 | 1373.2187 | 335.3 | 487577.1016 | 494358.7363 | 224246.6157 | 0 | 2285997.1899
5172 | 1296.8011 | 3058.5788 | 1347.123 | 2977.4058 | 1296.8011 | 343.8 | 473584.1258 | 466848.4014 | 211767.6221 | 0 | 2147762.0067
5173 | 1405.7098 | 2793.7563 | 1460.2582 | 2719.6115 | 1405.7098 | 354.95 | 532211.9978 | 506055.5413 | 229552.4164 | 0 | 2312462.9674
5174 | 1424.881 | 2203.6394 | 1480.1731 | 2145.156 | 1424.881 | 371.45 | 562980.5647 | 512957.1514 | 232683.0634 | 0 | 2320489.9135
5175 | 1143.2188 | 3181.0404 | 1187.5813 | 3096.6173 | 1143.2188 | 360.8 | 437902.9282 | 411558.7824 | 186687.6366 | 0 | 1873964.3225
5176 | 1188.5309 | 2391.6454 | 1234.6516 | 2328.1724 | 1188.5309 | 1129.6 | 1424830.0305 | 427871.124 | 194087.096 | 0 | 1034497.2954
5177 | 1249.3245 | 1346.5642 | 1297.8037 | 1310.8271 | 1249.3245 | 1560.15 | 2069439.048 | 449756.8225 | 204014.692 | 0 | 549515.3844
5178 | 1404.2924 | 0 | 0 | 0 | 0 | 1651.65 | 0 | 0 | 0 | 2574067.9179 | 0
5179 | 1160.2693 | 0 | 0 | 0 | 0 | 1648.65 | 0 | 0 | 0 | 3942594.9421 | 0
5180 | 1162.6599 | 0 | 0 | 0 | 0 | 1655.5 | 0 | 0 | 0 | 3950718.4218 | 0
5181 | 1369.8509 | 0 | 0 | 0 | 0 | 1658.05 | 0 | 0 | 0 | 4654753.2325 | 0
5182 | 1357.1007 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1666.9 | 548013.2101 | 111351.8261 | 50510.4255 | 3560390.4984 | 101886.6294
5183 | 1209.6763 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1517.85 | 965245.8072 | 215514.4963 | 97759.7701 | 2076262.7819 | 285432.8
5184 | 945.9063 | 0 | 0 | 0 | 0 | 1502.85 | 0 | 0 | 0 | 1733846.2957 | 0
5185 | 1825.6709 | 0 | 0 | 0 | 0 | 1115.95 | 0 | 0 | 0 | 2172548.4055 | 0
5186 | 1777.8576 | 0 | 0 | 0 | 0 | 1077.2 | 0 | 0 | 0 | 2115650.5868 | 0
5187 | 1880.6562 | 0 | 0 | 0 | 0 | 1163.85 | 0 | 0 | 0 | 2237980.8982 | 0
5188 | 2020.9085 | 0 | 0 | 0 | 0 | 1071.6 | 0 | 0 | 0 | 2404881.1686 | 0
5189 | 2148.4107 | 0 | 0 | 0 | 0 | 1179.3 | 0 | 0 | 0 | 2556608.6866 | 0
5190 | 2121.3165 | 0 | 0 | 0 | 0 | 1198.5 | 0 | 0 | 0 | 2524366.5898 | 0
5191 | 1969.1108 | 322.2009 | 322.2009 | 313.6498 | 313.6498 | 1091.65 | 361617.5111 | 112913.9421 | 51219.0187 | 3034459.9595 | 278877.0752
5192 | 1123.1632 | 1166.7471 | 1166.7471 | 1135.7822 | 1123.1632 | 555.25 | 658807.7568 | 404338.7358 | 183412.5432 | 0 | 1613150.06
5193 | 1632.0301 | 1675.725 | 1675.725 | 1631.2522 | 1631.2522 | 294.25 | 507388.6609 | 587250.7911 | 266383.4838 | 1425.8551 | 2716287.4725
5194 | 1933.3126 | 2008.3347 | 2008.3347 | 1955.0346 | 1933.3126 | 302.75 | 618973.0524 | 695992.5356 | 315709.9474 | 0 | 3281314.8087
5195 | 2180.0402 | 2271.278 | 2264.6359 | 2210.9995 | 2180.0402 | 312.45 | 721125.9285 | 784814.4544 | 356000.5567 | 0 | 3678926.7568
5196 | 2017.7698 | 3301.818 | 2096.0691 | 3214.1896 | 2017.7698 | 313.95 | 672047.2292 | 726397.1284 | 329501.8085 | 0 | 3402060.773
5197 | 1936.1236 | 3328.9911 | 2011.2548 | 3240.6415 | 1936.1236 | 315.8 | 648921.6432 | 697004.5039 | 316168.9875 | 0 | 3260819.4042
5198 | 2326.1845 | 3179.4437 | 2416.452 | 3095.063 | 2326.1845 | 330.6 | 817208.0241 | 837426.4099 | 379865.9243 | 0 | 3883332.3576
5199 | 2160.3092 | 2353.5295 | 2244.1392 | 2291.0682 | 2160.3092 | 342.5 | 785922.8127 | 777711.3116 | 352778.4922 | 0 | 3580712.4973
5200 | 1965.9362 | 259.0156 | 259.0156 | 252.1414 | 252.1414 | 349.25 | 93739.2081 | 90770.9198 | 41174.6978 | 3141385.801 | 407418.306
5201 | 2270.9292 | 373.5874 | 373.5874 | 363.6726 | 363.6726 | 340.55 | 131644.762 | 130922.1441 | 59387.7393 | 3496001.3761 | 590731.011
5202 | 1602.9128 | 92.678 | 92.678 | 90.2184 | 90.2184 | 321.7 | 30877.9268 | 32478.6171 | 14732.6616 | 2772768.8321 | 148210.673
5203 | 2148.4226 | 0 | 0 | 0 | 0 | 1137.1 | 0 | 0 | 0 | 7300340.0458 | 0
5204 | 2164.3484 | 0 | 0 | 0 | 0 | 1358.95 | 0 | 0 | 0 | 7354455.9515 | 0
5205 | 1992.2206 | 0 | 0 | 0 | 0 | 1249.4 | 0 | 0 | 0 | 6769565.4935 | 0
5206 | 1660.7151 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1254.25 | 411964.2302 | 111351.8261 | 50510.4255 | 4592072.2805 | 228105.5355
5207 | 2342.8514 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1246.1 | 791767.5793 | 215514.4963 | 97759.7701 | 5926791.6358 | 446308.8
5208 | 2067.1281 | 0 | 0 | 0 | 0 | 1062.75 | 0 | 0 | 0 | 3789045.7376 | 0
5209 | 1512.4939 | 0 | 0 | 0 | 0 | 1351.75 | 0 | 0 | 0 | 1799867.6886 | 0
5210 | 1488.5872 | 0 | 0 | 0 | 0 | 306.35 | 0 | 0 | 0 | 1771418.7787 | 0
5211 | 1255.099 | 0 | 0 | 0 | 0 | 296.55 | 0 | 0 | 0 | 1493567.76 | 0
5212 | 1229.5985 | 0 | 0 | 0 | 0 | 289.2 | 0 | 0 | 0 | 1463222.2567 | 0
5213 | 1267.0523 | 0 | 0 | 0 | 0 | 283.7 | 0 | 0 | 0 | 1507792.2156 | 0
5214 | 1408.8984 | 0 | 0 | 0 | 0 | 578.8 | 0 | 0 | 0 | 1676589.0793 | 0
5215 | 1368.2571 | 0 | 0 | 0 | 0 | 1061 | 0 | 0 | 0 | 2508015.2405 | 0
5216 | 992.7355 | 38.1813 | 38.1813 | 37.168 | 37.168 | 973.95 | 38260.6485 | 13380.4651 | 6069.5276 | 1751555.2352 | 37328.7251
5217 | 1172.2624 | 502.4293 | 502.4293 | 489.0951 | 489.0951 | 1072.8 | 555888.7324 | 176074.2513 | 79869.2368 | 1252245.6325 | 443897
5218 | 1292.8316 | 1225.4572 | 1225.4572 | 1192.9342 | 1192.9342 | 1113.65 | 1407482.5751 | 429456.3192 | 194806.1581 | 183111.9271 | 1034990.895
5219 | 1352.5624 | 2115.5986 | 1405.0489 | 2059.4518 | 1352.5624 | 989.1 | 1415067.6928 | 486922.4543 | 220873.4355 | 0 | 1367305.3029
5220 | 1429.4651 | 2726.5571 | 1484.9361 | 2654.1957 | 1429.4651 | 359.3 | 544362.7044 | 514607.427 | 233431.6467 | 0 | 2345323.3486
5221 | 1429.4511 | 3434.5794 | 1484.9205 | 3343.4275 | 1429.4511 | 377.2 | 571677.26 | 514602.4068 | 233429.3695 | 0 | 2319713.2938
5222 | 1083.6514 | 2909.5165 | 1125.7018 | 2832.2996 | 1083.6514 | 1195.45 | 1374435.5384 | 390114.5202 | 176960.281 | 0 | 871851.7701
5223 | 1206.68 | 2031.6362 | 1253.5049 | 1977.7176 | 1206.68 | 1302.25 | 1663835.1962 | 434404.8108 | 197050.8489 | 0 | 841960.9909
5224 | 1434.9975 | 763.8227 | 763.8227 | 743.5513 | 743.5513 | 1462.1 | 1151833.7919 | 267678.4695 | 121421.928 | 1267420.8256 | 391495.9917
5225 | 1270.9311 | 692.7664 | 692.7664 | 674.3808 | 674.3808 | 1731.1 | 1236161.3257 | 242777.08 | 110126.381 | 1093476.8046 | 177504.9235
5226 | 1239.3475 | 277.9229 | 277.9229 | 270.5469 | 270.5469 | 1668.75 | 478147.5665 | 97396.8984 | 44180.3153 | 1775811.3643 | 87722.95
5227 | 795.2945 | 0 | 0 | 0 | 0 | 1750.15 | 0 | 0 | 0 | 2702410.5448 | 0
5228 | 1205.6919 | 0 | 0 | 0 | 0 | 1784.9 | 0 | 0 | 0 | 4096941.0354 | 0
5229 | 1452.7272 | 0 | 0 | 0 | 0 | 1780.3 | 0 | 0 | 0 | 4936367.1581 | 0
5230 | 1126.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1878.35 | 614930.7883 | 111351.8261 | 50510.4255 | 2777828.73 | 37209.5721
5231 | 1046.3142 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1879.2 | 1190319.2119 | 215514.4963 | 97759.7701 | 1521158.4136 | 71513.6
5232 | 945.9063 | 0 | 0 | 0 | 0 | 1859.5 | 0 | 0 | 0 | 1733846.2957 | 0
5233 | 1189.7541 | 0 | 0 | 0 | 0 | 1705.1 | 0 | 0 | 0 | 1415807.4076 | 0
5234 | 1080.5804 | 0 | 0 | 0 | 0 | 1495.75 | 0 | 0 | 0 | 1285890.72 | 0
5235 | 1216.8483 | 0 | 0 | 0 | 0 | 1225.55 | 0 | 0 | 0 | 1448049.5044 | 0
5236 | 1073.4084 | 0 | 0 | 0 | 0 | 1205.65 | 0 | 0 | 0 | 1277356.046 | 0
5237 | 1196.1292 | 0 | 0 | 0 | 0 | 1163.2 | 0 | 0 | 0 | 1423393.7825 | 0
5238 | 1135.5657 | 0 | 0 | 0 | 0 | 1196.2 | 0 | 0 | 0 | 1351323.2116 | 0
5239 | 1033.564 | 156.2009 | 156.2009 | 152.0554 | 152.0554 | 1212.6 | 195407.2093 | 54739.954 | 24830.6513 | 1615805.2699 | 117195.8286
5240 | 863.52 | 897.0287 | 897.0287 | 873.222 | 863.52 | 1178.15 | 1079037.6451 | 310867.2132 | 141012.822 | 0 | 709683.912
5241 | 1062.6763 | 1981.2583 | 1103.9139 | 1928.6768 | 1062.6763 | 1252.8 | 1412229.1799 | 382563.486 | 173535.048 | 0 | 794031.7687
5242 | 1360.7414 | 3280.8976 | 1413.5442 | 3193.8243 | 1360.7414 | 1256.6 | 1813376.1163 | 489866.9166 | 222209.0763 | 0 | 1011575.1828
5243 | 1568.4882 | 3818.5694 | 1629.3528 | 3717.2266 | 1568.4882 | 1280.95 | 2126857.6075 | 564655.7531 | 256134.1235 | 0 | 1127821.4424
5244 | 1509.8552 | 3242.4098 | 1568.4445 | 3156.358 | 1509.8552 | 1249.95 | 2002825.0937 | 543547.8576 | 246559.3476 | 0 | 1132466.8628
5245 | 1563.935 | 2840.0984 | 1624.6231 | 2764.7238 | 1563.935 | 1089.35 | 1810856.2612 | 563016.5939 | 255390.5827 | 0 | 1424197.3923
5246 | 1577.8526 | 3828.1555 | 1639.0801 | 3726.5583 | 1577.8526 | 1437.25 | 2401948.7231 | 568026.949 | 257663.3355 | 0 | 887936.5709
5247 | 1437.9908 | 949.4634 | 949.4634 | 924.2651 | 924.2651 | 1798.1 | 1758663.1988 | 332735.4519 | 150932.498 | 941659.0961 | 182661.7566
5248 | 1849.9352 | 122.1541 | 122.1541 | 118.9122 | 118.9122 | 1818.65 | 229044.6877 | 42808.387 | 19418.36 | 3172965.1476 | 21108.4146
5249 | 2043.3748 | 46.1053 | 46.1053 | 44.8817 | 44.8817 | 1848.15 | 87794.3739 | 16157.3985 | 7329.1755 | 3663237.9506 | 6671.226
5250 | 1857.415 | 175.5746 | 175.5746 | 170.915 | 170.915 | 1763.25 | 319689.1281 | 61529.3887 | 27910.4144 | 3091354.5063 | 39608.275
5251 | 1680.6373 | 0 | 0 | 0 | 0 | 1769.65 | 0 | 0 | 0 | 5710805.4503 | 0
5252 | 1432.0081 | 0 | 0 | 0 | 0 | 1785.5 | 0 | 0 | 0 | 4865963.6767 | 0
5253 | 1791.4047 | 0 | 0 | 0 | 0 | 1793.4 | 0 | 0 | 0 | 6087193.2895 | 0
5254 | 1433.6019 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1870.85 | 612371.1463 | 111351.8261 | 50510.4255 | 3820341.8138 | 39503.6271
5255 | 1313.2718 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1844.3 | 1167779.708 | 215514.4963 | 97759.7701 | 2428280.1889 | 92174.4
5256 | 1328.4127 | 0 | 0 | 0 | 0 | 1769.05 | 0 | 0 | 0 | 2434980.4333 | 0
5257 | 1421.6486 | 0 | 0 | 0 | 0 | 1728.6 | 0 | 0 | 0 | 1691761.8316 | 0
5258 | 1459.1023 | 0 | 0 | 0 | 0 | 1705.35 | 0 | 0 | 0 | 1736331.7906 | 0
5259 | 1105.284 | 0 | 0 | 0 | 0 | 1695.55 | 0 | 0 | 0 | 1315287.9267 | 0
5260 | 1154.691 | 0 | 0 | 0 | 0 | 1636.7 | 0 | 0 | 0 | 1374082.34 | 0
5261 | 1428.0237 | 0 | 0 | 0 | 0 | 1579.7 | 0 | 0 | 0 | 1699348.2078 | 0
5262 | 1184.9728 | 0 | 0 | 0 | 0 | 1576.8 | 0 | 0 | 0 | 1410117.6249 | 0
5263 | 1434.3988 | 331.2374 | 331.2374 | 322.4466 | 322.4466 | 1523.25 | 521444.5339 | 116080.7675 | 52655.5259 | 2038208.4444 | 150474.6955
5264 | 1038.439 | 1078.7354 | 1078.7354 | 1050.1063 | 1038.439 | 1334.15 | 1472205.4794 | 373838.0382 | 169577.0879 | 0 | 691444.6048
5265 | 1255.5094 | 1304.2287 | 1304.2287 | 1269.6152 | 1255.5094 | 1671.3 | 2222458.5181 | 451983.3682 | 205024.6778 | 0 | 412685.9253
5266 | 1522.3454 | 1818.8339 | 1581.4192 | 1770.563 | 1522.3454 | 1529.55 | 2468192.3709 | 548044.3393 | 248599.0017 | 0 | 716187.3873
5267 | 1627.697 | 2963.0202 | 1690.8594 | 2884.3832 | 1627.697 | 1222.45 | 2111708.922 | 585970.9196 | 265802.9199 | 0 | 1265615.8016
5268 | 1740.9657 | 3244.905 | 1808.5227 | 3158.787 | 1740.9657 | 1233.3 | 2279559.4208 | 626747.6502 | 284299.698 | 0 | 1334798.3984
5269 | 1456.1419 | 3198.6699 | 1512.6472 | 3113.779 | 1456.1419 | 1146.2 | 1768315.4002 | 524211.0858 | 237787.9731 | 0 | 1243253.9585
5270 | 1415.659 | 1654.79 | 1470.5933 | 1610.8728 | 1415.659 | 1589.15 | 2381792.1936 | 509637.2353 | 231177.1126 | 0 | 581623.4948
5271 | 1574.2258 | 1186.2953 | 1186.2953 | 1154.8117 | 1154.8117 | 1564.75 | 1910848.1188 | 415732.1959 | 188580.7433 | 768786.1239 | 491999.2007
5272 | 1456.6718 | 108.9239 | 108.9239 | 106.0331 | 106.0331 | 1804.6 | 202324.7302 | 38171.913 | 17315.2039 | 2475720.8165 | 20280.566
5273 | 1710.5644 | 631.9351 | 631.9351 | 615.1638 | 615.1638 | 1786.6 | 1163524.0401 | 221458.9831 | 100456.2554 | 2007869.2395 | 128499.0234
5274 | 1605.2895 | 153.6039 | 153.6039 | 149.5273 | 149.5273 | 1754.2 | 277572.0835 | 53829.8421 | 24417.8145 | 2668412.0373 | 35976.517
5275 | 1610.0698 | 0 | 0 | 0 | 0 | 1761.7 | 0 | 0 | 0 | 5471017.2857 | 0
5276 | 1475.0401 | 0 | 0 | 0 | 0 | 1796.8 | 0 | 0 | 0 | 5012186.2904 | 0
5277 | 1838.4211 | 0 | 0 | 0 | 0 | 1827.5 | 0 | 0 | 0 | 6246955.0371 | 0
5278 | 1491.7748 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1873.35 | 613018.8127 | 111351.8261 | 50510.4255 | 4018013.1275 | 38738.9421
5279 | 1526.041 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1879.25 | 1190298.4608 | 215514.4963 | 97759.7701 | 3151269.7844 | 71484
5280 | 1497.353 | 0 | 0 | 0 | 0 | 1829.55 | 0 | 0 | 0 | 2744648.0105 | 0
5281 | 1734.0288 | 0 | 0 | 0 | 0 | 1748.6 | 0 | 0 | 0 | 2063494.2518 | 0
5282 | 1447.9459 | 0 | 0 | 0 | 0 | 1748.45 | 0 | 0 | 0 | 1723055.6317 | 0
5283 | 1251.1145 | 0 | 0 | 0 | 0 | 1643.05 | 0 | 0 | 0 | 1488826.2752 | 0
5284 | 1269.4429 | 0 | 0 | 0 | 0 | 1442.85 | 0 | 0 | 0 | 1510637.1057 | 0
5285 | 1431.2113 | 0 | 0 | 0 | 0 | 1406.7 | 0 | 0 | 0 | 1703141.3958 | 0
5286 | 1506.9156 | 0 | 0 | 0 | 0 | 1519.45 | 0 | 0 | 0 | 1793229.6092 | 0
5287 | 1356.3038 | 317.4992 | 317.4992 | 309.073 | 309.073 | 1436.75 | 470200.8792 | 111266.2755 | 50471.6189 | 1919574.0113 | 170402.8387
5288 | 1302.3903 | 1138.77 | 1138.77 | 1108.5476 | 1108.5476 | 1087.65 | 1278589.9725 | 399077.1482 | 181025.8286 | 355313.5886 | 989989.1603
5289 | 1113.0576 | 1215.1626 | 1156.2499 | 1182.9129 | 1113.0576 | 1562.45 | 1839407.8597 | 400700.7418 | 181762.3087 | 0 | 487018.3599
5290 | 1552.2695 | 1969.848 | 1612.5044 | 1917.5694 | 1552.2695 | 1578.8 | 2592340.0622 | 558817.033 | 253485.6152 | 0 | 653815.9286
5291 | 1629.2201 | 2527.413 | 1692.4415 | 2460.3368 | 1629.2201 | 1410.95 | 2434157.6306 | 586519.2184 | 266051.6343 | 0 | 959692.071
5292 | 1607.9571 | 4042.1544 | 1670.3544 | 3934.8779 | 1607.9571 | 1313.3 | 2238104.8552 | 578864.5492 | 262579.3913 | 0 | 1104184.1275
5293 | 1593.6599 | 3174.6351 | 1655.5016 | 3090.382 | 1593.6599 | 1146.2 | 1935714.867 | 573717.5676 | 260244.6633 | 0 | 1360666.8312
5294 | 1528.3529 | 2218.0455 | 1587.6604 | 2159.1798 | 1528.3529 | 1614.85 | 2609730.8343 | 550207.0541 | 249580.0331 | 0 | 588645.1302
5295 | 1862.026 | 2630.6297 | 1934.2815 | 2560.8142 | 1862.026 | 1810.6 | 3565981.5836 | 670329.3478 | 304068.8402 | 0 | 352667.718
5296 | 1724.6753 | 1072.1545 | 1072.1545 | 1043.7001 | 1043.7001 | 1842.7 | 2033706.6403 | 375732.0501 | 170436.2327 | 1248227.4828 | 160701.2979
5297 | 1844.8819 | 920.7861 | 920.7861 | 896.349 | 896.349 | 1821.15 | 1724022.1236 | 322685.6323 | 146373.7882 | 1738660.8668 | 156920.8438
5298 | 1817.6831 | 0 | 0 | 0 | 0 | 1790.2 | 0 | 0 | 0 | 3331813.1608 | 0
5299 | 1765.9551 | 0 | 0 | 0 | 0 | 1787.35 | 0 | 0 | 0 | 6000715.4774 | 0
5300 | 1718.8879 | 0 | 0 | 0 | 0 | 1819.6 | 0 | 0 | 0 | 5840781.108 | 0
5301 | 1542.7756 | 0 | 0 | 0 | 0 | 1830.3 | 0 | 0 | 0 | 5242351.516 | 0
5302 | 1653.5431 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1878.3 | 614075.5051 | 111351.8261 | 50510.4255 | 4567701.8449 | 37224.8658
5303 | 1906.9535 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1879.3 | 1188975.9135 | 215514.4963 | 97759.7701 | 4445610.7041 | 71454.4
5304 | 1835.2336 | 0 | 0 | 0 | 0 | 1854.95 | 0 | 0 | 0 | 3363983.1668 | 0
5305 | 1701.3564 | 0 | 0 | 0 | 0 | 1823.6 | 0 | 0 | 0 | 3118586.2189 | 0
5306 | 1351.5224 | 0 | 0 | 0 | 0 | 1759.75 | 0 | 0 | 0 | 2477340.6215 | 0
5307 | 1069.424 | 0 | 0 | 0 | 0 | 1738.65 | 0 | 0 | 0 | 1960254.1938 | 0
5308 | 1283.7869 | 0 | 0 | 0 | 0 | 1731.3 | 0 | 0 | 0 | 2353181.4519 | 0
5309 | 1391.3668 | 0 | 0 | 0 | 0 | 1586.1 | 0 | 0 | 0 | 2550375.4269 | 0
5310 | 1366.6633 | 0 | 0 | 0 | 0 | 1522.8 | 0 | 0 | 0 | 2505093.8472 | 0
5311 | 1409.6953 | 204.6715 | 204.6715 | 199.2397 | 199.2397 | 1529.1 | 323831.8523 | 71726.2823 | 32535.8386 | 2218765.1164 | 91837.2725
5312 | 1126.6764 | 758.0688 | 758.0688 | 737.9501 | 737.9501 | 1420.15 | 1113963.6461 | 265662.0256 | 120507.2466 | 712535.4269 | 418848.2691
5313 | 1236.8333 | 1284.828 | 1284.828 | 1250.7294 | 1236.8333 | 1719.35 | 2250524.6098 | 445259.9822 | 201974.8753 | 0 | 347117.2612
5314 | 853.2232 | 1909.8093 | 886.3331 | 1859.124 | 853.2232 | 1633.65 | 1475736.5139 | 307160.3681 | 139331.3558 | 0 | 312578.3357
5315 | 1279.1002 | 2498.8261 | 1328.7352 | 2432.5086 | 1279.1002 | 1534.95 | 2080454.1928 | 460476.085 | 208877.0685 | 0 | 594845.5648
5316 | 1487.5921 | 3328.3398 | 1545.3176 | 3240.0074 | 1487.5921 | 1361.9 | 2148039.0139 | 535533.1542 | 242923.7891 | 0 | 949232.5158
5317 | 1377.6534 | 3150.2637 | 1431.1125 | 3066.6574 | 1377.6534 | 1191.45 | 1737581.6837 | 495955.2222 | 224970.7994 | 0 | 1113901.6525
5318 | 1389.6814 | 3074.3281 | 1443.6083 | 2992.7371 | 1389.6814 | 1747.9 | 2571846.9884 | 500285.3137 | 226934.977 | 0 | 350338.6877
5319 | 1142.5534 | 1593.2792 | 1186.8905 | 1550.9945 | 1142.5534 | 1853.7 | 2240381.5521 | 411319.2377 | 186578.9764 | 0 | 167155.568
5320 | 1250.1114 | 1094.0016 | 1094.0016 | 1064.9674 | 1064.9674 | 1842.7 | 2076670.1711 | 383388.2754 | 173909.1816 | 339368.9565 | 163975.6547
5321 | 1587.4332 | 277.4315 | 277.4315 | 270.0686 | 270.0686 | 1853.8 | 529321.0187 | 97224.7052 | 44102.2066 | 2414729.3107 | 38648.8472
5322 | 1534.0547 | 163.1017 | 163.1017 | 158.7731 | 158.7731 | 1821.4 | 305480.213 | 57158.3033 | 25927.6415 | 2520891.1697 | 27757.119
5323 | 1588.2052 | 0 | 0 | 0 | 0 | 1812.35 | 0 | 0 | 0 | 2911180.1499 | 0
5324 | 1595.3702 | 0 | 0 | 0 | 0 | 1842.4 | 0 | 0 | 0 | 2924313.6334 | 0
5325 | 1622.4644 | 0 | 0 | 0 | 0 | 1855.3 | 0 | 0 | 0 | 2973977.302 | 0
5326 | 1469.4619 | 0 | 0 | 0 | 0 | 1878.35 | 0 | 0 | 0 | 2693523.648 | 0
5327 | 1749.1697 | 0 | 0 | 0 | 0 | 1879.3 | 0 | 0 | 0 | 3206227.9849 | 0
5328 | 1341.9598 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1857.5 | 605457.9143 | 111351.8261 | 50510.4255 | 1892845.8866 | 43587.045
5329 | 1458.3055 | 0 | 0 | 0 | 0 | 1777.2 | 0 | 0 | 0 | 1735383.4926 | 0
5330 | 1478.2277 | 0 | 0 | 0 | 0 | 1784.05 | 0 | 0 | 0 | 1759090.9178 | 0
5331 | 1371.4446 | 0 | 0 | 0 | 0 | 1763.8 | 0 | 0 | 0 | 1632019.1216 | 0
5332 | 1293.3496 | 0 | 0 | 0 | 0 | 1752.9 | 0 | 0 | 0 | 1539086.0157 | 0
5333 | 1466.2743 | 0 | 0 | 0 | 0 | 1743.55 | 0 | 0 | 0 | 1744866.4634 | 0
5334 | 1534.8067 | 0 | 0 | 0 | 0 | 1734.45 | 0 | 0 | 0 | 1826420.0039 | 0
5335 | 1117.2373 | 921.3886 | 921.3886 | 896.9355 | 896.9355 | 1600.15 | 1522664.1724 | 322896.7783 | 146469.5664 | 403813.199 | 353457.0039
5336 | 1320.5663 | 1371.8102 | 1371.8102 | 1335.4031 | 1320.5663 | 1415.35 | 1979573.2603 | 475403.8734 | 215648.4792 | 0 | 772068.9119
5337 | 1426.2447 | 1481.5901 | 1481.5901 | 1442.2695 | 1426.2447 | 1461.1 | 2200581.8111 | 513448.0744 | 232905.7515 | 0 | 768603.2424
5338 | 1743.702 | 1811.3659 | 1811.3659 | 1763.2933 | 1743.702 | 1429.55 | 2630544.6529 | 627732.7236 | 284746.5382 | 0 | 994694.8059
5339 | 1773.4518 | 2725.2399 | 1842.2693 | 2652.9135 | 1773.4518 | 1207.5 | 2266777.5293 | 638442.6624 | 289604.6855 | 0 | 1405460.5832
5340 | 1551.0702 | 3202.3244 | 1611.2589 | 3117.3365 | 1551.0702 | 1124.45 | 1847174.8692 | 558385.2788 | 253289.7668 | 0 | 1358039.5302
5341 | 1468.154 | 3304.7963 | 1525.1253 | 3217.0888 | 1468.154 | 1165.05 | 1809422.2518 | 528535.4396 | 239749.548 | 0 | 1225835.1815
5342 | 1368.2013 | 1558.7587 | 1421.2937 | 1517.3901 | 1368.2013 | 1691 | 2452041.5723 | 492552.4694 | 223427.2729 | 0 | 422774.2029
5343 | 1425.388 | 485.5872 | 485.5872 | 472.7 | 472.7 | 1802.9 | 902122.0076 | 170171.9937 | 77191.9071 | 1746277.129 | 91198.17
5344 | 1789.557 | 1219.2773 | 1219.2773 | 1186.9184 | 1186.9184 | 1791.05 | 2244575.1428 | 427290.6169 | 193823.7715 | 1104636.5002 | 242760.4085
5345 | 1671.8207 | 42.0311 | 42.0311 | 40.9156 | 40.9156 | 1787.15 | 77174.0594 | 14729.6149 | 6681.517 | 2989449.0538 | 8524.6425
5346 | 1623.3211 | 0 | 0 | 0 | 0 | 1771.65 | 0 | 0 | 0 | 2975547.5506 | 0
5347 | 1399.3357 | 0 | 0 | 0 | 0 | 1769.15 | 0 | 0 | 0 | 4754942.8037 | 0
5348 | 1383.398 | 0 | 0 | 0 | 0 | 1825.5 | 0 | 0 | 0 | 4700786.2783 | 0
5349 | 1339.5691 | 0 | 0 | 0 | 0 | 1836.05 | 0 | 0 | 0 | 4551855.8358 | 0
5350 | 1674.2622 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1847.4 | 601562.5522 | 111351.8261 | 50510.4255 | 4638105.3263 | 46676.3724
5351 | 1441.5708 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1843.55 | 1162174.3113 | 215514.4963 | 97759.7701 | 2864240.2079 | 92618.4
5352 | 1500.5405 | 0 | 0 | 0 | 0 | 1823.55 | 0 | 0 | 0 | 2750490.7952 | 0
5353 | 1355.5069 | 0 | 0 | 0 | 0 | 1736.5 | 0 | 0 | 0 | 1613053.1812 | 0
5354 | 1402.5233 | 0 | 0 | 0 | 0 | 1725.3 | 0 | 0 | 0 | 1669002.7032 | 0
5355 | 1098.9089 | 0 | 0 | 0 | 0 | 1721.75 | 0 | 0 | 0 | 1307701.5505 | 0
5356 | 1362.6789 | 0 | 0 | 0 | 0 | 1712.8 | 0 | 0 | 0 | 1621587.8541 | 0
5357 | 1237.5674 | 0 | 0 | 0 | 0 | 1563.25 | 0 | 0 | 0 | 1472705.2262 | 0
5358 | 1263.8647 | 0 | 0 | 0 | 0 | 1543.5 | 0 | 0 | 0 | 1503999.0275 | 0
5359 | 1380.2104 | 234.5902 | 234.5902 | 228.3643 | 228.3643 | 1422.95 | 344165.999 | 82211.1354 | 37291.8845 | 2111333.9839 | 128990.2947
5360 | 1386.2658 | 90.8092 | 90.8092 | 88.3992 | 88.3992 | 1081.65 | 101265.9222 | 31823.7005 | 14435.5842 | 2378989.4702 | 79463.9071
5361 | 1418.5776 | 537.6064 | 537.6064 | 523.3386 | 523.3386 | 443.25 | 244792.9478 | 188401.8989 | 85461.1947 | 1640973.0538 | 797473.209
5362 | 1606.5008 | 1668.8409 | 1668.8409 | 1624.5507 | 1606.5008 | 600.75 | 1021925.9285 | 578340.2765 | 262341.5754 | 0 | 2247896.1996
5363 | 1395.5694 | 1449.7237 | 1449.7237 | 1411.2488 | 1395.5694 | 610.45 | 900830.5118 | 502404.9966 | 227896.4887 | 0 | 1939212.9039
5364 | 1749.1418 | 2237.6519 | 1817.017 | 2178.2658 | 1749.1418 | 611.95 | 1131410.2604 | 629691.0365 | 285634.8507 | 0 | 2427896.2311
5365 | 1070.1512 | 1392.524 | 1111.6779 | 1355.5672 | 1070.1512 | 613.8 | 696672.9287 | 385254.4183 | 174755.6848 | 0 | 1483443.5408
5366 | 1155.2987 | 968.1401 | 968.1401 | 942.4461 | 942.4461 | 479.6 | 479001.9573 | 339280.6126 | 153901.4556 | 390158.6746 | 1402584.204
5367 | 1561.8691 | 632.6186 | 632.6186 | 615.8292 | 615.8292 | 342.5 | 223169.7014 | 221698.5245 | 100564.914 | 1734090.9812 | 978916.185
5368 | 1337.3169 | 1389.2112 | 1389.2112 | 1352.3423 | 1337.3169 | 349.25 | 494796.0679 | 481434.0858 | 218383.8506 | 0 | 2207575.8809
5369 | 1556.0846 | 1006.929 | 1006.929 | 980.2057 | 980.2057 | 695.9 | 724467.1212 | 352874.0438 | 160067.5871 | 1055586.1351 | 1251246.1311
5370 | 1554.3395 | 183.5288 | 183.5288 | 178.658 | 178.658 | 1167.1 | 221243.4933 | 64316.8794 | 29174.8511 | 2521624.1065 | 145656.7191
5371 | 914.8386 | 0 | 0 | 0 | 0 | 1433.75 | 0 | 0 | 0 | 3108621.7069 | 0
5372 | 1265.4585 | 0 | 0 | 0 | 0 | 1662.65 | 0 | 0 | 0 | 4300028 | 0
5373 | 1199.3168 | 0 | 0 | 0 | 0 | 1753.9 | 0 | 0 | 0 | 4075278.4252 | 0
5374 | 1364.2726 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1770.8 | 581988.3184 | 111351.8261 | 50510.4255 | 3584760.934 | 70106.3208
5375 | 1340.366 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1766.1 | 1123053.0923 | 215514.4963 | 97759.7701 | 2520346.2805 | 138468.8
5376 | 1275.0212 | 0 | 0 | 0 | 0 | 1747.45 | 0 | 0 | 0 | 2337113.7936 | 0
5377 | 2321.3354 | 0 | 0 | 0 | 0 | 1696.6 | 0 | 0 | 0 | 2762389.1343 | 0
5378 | 2049.5965 | 0 | 0 | 0 | 0 | 1653.35 | 0 | 0 | 0 | 2439019.86 | 0
5379 | 2418.5558 | 0 | 0 | 0 | 0 | 1407.55 | 0 | 0 | 0 | 2878081.3663 | 0
5380 | 2200.2084 | 0 | 0 | 0 | 0 | 1218.1 | 0 | 0 | 0 | 2618247.9912 | 0
5381 | 1996.205 | 0 | 0 | 0 | 0 | 1189.25 | 0 | 0 | 0 | 2375483.9619 | 0
5382 | 2369.9456 | 0 | 0 | 0 | 0 | 1304.75 | 0 | 0 | 0 | 2820235.2509 | 0
5383 | 2032.8619 | 143.2906 | 143.2906 | 139.4878 | 139.4878 | 1628.6 | 239611.1187 | 50215.6057 | 22778.3567 | 3470554.6783 | 50709.8418
5384 | 1717.081 | 552.3616 | 552.3616 | 537.7022 | 537.7022 | 1599.05 | 908138.8446 | 193572.7906 | 87806.7686 | 2161801.2795 | 211031.2116
5385 | 1818.1981 | 1626.4919 | 1626.4919 | 1583.3257 | 1583.3257 | 1670.8 | 2801726.9931 | 569997.2538 | 258557.0876 | 430521.1182 | 510205.0236
5386 | 2087.6529 | 2168.6638 | 2168.6638 | 2111.1087 | 2087.6529 | 1576.15 | 3496158.3861 | 751555.0494 | 340913.721 | 0 | 884851.688
5387 | 2288.3681 | 2473.6143 | 2377.1675 | 2407.966 | 2288.3681 | 1232.8 | 2998083.0461 | 823812.5308 | 373690.5174 | 0 | 1755636.0378
5388 | 2277.5584 | 3139.4009 | 2365.9381 | 3056.0829 | 2277.5584 | 1048.55 | 2539763.1851 | 819921.0067 | 371925.2789 | 0 | 2166982.894
5389 | 2252.5022 | 3037.838 | 2339.9098 | 2957.2155 | 2252.5022 | 775.7 | 1855411.9394 | 810900.7898 | 367833.6083 | 0 | 2757738.4361
5390 | 2381.0831 | 2577.9062 | 2473.4803 | 2509.4899 | 2381.0831 | 1405.1 | 3550776.3134 | 857189.9153 | 388830.8699 | 0 | 1416506.335
5391 | 2172.9459 | 1183.7585 | 1183.7585 | 1152.3422 | 1152.3422 | 1086.9 | 1332411.1659 | 414843.1986 | 188177.4842 | 1870766.4644 | 1029945.7546
5392 | 1845.8412 | 158.7439 | 158.7439 | 154.5309 | 154.5309 | 1511.6 | 248276.9919 | 55631.1355 | 25234.9012 | 3100171.6589 | 73876.3608
5393 | 2378.556 | 38.0452 | 38.0452 | 37.0355 | 37.0355 | 1764.55 | 69294.2232 | 13332.7752 | 6047.895 | 4292007.0387 | 8535.5334
5394 | 2247.4788 | 20.2671 | 20.2671 | 19.7292 | 19.7292 | 1764.2 | 36858.1665 | 7102.5132 | 3221.7789 | 4083465.029 | 4553.7696
5395 | 2405.0087 | 0 | 0 | 0 | 0 | 1768.1 | 0 | 0 | 0 | 8172219.4641 | 0
5396 | 1889.422 | 0 | 0 | 0 | 0 | 1785.5 | 0 | 0 | 0 | 6420255.9118 | 0
5397 | 2380.3051 | 0 | 0 | 0 | 0 | 1791.85 | 0 | 0 | 0 | 8088276.8521 | 0
5398 | 2206.5835 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1811.45 | 592034.7439 | 111351.8261 | 50510.4255 | 6446933.2261 | 57672.5427
5399 | 2286.2723 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1812.4 | 1146078.7995 | 215514.4963 | 97759.7701 | 5734535.9763 | 111059.2
5400 | 1948.3917 | 0 | 0 | 0 | 0 | 1770 | 0 | 0 | 0 | 3571402.0154 | 0
5401 | 1804.9518 | 0 | 0 | 0 | 0 | 1652 | 0 | 0 | 0 | 2147892.6837 | 0
5402 | 1843.2025 | 0 | 0 | 0 | 0 | 1412.35 | 0 | 0 | 0 | 2193410.9393 | 0
5403 | 1243.9425 | 0 | 0 | 0 | 0 | 1388.55 | 0 | 0 | 0 | 1480291.6024 | 0
5404 | 1298.1309 | 0 | 0 | 0 | 0 | 1410.75 | 0 | 0 | 0 | 1544775.7984 | 0
5405 | 1563.4947 | 0 | 0 | 0 | 0 | 1418.75 | 0 | 0 | 0 | 1860558.6954 | 0
5406 | 1161.0661 | 0 | 0 | 0 | 0 | 1386.8 | 0 | 0 | 0 | 1381668.7149 | 0
5407 | 1122.8155 | 275.303 | 275.303 | 267.9966 | 267.9966 | 1389.6 | 393822.415 | 96478.7775 | 43763.8455 | 1566883.0599 | 160124.4008
5408 | 842.0808 | 874.7577 | 874.7577 | 851.5421 | 842.0808 | 1179.5 | 1051716.5541 | 303149.0718 | 137511.7873 | 0 | 690927.2595
5409 | 1173.7765 | 1414.5892 | 1219.3241 | 1377.0468 | 1173.7765 | 1264.4 | 1572991.3455 | 422559.5454 | 191677.7049 | 0 | 863430.0044
5410 | 1566.0129 | 2525.7987 | 1626.7817 | 2458.7654 | 1566.0129 | 1036.15 | 1718719.2996 | 563764.6328 | 255729.9015 | 0 | 1509401.5038
5411 | 1402.9586 | 2502.3259 | 1457.4005 | 2435.9155 | 1402.9586 | 939.1 | 1398083.796 | 505065.0892 | 229103.1363 | 0 | 1488398.7586
5412 | 1433.2991 | 2857.1068 | 1488.9178 | 2781.2807 | 1433.2991 | 845.95 | 1286928.8963 | 515987.6774 | 234057.7437 | 0 | 1654098.831
5413 | 1510.4219 | 3429.1267 | 1569.0335 | 3338.1195 | 1510.4219 | 675.2 | 1080524.0555 | 543751.9006 | 246651.9038 | 0 | 2001006.9941
5414 | 1372.2356 | 3207.641 | 1425.4842 | 3122.512 | 1372.2356 | 1183.25 | 1723156.5487 | 494004.7984 | 224086.0655 | 0 | 1120773.3863
5415 | 1544.9103 | 2569.8336 | 1604.8598 | 2501.6316 | 1544.9103 | 1562.75 | 2564536.4097 | 556167.6983 | 252283.8476 | 0 | 675512.0169
5416 | 1537.5301 | 2006.3361 | 1597.1935 | 1953.089 | 1537.5301 | 1772.6 | 2894328.9562 | 553510.8331 | 251078.664 | 0 | 349634.3429
5417 | 1196.4679 | 1394.6099 | 1242.8966 | 1357.5977 | 1196.4679 | 1796.6 | 2276859.9115 | 430728.4465 | 195383.2092 | 0 | 243361.5723
5418 | 1288.0652 | 329.9711 | 329.9711 | 321.2139 | 321.2139 | 1784.2 | 605568.0184 | 115636.9969 | 52454.2266 | 1772238.5204 | 67851.836
5419 | 1408.1115 | 0 | 0 | 0 | 0 | 1775.15 | 0 | 0 | 0 | 4784762.7377 | 0
5420 | 1260.6772 | 0 | 0 | 0 | 0 | 1787.4 | 0 | 0 | 0 | 4283781.044 | 0
5421 | 1176.207 | 0 | 0 | 0 | 0 | 1790.3 | 0 | 0 | 0 | 3996751.4676 | 0
5422 | 1688.6062 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1835.85 | 601962.6617 | 111351.8261 | 50510.4255 | 4686846.1976 | 50209.2171
5423 | 1341.1629 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1869.3 | 1185996.2565 | 215514.4963 | 97759.7701 | 2523054.106 | 77374.4
5424 | 1206.4888 | 0 | 0 | 0 | 0 | 1795 | 0 | 0 | 0 | 2211493.9264 | 0
5425 | 1402.5233 | 0 | 0 | 0 | 0 | 1738.6 | 0 | 0 | 0 | 1669002.7032 | 0
5426 | 1134.7688 | 0 | 0 | 0 | 0 | 1705.35 | 0 | 0 | 0 | 1350374.9148 | 0
5427 | 1440.7739 | 0 | 0 | 0 | 0 | 1695.55 | 0 | 0 | 0 | 1714520.9589 | 0
5428 | 1137.9564 | 0 | 0 | 0 | 0 | 1680.05 | 0 | 0 | 0 | 1354168.1029 | 0
5429 | 876.5771 | 0 | 0 | 0 | 0 | 1655.7 | 0 | 0 | 0 | 1043126.6899 | 0
5430 | 1141.1439 | 0 | 0 | 0 | 0 | 1679.8 | 0 | 0 | 0 | 1357961.291 | 0
5431 | 939.5312 | 321.2483 | 321.2483 | 312.7225 | 312.7225 | 1682.6 | 556681.0156 | 112580.1131 | 51067.5902 | 1148940.3176 | 97158.6792
5432 | 1269.4808 | 1161.7577 | 1161.7577 | 1130.9253 | 1130.9253 | 1540.65 | 1847968.445 | 407133.0946 | 184680.0954 | 253972.2977 | 508501.828
5433 | 1423.8829 | 1479.1354 | 1479.1354 | 1439.8799 | 1423.8829 | 1722.8 | 2602453.7011 | 512597.8343 | 232520.0732 | 0 | 394700.0904
5434 | 1541.5026 | 2269.0695 | 1601.3196 | 2208.8497 | 1541.5026 | 1685.15 | 2752320.1023 | 554940.9288 | 251727.3713 | 0 | 485342.0873
5435 | 1400.2571 | 3804.772 | 1454.5936 | 3703.7954 | 1400.2571 | 1551.05 | 2308716.0275 | 504092.5668 | 228661.9893 | 0 | 628645.4385
5436 | 1426.2825 | 3342.3626 | 1481.6296 | 3253.6581 | 1426.2825 | 1256.45 | 1906101.9622 | 513461.7011 | 232911.9327 | 0 | 1060512.3551
5437 | 1362.2406 | 2957.4262 | 1415.1024 | 2878.9377 | 1362.2406 | 675.2 | 976317.1587 | 490406.6092 | 222453.8869 | 0 | 1804696.3217
5438 | 1667.2764 | 3050.1749 | 1731.9742 | 2969.2249 | 1667.2764 | 892.5 | 1578525.5603 | 600219.5202 | 272266.2435 | 0 | 1846508.6628
5439 | 1636.4498 | 2468.492 | 1699.952 | 2402.9796 | 1636.4498 | 1452.25 | 2521995.5278 | 589121.9352 | 267232.2556 | 0 | 896365.3889
5440 | 1895.057 | 1774.8623 | 1774.8623 | 1727.7584 | 1727.7584 | 1799.6 | 3296795.9369 | 621993.0384 | 282142.9533 | 306658.2292 | 338918.6844
5441 | 1891.8794 | 368.2584 | 368.2584 | 358.485 | 358.485 | 1816.6 | 689435.8644 | 129054.5945 | 58540.598 | 2810711.9467 | 64355.4268
5442 | 1615.2725 | 49.2632 | 49.2632 | 47.9558 | 47.9558 | 1784.2 | 90422.198 | 17264.0945 | 7831.1851 | 2872891.5054 | 10130.0836
5443 | 1799.3766 | 0 | 0 | 0 | 0 | 1775.15 | 0 | 0 | 0 | 6114281.7072 | 0
5444 | 1355.5069 | 0 | 0 | 0 | 0 | 1824.9 | 0 | 0 | 0 | 4606012.3613 | 0
5445 | 1471.8526 | 0 | 0 | 0 | 0 | 1797.5 | 0 | 0 | 0 | 5001354.9853 | 0
5446 | 1823.2803 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1865.85 | 611752.1148 | 111351.8261 | 50510.4255 | 5144468.8267 | 41032.9971
5447 | 1494.9623 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1849.3 | 1173263.3653 | 215514.4963 | 97759.7701 | 3045664.5623 | 89214.4
5448 | 1516.4783 | 0 | 0 | 0 | 0 | 1790 | 0 | 0 | 0 | 2779704.7184 | 0
5449 | 1078.9867 | 0 | 0 | 0 | 0 | 1768.6 | 0 | 0 | 0 | 1283994.1254 | 0
5450 | 1199.3168 | 0 | 0 | 0 | 0 | 1745.35 | 0 | 0 | 0 | 1427186.9706 | 0
5451 | 1483.009 | 0 | 0 | 0 | 0 | 1723.5 | 0 | 0 | 0 | 1764780.6993 | 0
5452 | 1071.8147 | 0 | 0 | 0 | 0 | 1688.2 | 0 | 0 | 0 | 1275459.4525 | 0
5453 | 1069.424 | 0 | 0 | 0 | 0 | 1682.7 | 0 | 0 | 0 | 1272614.5612 | 0
5454 | 908.4526 | 0 | 0 | 0 | 0 | 1679.8 | 0 | 0 | 0 | 1081058.5695 | 0
5455 | 961.0472 | 321.0831 | 321.0831 | 312.5617 | 312.5617 | 1682.6 | 558074.8713 | 112522.23 | 51041.3338 | 1188673.8345 | 97108.53
5456 | 1232.0808 | 1163.4499 | 1163.4499 | 1132.5726 | 1132.5726 | 1597.7 | 1921860.2757 | 407726.1236 | 184949.0999 | 182398.671 | 445995.4122
5457 | 898.5931 | 1390.8079 | 933.4627 | 1353.8966 | 898.5931 | 1722.8 | 1642090.5197 | 323493.5087 | 146740.2499 | 0 | 249090.0017
5458 | 1637.5824 | 2156.3582 | 1701.128 | 2099.1296 | 1637.5824 | 1572.15 | 2729120.9519 | 589529.6629 | 267417.2054 | 0 | 700639.6286
5459 | 1399.4642 | 2799.8946 | 1453.7698 | 2725.5869 | 1399.4642 | 1231.45 | 1829764.7171 | 503807.1214 | 228532.5081 | 0 | 1075558.2309
5460 | 1253.0838 | 4203.0269 | 1301.7096 | 4091.4808 | 1253.0838 | 845.95 | 1126965.6585 | 451110.1777 | 204628.5889 | 0 | 1446121.3905
5461 | 1139.5362 | 3288.326 | 1183.7554 | 3201.0557 | 1139.5362 | 675.2 | 816992.0319 | 410233.0392 | 186086.2647 | 0 | 1509657.5843
5462 | 1059.7836 | 3883.6588 | 1100.9087 | 3780.5886 | 1059.7836 | 1546.45 | 1740636.9284 | 381522.1126 | 173062.6694 | 0 | 480664.8726
5463 | 1558.9445 | 3293.3767 | 1619.4395 | 3205.9723 | 1558.9445 | 1810.6 | 2997345.379 | 561220.0096 | 254575.6321 | 0 | 295264.0828
5464 | 1523.5696 | 2069.3385 | 1582.6918 | 2014.4194 | 1523.5696 | 1834.6 | 2968406.1316 | 548485.0582 | 248798.9167 | 0 | 251998.4128
5465 | 1542.7437 | 1351.1598 | 1351.1598 | 1315.3008 | 1315.3008 | 1831.6 | 2554503.3196 | 473508.2831 | 214788.6184 | 416902.9212 | 216811.2952
5466 | 951.0801 | 273.6409 | 273.6409 | 266.3786 | 266.3786 | 1844.2 | 521959.1389 | 95896.3059 | 43499.6299 | 1255057.8411 | 40623.9152
5467 | 976.1213 | 0 | 0 | 0 | 0 | 1835.15 | 0 | 0 | 0 | 3316860.3109 | 0
5468 | 1243.9425 | 0 | 0 | 0 | 0 | 1852.4 | 0 | 0 | 0 | 4226916.6932 | 0
5469 | 1221.6297 | 0 | 0 | 0 | 0 | 1860.3 | 0 | 0 | 0 | 4151097.5609 | 0
5470 | 1326.8189 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1878.35 | 617025.3424 | 111351.8261 | 50510.4255 | 3457493.1051 | 37209.5721
5471 | 1231.9892 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1879.3 | 1195260.5994 | 215514.4963 | 97759.7701 | 2152081.9175 | 71454.4
5472 | 1280.5994 | 0 | 0 | 0 | 0 | 1852.45 | 0 | 0 | 0 | 2347338.6672 | 0
5473 | 1526.8378 | 0 | 0 | 0 | 0 | 1768.6 | 0 | 0 | 0 | 2798693.7681 | 0
5474 | 1339.5691 | 0 | 0 | 0 | 0 | 1745.35 | 0 | 0 | 0 | 2455430.1786 | 0
5475 | 1200.1137 | 0 | 0 | 0 | 0 | 1735.55 | 0 | 0 | 0 | 2199808.3589 | 0
5476 | 1116.4404 | 0 | 0 | 0 | 0 | 1728.2 | 0 | 0 | 0 | 2046435.266 | 0
5477 | 1081.3773 | 0 | 0 | 0 | 0 | 1722.7 | 0 | 0 | 0 | 1982164.6367 | 0
5478 | 1066.2364 | 0 | 0 | 0 | 0 | 1719.8 | 0 | 0 | 0 | 1954411.4092 | 0
5479 | 1336.3816 | 182.411 | 182.411 | 177.5699 | 177.5699 | 1715.55 | 323696.3203 | 63925.1672 | 28997.1661 | 2124101.7527 | 49441.3923
5480 | 911.6949 | 947.0731 | 947.0731 | 921.9383 | 911.6949 | 1557.7 | 1508504.4526 | 328210.1706 | 148879.7802 | 0 | 403242.6624
5481 | 1039.4979 | 1950.1482 | 1079.8355 | 1898.3923 | 1039.4979 | 1722.8 | 1901566.6687 | 374219.2296 | 169750.0005 | 0 | 288148.8068
5482 | 1131.3791 | 2650.6506 | 1175.2819 | 2580.3037 | 1131.3791 | 1523.45 | 1830726.7398 | 407296.4663 | 184754.2026 | 0 | 539158.6972
5483 | 1048.2088 | 3874.3615 | 1088.8834 | 3771.5381 | 1048.2088 | 1471 | 1639184.7902 | 377355.1838 | 171172.5042 | 0 | 554502.4785
5484 | 1006.9788 | 4144.5962 | 1046.0546 | 4034.6009 | 1006.9788 | 1358.55 | 1456028.7981 | 362512.3838 | 164439.6452 | 0 | 645926.5795
5485 | 904.3835 | 4144.0643 | 939.4784 | 4034.0831 | 904.3835 | 1154.6 | 1109131.3983 | 325578.0488 | 147685.8205 | 0 | 764565.7845
5486 | 1037.6411 | 3834.8443 | 1077.9064 | 3733.0697 | 1037.6411 | 1670 | 1841026.524 | 373550.7996 | 169446.7933 | 0 | 342421.5663
5487 | 1025.9707 | 3257.9223 | 1065.7835 | 3171.4588 | 1025.9707 | 1530.7 | 1667517.059 | 369349.4455 | 167541.0124 | 0 | 481488.0411
5488 | 1029.466 | 2424.8819 | 1069.4142 | 2360.5269 | 1029.466 | 1743 | 1903032.7795 | 370607.7719 | 168111.8032 | 0 | 264572.7705
5489 | 1371.0223 | 1340.0768 | 1340.0768 | 1304.5119 | 1304.5119 | 1851.6 | 2559669.5542 | 469624.2896 | 213026.7958 | 121913.5147 | 189494.4828
5490 | 1163.9011 | 286.1606 | 286.1606 | 278.566 | 278.566 | 1819.2 | 538926.8337 | 100283.7733 | 45489.8338 | 1622819.1284 | 49299.4592
5491 | 1193.7386 | 0 | 0 | 0 | 0 | 1807.65 | 0 | 0 | 0 | 2188122.7896 | 0
5492 | 1105.284 | 0 | 0 | 0 | 0 | 1852.4 | 0 | 0 | 0 | 2025985.5207 | 0
5493 | 1094.1275 | 0 | 0 | 0 | 0 | 1860.25 | 0 | 0 | 0 | 2005535.7735 | 0
5494 | 1174.6132 | 0 | 0 | 0 | 0 | 1878.35 | 0 | 0 | 0 | 2153066.0818 | 0
5495 | 1165.0506 | 218.3048 | 218.3048 | 212.5111 | 212.5111 | 1879.3 | 422665.0603 | 76504.0057 | 34703.067 | 1746004.8338 | 25191.297
5496 | 495.6645 | 514.8981 | 514.8981 | 501.233 | 495.6645 | 1825 | 959186.8942 | 178439.2119 | 80942.0092 | 0 | 86741.2
5497 | 368.1624 | 0 | 0 | 0 | 0 | 1777.2 | 0 | 0 | 0 | 438113.2097 | 0
5498 | 341.0682 | 0 | 0 | 0 | 0 | 1784.05 | 0 | 0 | 0 | 405871.1121 | 0
5499 | 376.9281 | 0 | 0 | 0 | 0 | 1746.6 | 0 | 0 | 0 | 448544.4766 | 0
5500 | 385.6939 | 0 | 0 | 0 | 0 | 1709.8 | 0 | 0 | 0 | 458975.7435 | 0
5501 | 367.3655 | 0 | 0 | 0 | 0 | 1700.45 | 0 | 0 | 0 | 437164.9128 | 0
5502 | 324.3335 | 0 | 0 | 0 | 0 | 1691.35 | 0 | 0 | 0 | 385956.8752 | 0
5503 | 333.8962 | 346.8528 | 346.8528 | 337.6475 | 333.8962 | 1688.2 | 596731.6673 | 120202.6202 | 54525.2441 | 0 | 104108.7728
5504 | 280.1859 | 849.3403 | 291.0585 | 826.7992 | 280.1859 | 1447.5 | 430646.0738 | 100866.9243 | 45754.3576 | 0 | 154802.7102
5505 | 809.242 | 2137.8893 | 840.6455 | 2081.1508 | 809.242 | 1428.95 | 1228124.876 | 291327.1154 | 132149.2165 | 0 | 462117.6368
5506 | 1188.3885 | 3390.4489 | 1234.5031 | 3300.4682 | 1188.3885 | 1113.1 | 1403501.1134 | 427819.8442 | 194063.8349 | 0 | 1053981.7216
5507 | 993.5084 | 3983.9014 | 1032.0619 | 3878.1708 | 993.5084 | 733.8 | 774700.0569 | 357663.0399 | 162239.929 | 0 | 1257980.3922
5508 | 1233.7922 | 3606.3333 | 1281.669 | 3510.6231 | 1233.7922 | 641.8 | 841384.8286 | 444165.1772 | 201478.2596 | 0 | 1675736.5104
5509 | 1154.0047 | 2644.3855 | 1198.7848 | 2574.205 | 1154.0047 | 949 | 1163892.6415 | 415441.6999 | 188448.9711 | 0 | 1212858.9628
5510 | 1230.0597 | 3017.8847 | 1277.7922 | 2937.7916 | 1230.0597 | 1399.2 | 1828876.6154 | 442821.5042 | 200868.7546 | 0 | 739019.8882
5511 | 1043.0311 | 2593.0935 | 1083.5056 | 2524.2742 | 1043.0311 | 1759.8 | 1948097.9568 | 375491.1827 | 170326.9726 | 0 | 250536.0613
5512 | 1276.6757 | 1962.7385 | 1326.2171 | 1910.6485 | 1276.6757 | 1747.95 | 2367950.6588 | 459603.2531 | 208481.1423 | 0 | 321786.1109
5513 | 1051.0647 | 1359.463 | 1091.8513 | 1323.3836 | 1051.0647 | 1787.15 | 1991515.6459 | 378383.2895 | 171638.8644 | 0 | 223719.1199
5514 | 1040.0298 | 277.686 | 277.686 | 270.3164 | 270.3164 | 1759.6 | 505941.9526 | 97313.8962 | 44142.6646 | 1410884.6709 | 63609.3592
5515 | 1084.0897 | 0 | 0 | 0 | 0 | 1769.15 | 0 | 0 | 0 | 3683736.9127 | 0
5516 | 894.9055 | 460.8626 | 460.8626 | 448.6316 | 448.6316 | 1782.7 | 850489.7379 | 161507.3644 | 73261.535 | 1516438.7521 | 96404.4931
5517 | 269.3482 | 279.8 | 279.8 | 272.3742 | 269.3482 | 1803.55 | 516600.9764 | 96965.3595 | 43984.5645 | 0 | 52913.4146
5518 | 90.8453 | 94.3702 | 94.3702 | 91.8657 | 90.8453 | 1847.4 | 177860.1668 | 32704.2929 | 14835.0306 | 0 | 13862.947
5519 | 94.0328 | 97.6819 | 97.6819 | 95.0895 | 94.0328 | 1843.55 | 183618.5644 | 33851.8119 | 15355.558 | 0 | 14711.4333
5520 | 90.8453 | 0 | 0 | 0 | 0 | 1816.05 | 0 | 0 | 0 | 166519.3578 | 0
5521 | 95.6266 | 0 | 0 | 0 | 0 | 1774.95 | 0 | 0 | 0 | 113795.6389 | 0
5522 | 87.6577 | 0 | 0 | 0 | 0 | 1755.3 | 0 | 0 | 0 | 104312.669 | 0
5523 | 94.0328 | 0 | 0 | 0 | 0 | 1723.95 | 0 | 0 | 0 | 111899.0449 | 0
5524 | 85.267 | 0 | 0 | 0 | 0 | 1719.7 | 0 | 0 | 0 | 101467.778 | 0
5525 | 94.8297 | 0 | 0 | 0 | 0 | 1718.25 | 0 | 0 | 0 | 112847.3419 | 0
5526 | 87.6577 | 0 | 0 | 0 | 0 | 1718.5 | 0 | 0 | 0 | 104312.669 | 0
5527 | 93.2359 | 96.854 | 96.854 | 94.2835 | 93.2359 | 1708.75 | 168773.9307 | 33564.9321 | 15225.4262 | 0 | 27154.9625
5528 | 76.7762 | 870.5651 | 79.7553 | 847.4608 | 76.7762 | 1195.6 | 96961.9161 | 27639.4307 | 12537.5529 | 0 | 61758.7723
5529 | 83.0716 | 2417.5261 | 86.2956 | 2353.3663 | 83.0716 | 443.3 | 38861.9499 | 29905.7808 | 13565.5944 | 0 | 129317.5804
5530 | 78.5941 | 3393.5185 | 81.6438 | 3303.4564 | 78.5941 | 600.75 | 49969.7782 | 28293.8751 | 12834.4161 | 0 | 109972.791
5531 | 85.6854 | 3939.0552 | 89.01 | 3834.5148 | 85.6854 | 610.45 | 55524.6126 | 30846.7464 | 13992.4269 | 0 | 119064.1568
5532 | 80.162 | 4192.2513 | 83.2727 | 4080.9913 | 80.162 | 611.95 | 52137.9781 | 28858.3111 | 13090.4505 | 0 | 111268.8296
5533 | 88.2653 | 4164.0655 | 91.6911 | 4053.5534 | 88.2653 | 613.8 | 57677.121 | 31775.5196 | 14413.7288 | 0 | 122353.4036
5534 | 80.4469 | 3871.9255 | 83.5687 | 3769.1667 | 80.4469 | 628.6 | 53872.9572 | 28960.8706 | 13136.9727 | 0 | 110324.8275
5535 | 94.9911 | 2640.9855 | 98.6771 | 2570.8952 | 94.9911 | 640.5 | 64705.7197 | 34196.7848 | 15512.0416 | 0 | 129140.3582
5536 | 84.2281 | 2445.4804 | 87.4964 | 2380.5787 | 84.2281 | 1059.95 | 94906.5945 | 30322.115 | 13754.4483 | 0 | 79178.6229
5537 | 89.7426 | 1339.1014 | 93.2255 | 1303.5624 | 89.7426 | 1141.45 | 108726.1693 | 32307.323 | 14654.9607 | 0 | 77048.4782
5538 | 80.4598 | 277.8512 | 83.5812 | 270.4772 | 80.4598 | 1585.85 | 135366.5137 | 28965.5324 | 13139.0873 | 0 | 33322.4312
5539 | 96.4285 | 100.1699 | 100.1699 | 97.5114 | 96.4285 | 1754.2 | 180004.027 | 34714.2442 | 15746.7669 | 0 | 23702.0024
5540 | 86.0639 | 89.4037 | 89.4037 | 87.031 | 86.0639 | 1801.3 | 164602.3477 | 30983.0143 | 14054.2395 | 0 | 17100.9026
5541 | 93.2359 | 96.854 | 96.854 | 94.2835 | 93.2359 | 1799.4 | 178287.9823 | 33564.9321 | 15225.4262 | 0 | 18703.1261
5542 | 86.8608 | 90.2316 | 90.2316 | 87.8369 | 86.8608 | 1819.25 | 167553.1363 | 31269.894 | 14184.3714 | 0 | 15700.0926
5543 | 92.439 | 96.0261 | 96.0261 | 93.4776 | 92.439 | 1816.1 | 177635.3561 | 33278.0524 | 15095.2943 | 0 | 16999.5321
5544 | 86.8608 | 90.2316 | 90.2316 | 87.8369 | 86.8608 | 1790.9 | 164840.5083 | 31269.894 | 14184.3714 | 0 | 18162.5968
5545 | 93.2359 | 0 | 0 | 0 | 0 | 1788.6 | 0 | 0 | 0 | 110950.7479 | 0
5546 | 87.6577 | 0.59524 | 0.59524 | 0.57944 | 0.57944 | 1743.3 | 1074.4074 | 208.5976 | 94.6222 | 103623.1379 | 147.0891
5547 | 92.439 | 96.0261 | 96.0261 | 93.4776 | 92.439 | 1285.8 | 126570.7881 | 33278.0524 | 15095.2943 | 0 | 66019.9338
5548 | 86.8608 | 90.2316 | 90.2316 | 87.8369 | 86.8608 | 964.5 | 88906.0326 | 31269.894 | 14184.3714 | 0 | 89944.3758
5549 | 93.2359 | 96.854 | 96.854 | 94.2835 | 93.2359 | 959 | 94918.159 | 33564.9321 | 15225.4262 | 0 | 97058.5954
5550 | 82.8764 | 86.092 | 86.092 | 83.8071 | 82.8764 | 1058.2 | 93061.8329 | 29835.4952 | 13533.7121 | 0 | 78052.6168
5551 | 84.4702 | 87.7478 | 87.7478 | 85.4191 | 84.4702 | 1163.1 | 104108.5481 | 30409.2548 | 13793.9758 | 0 | 70692.943
5552 | 79.4856 | 852.279 | 82.5704 | 829.66 | 79.4856 | 844.15 | 71267.7382 | 28614.8219 | 12980.0011 | 0 | 91873.4495
5553 | 83.7151 | 2409.972 | 86.9635 | 2346.0126 | 83.7151 | 1627.9 | 144233.0526 | 30137.4362 | 13670.6759 | 0 | 31150.3889
5554 | 80.1929 | 3383.1336 | 83.3049 | 3293.3471 | 80.1929 | 1725.1 | 146572.2133 | 28869.4276 | 13095.4931 | 0 | 22045.0157
5555 | 80.8682 | 4000.3779 | 84.0071 | 3894.21 | 80.8682 | 1460.95 | 125498.8386 | 29112.5582 | 13205.7799 | 0 | 43592.0126
5556 | 79.7665 | 4251.0363 | 82.8613 | 4138.2161 | 79.7665 | 1358.55 | 115014.649 | 28715.947 | 13025.8726 | 0 | 51166.2338
5557 | 81.1979 | 4218.6983 | 84.3489 | 4106.7363 | 81.1979 | 1052.5 | 90606.0175 | 29231.2547 | 13259.6219 | 0 | 76935.0385
5558 | 74.3586 | 3881.3994 | 77.2434 | 3778.3892 | 74.3586 | 1654.85 | 130591.8337 | 26769.1092 | 12142.7654 | 0 | 25664.8834
5559 | 87.9635 | 2496.95 | 91.3774 | 2430.6823 | 87.9635 | 1810.6 | 168947.7221 | 31666.8639 | 14364.4413 | 0 | 16660.289
5560 | 78.7595 | 2116.5616 | 81.8163 | 2060.3892 | 78.7595 | 1824.6 | 152273.733 | 28353.4027 | 12861.4185 | 0 | 13814.4079
5561 | 83.995 | 1220.9155 | 87.2544 | 1188.5131 | 83.995 | 1864.1 | 165832.3091 | 30238.2027 | 13716.3847 | 0 | 11414.9215
5562 | 78.9318 | 280.1407 | 81.9949 | 272.7059 | 78.9318 | 1844.2 | 153846.8986 | 28415.4404 | 12889.5595 | 0 | 12297.5712
5563 | 94.8446 | 98.5254 | 98.5254 | 95.9106 | 94.8446 | 1845.15 | 185071.4305 | 34144.0707 | 15488.1298 | 0 | 14686.6926
5564 | 89.2515 | 92.7144 | 92.7144 | 90.2538 | 89.2515 | 1852.4 | 175158.1072 | 32130.5333 | 14574.7669 | 0 | 13173.4476
5565 | 93.2359 | 96.854 | 96.854 | 94.2835 | 93.2359 | 1860.3 | 183788.8704 | 33564.9321 | 15225.4262 | 0 | 13025.0584
5566 | 86.8608 | 90.2316 | 90.2316 | 87.8369 | 86.8608 | 1878.35 | 172513.851 | 31269.894 | 14184.3714 | 0 | 10566.6184
5567 | 96.4235 | 100.1647 | 100.1647 | 97.5064 | 96.4235 | 1879.3 | 191515.5392 | 34712.4512 | 15745.9536 | 0 | 11638.2561
5568 | 86.8608 | 90.2316 | 90.2316 | 87.8369 | 86.8608 | 1855 | 170802.5951 | 31269.894 | 14184.3714 | 0 | 12594.8184
5569 | 93.2359 | 0 | 0 | 0 | 0 | 1823.6 | 0 | 0 | 0 | 110950.7479 | 0
5570 | 88.4546 | 0 | 0 | 0 | 0 | 1743.3 | 0 | 0 | 0 | 105260.966 | 0
5571 | 86.8608 | 89.9885 | 89.9885 | 87.6003 | 86.8608 | 1553.1 | 143311.6049 | 31269.894 | 14184.3714 | 0 | 38713.6063
5572 | 86.8608 | 90.2316 | 90.2316 | 87.8369 | 86.8608 | 1276.3 | 117506.7877 | 31269.894 | 14184.3714 | 0 | 62861.1731
5573 | 93.2359 | 96.854 | 96.854 | 94.2835 | 93.2359 | 1280.6 | 126651.254 | 33564.9321 | 15225.4262 | 0 | 67073.9227
5574 | 83.6733 | 86.9199 | 86.9199 | 84.6131 | 83.6733 | 1386.3 | 123100.7269 | 30122.375 | 13663.844 | 0 | 51350.1201
5575 | 86.8608 | 90.2316 | 90.2316 | 87.8369 | 86.8608 | 1402.6 | 129066.4838 | 31269.894 | 14184.3714 | 0 | 51890.652
5576 | 75.7243 | 876.4084 | 78.6625 | 853.149 | 75.7243 | 1295.45 | 103953.2816 | 27260.7494 | 12365.7788 | 0 | 53351.5583
5577 | 84.1783 | 2431.6238 | 87.4445 | 2367.0898 | 84.1783 | 1442.8 | 128754.564 | 30304.185 | 13746.3151 | 0 | 46904.1442
5578 | 72.4879 | 3416.6008 | 75.3009 | 3325.926 | 72.4879 | 1336.95 | 102755.6412 | 26095.6589 | 11837.2808 | 0 | 48063.1296
5579 | 80.7865 | 3295.902 | 83.9219 | 3208.4306 | 80.7865 | 1027.25 | 87900.8135 | 29083.1531 | 13192.4414 | 0 | 78585.1032
5580 | 74.8706 | 3608.8586 | 77.7753 | 3513.0815 | 74.8706 | 946.45 | 75075.0275 | 26953.4294 | 12226.3751 | 0 | 78879.9599
5581 | 86.2801 | 4214.5347 | 89.6281 | 4102.6833 | 86.2801 | 964.35 | 88122.1045 | 31060.8304 | 14089.5378 | 0 | 89355.9695
5582 | 78.115 | 2456.2497 | 81.1462 | 2391.0621 | 78.115 | 1554.55 | 128671.5422 | 28121.3887 | 12756.1744 | 0 | 34796.3127
5583 | 78.5463 | 2696.465 | 81.595 | 2624.9022 | 78.5463 | 1562.75 | 130136.6371 | 28276.6623 | 12826.6082 | 0 | 34344.3628
5584 | 79.3432 | 2432.7592 | 82.4219 | 2368.1951 | 79.3432 | 1672.55 | 140671.8664 | 28563.5421 | 12956.7401 | 0 | 25980.9218
5585 | 88.3072 | 1319.8212 | 91.7337 | 1284.7938 | 88.3072 | 1866.6 | 174380.2424 | 31790.5808 | 14420.5607 | 0 | 11780.1763
5586 | 82.3435 | 271.394 | 85.5393 | 264.1913 | 82.3435 | 1849.2 | 160953.746 | 29643.6444 | 13446.6865 | 0 | 12417.3933
5587 | 97.2562 | 101.03 | 101.03 | 98.3487 | 97.2562 | 1840.15 | 189509.5648 | 35012.2405 | 15881.9413 | 0 | 15546.3716
5588 | 88.4546 | 91.8875 | 91.8875 | 89.4488 | 88.4546 | 1852.4 | 173702.6798 | 31843.6536 | 14444.6351 | 0 | 13055.898
5589 | 94.0328 | 97.6819 | 97.6819 | 95.0895 | 94.0328 | 1860.3 | 185508.9618 | 33851.8119 | 15355.558 | 0 | 13136.3837
5590 | 86.8608 | 90.2316 | 90.2316 | 87.8369 | 86.8608 | 1878.35 | 172650.4517 | 31269.894 | 14184.3714 | 0 | 10566.6184
5591 | 90.8453 | 94.3702 | 94.3702 | 91.8657 | 90.8453 | 1879.3 | 180519.7527 | 32704.2929 | 14835.0306 | 0 | 10964.9915
5592 | 84.4702 | 87.7478 | 87.7478 | 85.4191 | 84.4702 | 1860 | 166344.6612 | 30409.2548 | 13793.9758 | 0 | 11825.8
5593 | 93.2359 | 0 | 0 | 0 | 0 | 1828.6 | 0 | 0 | 0 | 110950.7479 | 0
5594 | 81.2826 | 14.6357 | 14.6357 | 14.2473 | 14.2473 | 1807.8 | 27307.1376 | 5129.0266 | 2326.5834 | 79772.0107 | 2707.9058
5595 | 92.439 | 96.0261 | 96.0261 | 93.4776 | 92.439 | 1708.5 | 168247.8002 | 33278.0524 | 15095.2943 | 0 | 26945.9685
5596 | 79.6888 | 82.7813 | 82.7813 | 80.5843 | 79.6888 | 1516.65 | 128770.3477 | 28687.9762 | 13013.1848 | 0 | 38517.5925
5597 | 90.0484 | 93.5423 | 93.5423 | 91.0597 | 90.0484 | 1682.7 | 161591.4893 | 32417.4131 | 14704.8988 | 0 | 28572.2304
5598 | 79.6888 | 82.7813 | 82.7813 | 80.5843 | 79.6888 | 1679.8 | 142791.5698 | 28687.9762 | 13013.1848 | 0 | 25516.361
5599 | 86.0639 | 89.4037 | 89.4037 | 87.031 | 86.0639 | 1708.5 | 156628.6616 | 30983.0143 | 14054.2395 | 0 | 25087.6352
5600 | 75.1595 | 551.6469 | 78.0755 | 537.0065 | 75.1595 | 1449.8 | 116179.0699 | 27057.4233 | 12273.5479 | 0 | 41352.762
5601 | 85.1346 | 1880.4506 | 88.4386 | 1830.5445 | 85.1346 | 1622.8 | 146877.0784 | 30648.4408 | 13902.4733 | 0 | 32112.7552
5602 | 74.1644 | 2674.6002 | 77.0419 | 2603.6178 | 74.1644 | 1612.2 | 127166.4457 | 26699.1822 | 12111.0457 | 0 | 28760.9524
5603 | 80.2656 | 3233.1541 | 83.3797 | 3147.3479 | 80.2656 | 1535.25 | 131108.5847 | 28895.6054 | 13107.3677 | 0 | 37303.4239
5604 | 72.995 | 3252.3387 | 75.8265 | 3166.0234 | 72.995 | 1136.7 | 88238.5618 | 26278.1862 | 11920.0772 | 0 | 63016.5504
5605 | 82.3325 | 3428.6114 | 85.5269 | 3337.618 | 82.3325 | 1111.35 | 97241.1692 | 29639.6998 | 13444.8972 | 0 | 73164.7756
5606 | 74.6694 | 2942.5287 | 77.5676 | 2864.4356 | 74.6694 | 1758.25 | 139672.0977 | 26880.9923 | 12193.5168 | 0 | 18051.333
5607 | 86.4494 | 2707.4524 | 89.8036 | 2635.5981 | 86.4494 | 1905.6 | 175107.0548 | 31121.7924 | 14117.1908 | 0 | 8160.8256
5608 | 80.9369 | 2070.9051 | 84.0777 | 2015.9444 | 80.9369 | 1899.6 | 163284.1622 | 29137.3016 | 13217.0038 | 0 | 8126.0697
5609 | 86.7502 | 1212.3464 | 90.1163 | 1180.1714 | 86.7502 | 1881.6 | 173390.3795 | 31230.0895 | 14166.3156 | 0 | 10271.2294
5610 | 79.3501 | 269.3766 | 82.4292 | 262.2275 | 79.3501 | 1854.15 | 156237.812 | 28566.0523 | 12957.8787 | 0 | 11573.2187
5611 | 96.4444 | 100.1865 | 100.1865 | 97.5276 | 96.4444 | 1845.15 | 189227.648 | 34719.9818 | 15749.3695 | 0 | 14934.3534
5612 | 87.6577 | 91.0595 | 91.0595 | 88.6429 | 87.6577 | 1852.4 | 172890.4317 | 31556.7738 | 14314.5032 | 0 | 12938.2773
5613 | 90.8453 | 94.3702 | 94.3702 | 91.8657 | 90.8453 | 1860.3 | 180164.0246 | 32704.2929 | 14835.0306 | 0 | 12691.0465
5614 | 86.0639 | 89.4037 | 89.4037 | 87.031 | 86.0639 | 1878.35 | 171905.5005 | 30983.0143 | 14054.2395 | 0 | 10469.6769
5615 | 92.439 | 96.0261 | 96.0261 | 93.4776 | 92.439 | 1879.3 | 184515.7985 | 33278.0524 | 15095.2943 | 0 | 11157.3873
5616 | 87.6577 | 91.0595 | 91.0595 | 88.6429 | 87.6577 | 1855 | 173062.9481 | 31556.7738 | 14314.5032 | 0 | 12710.3672
5617 | 94.0328 | 0 | 0 | 0 | 0 | 1821.1 | 0 | 0 | 0 | 111899.0449 | 0
5618 | 86.8608 | 9.6837 | 9.6837 | 9.4267 | 9.4267 | 1800.35 | 18111.7288 | 3393.6252 | 1539.3861 | 92146.5553 | 1861.1373
5619 | 93.2359 | 96.854 | 96.854 | 94.2835 | 93.2359 | 1790.55 | 178098.5313 | 33564.9321 | 15225.4262 | 0 | 19528.264
5620 | 79.6888 | 82.7813 | 82.7813 | 80.5843 | 79.6888 | 1778.2 | 151277.049 | 28687.9762 | 13013.1848 | 0 | 17674.9809
5621 | 88.4546 | 91.8875 | 91.8875 | 89.4488 | 88.4546 | 1777.7 | 167842.203 | 31843.6536 | 14444.6351 | 0 | 19663.4561
5622 | 86.0639 | 89.4037 | 89.4037 | 87.031 | 86.0639 | 1774.8 | 162966.9379 | 30983.0143 | 14054.2395 | 0 | 19381.5967
5623 | 88.4546 | 91.8864 | 91.8864 | 89.4478 | 88.4546 | 1755.1 | 165645.417 | 31843.6536 | 14444.6351 | 0 | 21662.3846
5624 | 78.9726 | 680.655 | 82.0375 | 662.5908 | 78.9726 | 1526.1 | 128475.6227 | 28430.143 | 12896.2288 | 0 | 37425.1244
5625 | 84.4114 | 1896.8149 | 87.6865 | 1846.4744 | 84.4114 | 1677.8 | 150571.3876 | 30388.0974 | 13784.3786 | 0 | 27197.3472
5626 | 75.3169 | 2740.3763 | 78.2397 | 2667.6482 | 75.3169 | 1685.15 | 135169.99 | 27114.0821 | 12299.2489 | 0 | 23713.5243
5627 | 86.3179 | 3150.0923 | 89.6675 | 3066.4906 | 86.3179 | 1604.35 | 147309.3699 | 31074.4572 | 14095.7191 | 0 | 34151.6917
5628 | 74.6116 | 3394.7661 | 77.5073 | 3304.6709 | 74.6116 | 1550.5 | 123121.7475 | 26860.1935 | 12184.0822 | 0 | 33537.9361
5629 | 87.3011 | 3205.7078 | 90.6897 | 3120.6301 | 87.3011 | 1528.35 | 141827.4662 | 31428.3951 | 14256.2692 | 0 | 41175.5627
5630 | 82.3166 | 1214.0376 | 85.5103 | 1181.8177 | 82.3166 | 1802.85 | 157875.555 | 29633.9622 | 13442.2945 | 0 | 16228.7101
5631 | 88.9845 | 1800.6122 | 92.438 | 1752.8249 | 88.9845 | 1905.6 | 180446.7176 | 32034.4286 | 14531.1728 | 0 | 8400.1391
5632 | 81.1182 | 1559.8412 | 84.2658 | 1518.4438 | 81.1182 | 1897.1 | 163511.1478 | 29202.5668 | 13246.6088 | 0 | 8347.067
5633 | 82.9302 | 546.1111 | 86.1491 | 531.6176 | 82.9302 | 1876.6 | 165398.2713 | 29854.8596 | 13542.496 | 0 | 10233.5824
5634 | 82.6104 | 155.9755 | 85.8157 | 151.836 | 82.6104 | 1854.2 | 162760.8768 | 29739.7491 | 13490.2806 | 0 | 12044.5984
5635 | 95.6336 | 99.3451 | 99.3451 | 96.7085 | 95.6336 | 1845.15 | 187498.3077 | 34428.0816 | 15616.9604 | 0 | 14808.8568
5636 | 90.8453 | 94.3702 | 94.3702 | 91.8657 | 90.8453 | 1852.4 | 179005.7604 | 32704.2929 | 14835.0306 | 0 | 13408.722
5637 | 93.2359 | 96.854 | 96.854 | 94.2835 | 93.2359 | 1860.3 | 184548.3273 | 33564.9321 | 15225.4262 | 0 | 13025.0584
5638 | 88.4546 | 91.8875 | 91.8875 | 89.4488 | 88.4546 | 1878.35 | 176406.153 | 31843.6536 | 14444.6351 | 0 | 10760.5013
5639 | 97.2204 | 100.9926 | 100.9926 | 98.3123 | 97.2204 | 1879.3 | 194111.9886 | 34999.331 | 15876.0854 | 0 | 11734.454
5640 | 90.0484 | 0 | 0 | 0 | 0 | 1855 | 0 | 0 | 0 | 165058.6617 | 0
5641 | 92.439 | 0 | 0 | 0 | 0 | 1818.6 | 0 | 0 | 0 | 169440.75 | 0
5642 | 86.0639 | 80.0628 | 80.0628 | 77.9379 | 77.9379 | 1777.85 | 147896.9225 | 28057.6575 | 12727.2652 | 14894.9415 | 17121.5448
5643 | 90.8453 | 94.3702 | 94.3702 | 91.8657 | 90.8453 | 1721.45 | 166667.3182 | 32704.2929 | 14835.0306 | 0 | 25304.8747
5644 | 86.8608 | 90.2316 | 90.2316 | 87.8369 | 86.8608 | 1693 | 156985.964 | 31269.894 | 14184.3714 | 0 | 26666.2708
5645 | 92.439 | 96.0261 | 96.0261 | 93.4776 | 92.439 | 1666.4 | 164312.2272 | 33278.0524 | 15095.2943 | 0 | 30837.6504
5646 | 85.267 | 88.5758 | 88.5758 | 86.225 | 85.267 | 1663.5 | 151236.3598 | 30696.1345 | 13924.1077 | 0 | 28692.3455
5647 | 76.5013 | 79.4706 | 79.4706 | 77.3615 | 76.5013 | 1708.5 | 139144.6622 | 27540.4571 | 12492.6574 | 0 | 22300.0415
5648 | 82.453 | 538.8021 | 85.6526 | 524.5025 | 82.453 | 1477 | 129361.2139 | 29683.0904 | 13464.5796 | 0 | 43122.9341
5649 | 644.2323 | 1887.0782 | 669.2313 | 1836.9961 | 644.2323 | 1643.05 | 1128391.0177 | 231923.6403 | 105203.1402 | 0 | 229958.7317
5650 | 550.7832 | 2702.195 | 572.156 | 2630.4802 | 550.7832 | 1640.55 | 960886.9522 | 198281.9678 | 89942.9037 | 0 | 197979.0371
5651 | 872.9741 | 2946.9644 | 906.8506 | 2868.7536 | 872.9741 | 1459.55 | 1352988.3668 | 314270.683 | 142556.6737 | 0 | 471798.8628
5652 | 946.1464 | 2115.6329 | 982.861 | 2059.4851 | 946.1464 | 1466.9 | 1472817.537 | 340612.6999 | 154505.7053 | 0 | 504390.6398
5653 | 1239.5337 | 1145.5108 | 1145.5108 | 1115.1095 | 1115.1095 | 1484.8 | 1753884.9862 | 401439.4346 | 182097.388 | 228069.5555 | 556873.4976
5654 | 1165.2976 | 1210.5171 | 1210.5171 | 1178.3906 | 1165.2976 | 1513.45 | 1874169.5162 | 419507.1446 | 190293.102 | 0 | 566975.2553
5655 | 1376.3664 | 193.4826 | 193.4826 | 188.3477 | 188.3477 | 1557.05 | 312561.0226 | 67805.1562 | 30757.1723 | 2177638.394 | 81663.5909
5656 | 885.9086 | 109.0246 | 109.0246 | 106.1312 | 106.1312 | 1546.05 | 174432.507 | 38207.2254 | 17331.2219 | 1429332.0289 | 47159.0497
5657 | 1355.6593 | 29.02 | 29.02 | 28.2499 | 28.2499 | 1814.55 | 54489.7666 | 10169.9543 | 4613.2043 | 2433141.4427 | 5128.0634
5658 | 1090.8972 | 65.7698 | 65.7698 | 64.0243 | 64.0243 | 1816.7 | 123658.6862 | 23048.7657 | 10455.1762 | 1882257.8457 | 11487.411
5659 | 1122.6312 | 0 | 0 | 0 | 0 | 1835.15 | 0 | 0 | 0 | 2057783.0483 | 0
5660 | 1206.4888 | 0 | 0 | 0 | 0 | 1851.9 | 0 | 0 | 0 | 2211493.9264 | 0
5661 | 1114.0497 | 0 | 0 | 0 | 0 | 1850.3 | 0 | 0 | 0 | 2042053.1771 | 0
5662 | 1332.3971 | 148.869 | 148.869 | 144.9181 | 144.9181 | 1873.3 | 288839.6229 | 52170.5261 | 23665.1303 | 2176648.9851 | 18157.1236
5663 | 1107.6746 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1869.3 | 1192557.7366 | 215514.4963 | 97759.7701 | 933039.631 | 77374.4
5664 | 162.5652 | 168.8733 | 168.8733 | 164.3915 | 162.5652 | 1847.5 | 320269.6673 | 58523.4714 | 26546.8969 | 0 | 24791.1625
5665 | 108.3768 | 0 | 0 | 0 | 0 | 1820 | 0 | 0 | 0 | 128968.3907 | 0
5666 | 94.0328 | 0 | 0 | 0 | 0 | 1772 | 0 | 0 | 0 | 111899.0449 | 0
5667 | 105.1892 | 0 | 0 | 0 | 0 | 1625.8 | 0 | 0 | 0 | 125175.2027 | 0
5668 | 101.2048 | 0 | 0 | 0 | 0 | 1494.1 | 0 | 0 | 0 | 120433.7178 | 0
5669 | 105.1892 | 0 | 0 | 0 | 0 | 1484.75 | 0 | 0 | 0 | 125175.2027 | 0
5670 | 94.8297 | 0 | 0 | 0 | 0 | 1475.65 | 0 | 0 | 0 | 112847.3419 | 0
5671 | 86.8608 | 90.2316 | 90.2316 | 87.8369 | 86.8608 | 1714.1 | 158220.1371 | 31269.894 | 14184.3714 | 0 | 24833.5075
5672 | 82.0825 | 904.9911 | 85.2682 | 880.9731 | 82.0825 | 1451.7 | 126726.8819 | 29549.6913 | 13404.0683 | 0 | 45005.8215
5673 | 832.2691 | 2266.9369 | 864.565 | 2206.7736 | 832.2691 | 1465.3 | 1297669.4331 | 299616.8647 | 135909.5389 | 0 | 445014.271
5674 | 1035.63 | 3450.0503 | 1075.8174 | 3358.4878 | 1035.63 | 1466 | 1614956.2805 | 372826.787 | 169118.3731 | 0 | 553026.4008
5675 | 888.0562 | 3967.614 | 922.5168 | 3862.3157 | 888.0562 | 1442.9 | 1359953.1544 | 319700.2411 | 145019.5816 | 0 | 494736.1231
5676 | 1347.1615 | 4236.8254 | 1399.4383 | 4124.3824 | 1347.1615 | 1428.8 | 2044497.4627 | 484978.1267 | 219991.4669 | 0 | 769498.6277
5677 | 1336.4483 | 4209.9515 | 1388.3085 | 4098.2217 | 1336.4483 | 1451.25 | 2067126.8381 | 481121.3869 | 218242.0069 | 0 | 733376.003
5678 | 1189.8149 | 3892.7899 | 1235.9855 | 3789.4774 | 1189.8149 | 1467.75 | 1858049.7219 | 428333.359 | 194296.7709 | 0 | 633278.9731
5679 | 1475.6089 | 2387.1982 | 1532.8696 | 2323.8433 | 1475.6089 | 1468.4 | 2302197.9437 | 531219.1997 | 240966.9314 | 0 | 784433.6849
5680 | 1639.9322 | 2431.0265 | 1703.5691 | 2366.5083 | 1639.9322 | 1476.35 | 2575873.4327 | 590375.5996 | 267800.9317 | 0 | 858750.5075
5681 | 1706.823 | 986.3191 | 986.3191 | 960.1428 | 960.1428 | 1721.65 | 1757749.368 | 345651.3958 | 156791.3137 | 1368664.9034 | 261602.5155
5682 | 1428.5228 | 121.5859 | 121.5859 | 118.359 | 118.359 | 1816.65 | 228362.3791 | 42609.2546 | 19328.0313 | 2401530.0888 | 21242.0142
5683 | 1533.5207 | 0 | 0 | 0 | 0 | 1819.15 | 0 | 0 | 0 | 5210903.5017 | 0
5684 | 1655.1368 | 0 | 0 | 0 | 0 | 1825.5 | 0 | 0 | 0 | 5624155.0129 | 0
5685 | 1609.7142 | 0 | 0 | 0 | 0 | 1826.05 | 0 | 0 | 0 | 5469808.9196 | 0
5686 | 1722.0755 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1837.4 | 604549.0911 | 111351.8261 | 50510.4255 | 4800574.8993 | 49735.1124
5687 | 1463.8837 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1833.55 | 1169318.7687 | 215514.4963 | 97759.7701 | 2940059.3402 | 98538.4
5688 | 1754.7479 | 0 | 0 | 0 | 0 | 1816.05 | 0 | 0 | 0 | 3216452.8585 | 0
5689 | 1349.1318 | 0 | 0 | 0 | 0 | 1632.1 | 0 | 0 | 0 | 1605466.8051 | 0
5690 | 1326.022 | 0 | 0 | 0 | 0 | 1772.8 | 0 | 0 | 0 | 1577966.1931 | 0
5691 | 1411.2891 | 0 | 0 | 0 | 0 | 1766.75 | 0 | 0 | 0 | 1679433.9707 | 0
5692 | 1294.1465 | 0 | 0 | 0 | 0 | 1769.7 | 0 | 0 | 0 | 1540034.3124 | 0
5693 | 1482.2121 | 0 | 0 | 0 | 0 | 1763.25 | 0 | 0 | 0 | 1763832.4026 | 0
5694 | 1483.009 | 0 | 0 | 0 | 0 | 1763.5 | 0 | 0 | 0 | 1764780.6993 | 0
5695 | 1287.7714 | 310.479 | 310.479 | 302.2391 | 302.2391 | 1745.5 | 560005.4376 | 108806.0611 | 49355.6383 | 1806480.7379 | 75292.807
5696 | 1284.4902 | 1126.4394 | 1126.4394 | 1096.5443 | 1096.5443 | 1227.75 | 1425914.0745 | 394755.9369 | 179065.6792 | 344504.869 | 828893.7653
5697 | 1520.7915 | 1579.806 | 1579.806 | 1537.8788 | 1520.7915 | 294.25 | 471915.4162 | 547484.9234 | 248345.2444 | 0 | 2594090.0227
5698 | 1079.7616 | 1810.3468 | 1121.6609 | 1762.3012 | 1079.7616 | 658.15 | 751796.0364 | 388714.1882 | 176325.0748 | 0 | 1448878.1486
5699 | 1397.4561 | 2781.6584 | 1451.6839 | 2707.8347 | 1397.4561 | 1023.15 | 1511485.9646 | 503084.1841 | 228204.5757 | 0 | 1365104.959
5700 | 1300.2516 | 3521.1243 | 1350.7069 | 3427.6755 | 1300.2516 | 1024.65 | 1409222.8467 | 468090.5908 | 212331.093 | 0 | 1268200.438
5701 | 1512.0147 | 3287.3381 | 1570.6884 | 3200.094 | 1512.0147 | 1026.5 | 1646362.7408 | 544325.3017 | 246912.0049 | 0 | 1471946.3367
5702 | 1330.6818 | 2852.5765 | 1382.3188 | 2776.8707 | 1330.6818 | 1041.3 | 1472269.1515 | 479045.453 | 217300.3402 | 0 | 1275724.6551
5703 | 1355.5716 | 2543.6526 | 1408.1736 | 2476.1455 | 1355.5716 | 894.35 | 1287896.8171 | 488005.7839 | 221364.8459 | 0 | 1498787.7639
5704 | 1598.3855 | 1136.8783 | 1136.8783 | 1106.7062 | 1106.7062 | 704.6 | 829873.8313 | 398414.2227 | 180725.1182 | 901248.1254 | 1403300.343
5705 | 1495.9604 | 545.5719 | 545.5719 | 531.0928 | 531.0928 | 1329.95 | 752673.5469 | 191193.3941 | 86727.4479 | 1768602.4127 | 348331.523
5706 | 1298.7306 | 168.7092 | 168.7092 | 164.2317 | 164.2317 | 1770.7 | 309779.0054 | 59123.4169 | 26819.0388 | 2079536.424 | 36861.5801
5707 | 1402.2623 | 0 | 0 | 0 | 0 | 1766.25 | 0 | 0 | 0 | 4764887.2954 | 0
5708 | 1392.1637 | 0 | 0 | 0 | 0 | 1816.3 | 0 | 0 | 0 | 4730572.3647 | 0
5709 | 1202.5043 | 0 | 0 | 0 | 0 | 1771.6 | 0 | 0 | 0 | 4086109.7303 | 0
5710 | 1352.3193 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1774.25 | 584755.993 | 111351.8261 | 50510.4255 | 3544143.5424 | 69051.0555
5711 | 1295.7403 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1742 | 1111173.6868 | 215514.4963 | 97759.7701 | 2368708.0126 | 152736
5712 | 1243.9425 | 0 | 0 | 0 | 0 | 1673.35 | 0 | 0 | 0 | 2280146.6447 | 0
5713 | 1173.8164 | 0 | 0 | 0 | 0 | 1795.1 | 0 | 0 | 0 | 1396841.4672 | 0
5714 | 1220.8328 | 0 | 0 | 0 | 0 | 1731.25 | 0 | 0 | 0 | 1452790.9904 | 0
5715 | 1220.0359 | 0 | 0 | 0 | 0 | 1721.45 | 0 | 0 | 0 | 1451842.6924 | 0
5716 | 899.6868 | 0 | 0 | 0 | 0 | 1667.2 | 0 | 0 | 0 | 1070627.3026 | 0
5717 | 1117.2373 | 0 | 0 | 0 | 0 | 1596.75 | 0 | 0 | 0 | 1329512.381 | 0
5718 | 1305.3029 | 0 | 0 | 0 | 0 | 1716.5 | 0 | 0 | 0 | 1553310.4712 | 0
5719 | 1147.519 | 382.3518 | 382.3518 | 372.2044 | 372.2044 | 1782.6 | 705814.1016 | 133993.5897 | 60780.9811 | 1421151.7206 | 79205.5594
5720 | 929.5402 | 965.6116 | 965.6116 | 939.9848 | 929.5402 | 1602.75 | 1582758.4863 | 334634.4843 | 151793.9202 | 0 | 369259.765
5721 | 1210.9693 | 1257.9614 | 1257.9614 | 1224.5758 | 1210.9693 | 1783.25 | 2294796.0165 | 435948.9412 | 197751.2836 | 0 | 262477.5307
5722 | 1135.0278 | 2352.7432 | 1179.0725 | 2290.3026 | 1135.0278 | 1773.6 | 2138495.6166 | 408610.017 | 185350.0438 | 0 | 256970.2996
5723 | 1545.1075 | 4023.4892 | 1605.0645 | 3916.708 | 1545.1075 | 1696.95 | 2785130.4619 | 556238.7011 | 252316.0552 | 0 | 468244.8288
5724 | 1332.948 | 1686.9275 | 1384.6727 | 1642.1574 | 1332.948 | 1623.45 | 2300552.6923 | 479861.2674 | 217670.4027 | 0 | 501921.5562
5725 | 1136.3975 | 4243.7148 | 1180.4946 | 4131.0889 | 1136.3975 | 1487.4 | 1792857.1669 | 409103.0914 | 185573.7078 | 0 | 582517.3462
5726 | 1310.148 | 2653.9903 | 1360.988 | 2583.5549 | 1310.148 | 1790.8 | 2489862.2644 | 471653.2789 | 213947.1679 | 0 | 274082.961
5727 | 1355.743 | 3267.4492 | 1408.3523 | 3180.7329 | 1355.743 | 1873.55 | 2692910.2724 | 488067.4631 | 221392.8242 | 0 | 171433.6964
5728 | 1265.597 | 2106.5132 | 1314.7082 | 2050.6075 | 1265.597 | 1904.6 | 2555838.9575 | 455614.9074 | 206671.9844 | 0 | 120737.9505
5729 | 1372.3541 | 63.1199 | 63.1199 | 61.4447 | 61.4447 | 1886.6 | 122549.1407 | 22120.0875 | 10033.9175 | 2402896.9309 | 6820.443
5730 | 1424.6399 | 213.0516 | 213.0516 | 207.3973 | 207.3973 | 1854.2 | 407209.7314 | 74663.0314 | 33867.9806 | 2231205.6997 | 29598.858
5731 | 1131.4817 | 0 | 0 | 0 | 0 | 1845.15 | 0 | 0 | 0 | 3844774.7215 | 0
5732 | 1318.85 | 0 | 0 | 0 | 0 | 1852.4 | 0 | 0 | 0 | 4481452.3578 | 0
5733 | 1212.067 | 0 | 0 | 0 | 0 | 1860.3 | 0 | 0 | 0 | 4118603.6456 | 0
5734 | 1363.4758 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1878.35 | 614940.938 | 111351.8261 | 50510.4255 | 3582053.1085 | 37209.5721
5735 | 1298.9278 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1879.25 | 1189279.8703 | 215514.4963 | 97759.7701 | 2379539.3177 | 71484
5736 | 502.0396 | 0 | 0 | 0 | 0 | 1854.95 | 0 | 0 | 0 | 920238.5562 | 0
5737 | 307.5989 | 0 | 0 | 0 | 0 | 1821.1 | 0 | 0 | 0 | 366042.6384 | 0
5738 | 222.3318 | 0 | 0 | 0 | 0 | 1745.5 | 0 | 0 | 0 | 264574.8604 | 0
5739 | 304.4113 | 0 | 0 | 0 | 0 | 1735.7 | 0 | 0 | 0 | 362249.4505 | 0
5740 | 233.4883 | 0 | 0 | 0 | 0 | 1762.9 | 0 | 0 | 0 | 277851.0183 | 0
5741 | 283.6922 | 0 | 0 | 0 | 0 | 1757.4 | 0 | 0 | 0 | 337593.7287 | 0
5742 | 279.7078 | 0 | 0 | 0 | 0 | 1779.8 | 0 | 0 | 0 | 332852.2438 | 0
5743 | 278.114 | 288.9061 | 288.9061 | 281.2387 | 278.114 | 1782.6 | 527685.264 | 100121.0369 | 45416.0148 | 0 | 60461.9817
5744 | 207.0754 | 912.0581 | 215.1115 | 887.8526 | 207.0754 | 1797.65 | 395233.4929 | 74547.1405 | 33815.4113 | 0 | 41901.7052
5745 | 1378.0269 | 1431.501 | 1431.501 | 1393.5097 | 1378.0269 | 1822.8 | 2669094.996 | 496089.697 | 225031.7986 | 0 | 244186.2072
5746 | 1300.4519 | 3260.5962 | 1350.9157 | 3174.0617 | 1300.4519 | 1810.65 | 2497251.3026 | 468162.6696 | 212363.7887 | 0 | 246240.5597
5747 | 1608.7589 | 3930.297 | 1671.1865 | 3825.989 | 1608.7589 | 1696.95 | 2895884.1594 | 579153.222 | 262710.3365 | 0 | 487534.3998
5748 | 1772.0822 | 4178.483 | 1840.8472 | 4067.5884 | 1772.0822 | 1623.45 | 3062516.4164 | 637949.5877 | 289381.0213 | 0 | 667277.5479
5749 | 1617.9401 | 3532.521 | 1680.7238 | 3438.7698 | 1617.9401 | 1568.4 | 2695729.1436 | 582458.4353 | 264209.618 | 0 | 698302.9463
5750 | 1533.0237 | 2394.5436 | 1592.5126 | 2330.9937 | 1533.0237 | 1882.05 | 3064249.9726 | 551888.528 | 250342.7684 | 0 | 180820.1441
5751 | 1780.7354 | 2539.1172 | 1849.837 | 2471.7304 | 1780.7354 | 1910.6 | 3620190.4693 | 641064.7433 | 290794.0905 | 0 | 159197.7446
5752 | 1349.0361 | 297.2851 | 297.2851 | 289.3954 | 289.3954 | 1909.6 | 586347.3832 | 104182.3286 | 47258.2618 | 1942321.5603 | 25607.8792
5753 | 1613.9387 | 380.0987 | 380.0987 | 370.011 | 370.011 | 1886.55 | 740587.5621 | 133203.9767 | 60422.8039 | 2280119.4315 | 41089.7748
5754 | 1295.9295 | 73.2918 | 73.2918 | 71.3467 | 71.3467 | 1854.2 | 140296.8447 | 25684.8138 | 11650.9169 | 2244660.2981 | 10182.3804
5755 | 1388.6465 | 0 | 0 | 0 | 0 | 1845.15 | 0 | 0 | 0 | 4718620.6983 | 0
5756 | 1267.0523 | 0 | 0 | 0 | 0 | 1852.4 | 0 | 0 | 0 | 4305443.6542 | 0
5757 | 1465.4775 | 0 | 0 | 0 | 0 | 1860.3 | 0 | 0 | 0 | 4979692.3751 | 0
5758 | 1438.3833 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1878.35 | 615458.3084 | 111351.8261 | 50510.4255 | 3836588.7732 | 37209.5721
5759 | 1352.3193 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1879.3 | 1192495.2087 | 215514.4963 | 97759.7701 | 2560963.6721 | 71454.4
5760 | 574.5564 | 0 | 0 | 0 | 0 | 1859.95 | 0 | 0 | 0 | 1053161.9032 | 0
5761 | 496.4614 | 0 | 0 | 0 | 0 | 1828.55 | 0 | 0 | 0 | 590789.0252 | 0
5762 | 496.4614 | 0 | 0 | 0 | 0 | 1805.35 | 0 | 0 | 0 | 590789.0252 | 0
5763 | 502.0396 | 0 | 0 | 0 | 0 | 1795.55 | 0 | 0 | 0 | 597427.1041 | 0
5764 | 419.9601 | 0 | 0 | 0 | 0 | 1785.7 | 0 | 0 | 0 | 499752.5141 | 0
5765 | 483.7112 | 0 | 0 | 0 | 0 | 1777.7 | 0 | 0 | 0 | 575616.2734 | 0
5766 | 465.3827 | 0 | 0 | 0 | 0 | 1777.3 | 0 | 0 | 0 | 553805.4426 | 0
5767 | 470.1641 | 315.4881 | 315.4881 | 307.1152 | 307.1152 | 1782.6 | 583877.1893 | 110561.4849 | 50151.918 | 298868.4841 | 65354.5706
5768 | 384.0224 | 516.902 | 398.9239 | 503.1837 | 384.0224 | 1526.65 | 624729.9781 | 138248.0745 | 62710.8627 | 0 | 181777.0168
5769 | 1040.75 | 1362.1732 | 1081.136 | 1326.0219 | 1040.75 | 1783.25 | 1968011.8349 | 374669.9896 | 169954.4703 | 0 | 225582.5562
5770 | 1686.0651 | 2268.5574 | 1751.4923 | 2208.3511 | 1686.0651 | 1604.3 | 2866597.5217 | 606983.4277 | 275334.4271 | 0 | 667175.951
5771 | 1865.857 | 3109.0252 | 1938.2611 | 3026.5134 | 1865.857 | 1490.1 | 2946902.3964 | 671708.5222 | 304694.4491 | 0 | 951400.4874
5772 | 1807.6941 | 2661.4417 | 1877.8411 | 2590.8084 | 1807.6941 | 1575.5 | 3020704.6273 | 650769.8857 | 295196.4509 | 0 | 767366.1569
5773 | 1599.518 | 4264.8815 | 1661.5869 | 4151.6938 | 1599.518 | 1593.4 | 2701511.845 | 575826.4926 | 261201.2951 | 0 | 650364.033
5774 | 1650.484 | 2207.1931 | 1714.5306 | 2148.6154 | 1650.484 | 1882.05 | 3296380.3395 | 594174.2461 | 269524.04 | 0 | 194674.5898
5775 | 1952.3423 | 2174.933 | 2028.1032 | 2117.2115 | 1952.3423 | 1910.6 | 3966062.287 | 702843.2244 | 318817.496 | 0 | 174539.4007
5776 | 1917.6398 | 821.5252 | 821.5252 | 799.7224 | 799.7224 | 1909.55 | 1622470.5636 | 287900.0636 | 130594.6678 | 2049142.5961 | 70804.8027
5777 | 1638.3992 | 116.3285 | 116.3285 | 113.2412 | 113.2412 | 1886.6 | 226450.7292 | 40766.824 | 18492.2844 | 2795614.6673 | 12569.9364
5778 | 1789.8428 | 120.5336 | 120.5336 | 117.3347 | 117.3347 | 1854.2 | 230497.3235 | 42240.4772 | 19160.7498 | 3065707.4867 | 16745.4216
5779 | 1557.9215 | 0 | 0 | 0 | 0 | 1845.15 | 0 | 0 | 0 | 5293817.1381 | 0
5780 | 1417.6642 | 0 | 0 | 0 | 0 | 1852.4 | 0 | 0 | 0 | 4817222.8055 | 0
5781 | 1755.5448 | 0 | 0 | 0 | 0 | 1860.3 | 0 | 0 | 0 | 5965341.1115 | 0
5782 | 1519.6659 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1878.35 | 613089.6129 | 111351.8261 | 50510.4255 | 4112787.0446 | 37209.5721
5783 | 1699.7626 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1879.3 | 1188928.9357 | 215514.4963 | 97759.7701 | 3741575.8934 | 71454.4
5784 | 524.3525 | 0 | 0 | 0 | 0 | 1860 | 0 | 0 | 0 | 961138.0476 | 0
5785 | 475.7423 | 0 | 0 | 0 | 0 | 1831.1 | 0 | 0 | 0 | 566133.3034 | 0
5786 | 485.3049 | 0 | 0 | 0 | 0 | 1807.85 | 0 | 0 | 0 | 577512.8674 | 0
5787 | 448.6481 | 0 | 0 | 0 | 0 | 1695.05 | 0 | 0 | 0 | 533891.2058 | 0
5788 | 408.8037 | 0 | 0 | 0 | 0 | 1533.25 | 0 | 0 | 0 | 486476.3562 | 0
5789 | 496.4614 | 0 | 0 | 0 | 0 | 1467 | 0 | 0 | 0 | 590789.0252 | 0
5790 | 478.9298 | 0 | 0 | 0 | 0 | 1418.95 | 0 | 0 | 0 | 569926.4914 | 0
5791 | 400.8348 | 260.8314 | 260.8314 | 253.9091 | 253.9091 | 1527.65 | 412154.1202 | 91407.27 | 41463.3533 | 269314.7991 | 117396.9243
5792 | 182.8679 | 337.0869 | 189.9641 | 328.1408 | 182.8679 | 1481.95 | 288361.53 | 65832.4506 | 29862.331 | 0 | 94734.725
5793 | 1356.1404 | 1408.7657 | 1408.7657 | 1371.3778 | 1356.1404 | 1701.2 | 2451008.1232 | 488210.5444 | 221457.7275 | 0 | 405214.7518
5794 | 1493.0687 | 2355.095 | 1551.0072 | 2292.5921 | 1493.0687 | 1802.1 | 2853607.4885 | 537504.7352 | 243818.1202 | 0 | 295478.2975
5795 | 1601.832 | 2944.9533 | 1663.9907 | 2866.7958 | 1601.832 | 1658.5 | 2815841.9158 | 576659.5196 | 261579.1654 | 0 | 547025.6277
5796 | 1394.3631 | 3131.6047 | 1448.4709 | 3048.4936 | 1394.3631 | 1704.3 | 2520726.7721 | 501970.7322 | 227699.5016 | 0 | 412313.182
5797 | 1717.3001 | 3084.1334 | 1783.9394 | 3002.2822 | 1717.3001 | 1762.15 | 3206309.1553 | 618228.0385 | 280435.1075 | 0 | 408459.8304
5798 | 1250.3824 | 3192.8329 | 1298.9038 | 3108.0968 | 1250.3824 | 1790.8 | 2370432.8092 | 450137.6554 | 204187.442 | 0 | 261579.9931
5799 | 1121.1221 | 2668.8348 | 1164.6279 | 2598.0054 | 1121.1221 | 1873.55 | 2216739.4116 | 403603.965 | 183079.243 | 0 | 141765.8927
5800 | 1607.7798 | 1137.2679 | 1137.2679 | 1107.0854 | 1107.0854 | 1876.8 | 2194133.5479 | 398550.7395 | 180787.0438 | 917772.8087 | 133507.7744
5801 | 1448.2039 | 288.4023 | 288.4023 | 280.7483 | 280.7483 | 1876.6 | 556935.8492 | 101069.3819 | 45846.1946 | 2139946.1496 | 33911.4306
5802 | 1364.7797 | 52.0909 | 52.0909 | 50.7084 | 50.7084 | 1844.2 | 98715.3079 | 18255.0243 | 8280.6819 | 2408692.6288 | 7733.133
5803 | 1446.5205 | 0 | 0 | 0 | 0 | 1842.65 | 0 | 0 | 0 | 4915276.5774 | 0
5804 | 1027.9858 | 0 | 0 | 0 | 0 | 1852.4 | 0 | 0 | 0 | 3493095.7926 | 0
5805 | 1208.0826 | 0 | 0 | 0 | 0 | 1860.3 | 0 | 0 | 0 | 4105064.5151 | 0
5806 | 1391.3668 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1878.35 | 613051.6039 | 111351.8261 | 50510.4255 | 3676827.0256 | 37209.5721
5807 | 960.2503 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1879.3 | 1186225.929 | 215514.4963 | 97759.7701 | 1228713.1832 | 71454.4
5808 | 1379.4135 | 0 | 0 | 0 | 0 | 1860 | 0 | 0 | 0 | 2528464.9858 | 0
5809 | 1115.6435 | 0 | 0 | 0 | 0 | 1718.1 | 0 | 0 | 0 | 2044974.5703 | 0
5810 | 1562.6978 | 0 | 0 | 0 | 0 | 1805.35 | 0 | 0 | 0 | 2864425.0931 | 0
5811 | 1405.7108 | 0 | 0 | 0 | 0 | 1795.55 | 0 | 0 | 0 | 2576667.9569 | 0
5812 | 1476.6339 | 0 | 0 | 0 | 0 | 1629.55 | 0 | 0 | 0 | 2706669.913 | 0
5813 | 1177.8008 | 0 | 0 | 0 | 0 | 1536.15 | 0 | 0 | 0 | 2158908.8664 | 0
5814 | 1127.5968 | 0 | 0 | 0 | 0 | 1509.3 | 0 | 0 | 0 | 2066885.0114 | 0
5815 | 1133.1751 | 331.9469 | 331.9469 | 323.1373 | 323.1373 | 1536.05 | 526885.8345 | 116329.41 | 52768.3129 | 1484799.3056 | 146748.3129
5816 | 181.302 | 950.5697 | 188.3374 | 925.3421 | 181.302 | 1279.9 | 246068.1145 | 65268.7318 | 29606.622 | 0 | 130555.5939
5817 | 479.2755 | 1310.0117 | 497.8742 | 1275.2447 | 479.2755 | 1489.85 | 757563.5219 | 172539.171 | 78265.6851 | 0 | 244502.3836
5818 | 453.9145 | 3412.5848 | 471.528 | 3322.0166 | 453.9145 | 1520.8 | 731994.7324 | 163409.2226 | 74124.239 | 0 | 217515.8319
5819 | 496.7951 | 3904.1565 | 516.073 | 3800.5423 | 496.7951 | 1442.45 | 760285.1254 | 178846.2226 | 81126.6337 | 0 | 276988.0872
5820 | 414.3719 | 4143.2717 | 430.4516 | 4033.3115 | 414.3719 | 1457.3 | 640290.8623 | 149173.8902 | 67666.9341 | 0 | 224879.6395
5821 | 318.7732 | 4120.8688 | 331.1429 | 4011.5032 | 318.7732 | 1475.2 | 497832.1122 | 114758.3596 | 52055.667 | 0 | 167292.1864
5822 | 334.3604 | 3801.4956 | 347.3348 | 3700.606 | 334.3604 | 1539 | 546140.0918 | 120369.7277 | 54601.0459 | 0 | 154140.1235
5823 | 406.4429 | 3239.0566 | 422.2149 | 3153.0938 | 406.4429 | 1748.6 | 752650.0034 | 146319.4365 | 66372.1222 | 0 | 102179.7399
5824 | 328.2074 | 2405.6204 | 340.944 | 2341.7766 | 328.2074 | 1825.5 | 634064.5965 | 118154.6573 | 53596.2654 | 0 | 57272.1881
5825 | 412.0002 | 1284.5153 | 427.9886 | 1250.425 | 412.0002 | 1876.6 | 817971.4675 | 148320.0643 | 67279.6292 | 0 | 50840.822
5826 | 284.013 | 211.5495 | 211.5495 | 205.9351 | 205.9351 | 1784.35 | 389580.083 | 74136.6227 | 33629.1958 | 143116.7789 | 43470.5113
5827 | 303.3544 | 0 | 0 | 0 | 0 | 1840.15 | 0 | 0 | 0 | 556048.67 | 0
5828 | 260.5825 | 0 | 0 | 0 | 0 | 1852.4 | 0 | 0 | 0 | 477647.6316 | 0
5829 | 203.2065 | 0 | 0 | 0 | 0 | 1859.8 | 0 | 0 | 0 | 372477.5108 | 0
5830 | 329.9117 | 289.6281 | 289.6281 | 281.9415 | 281.9415 | 1877.85 | 561828.9837 | 101498.9547 | 46041.0536 | 87929.3498 | 33758.3512
5831 | 295.6455 | 307.1185 | 307.1185 | 298.9677 | 295.6455 | 1869.3 | 585845.1332 | 106432.3917 | 48278.9154 | 0 | 38640.8711
5832 | 301.2237 | 312.9129 | 312.9129 | 304.6084 | 301.2237 | 1812.95 | 579525.9087 | 108440.55 | 49189.8384 | 0 | 56343.9024
5833 | 332.0389 | 0 | 0 | 0 | 0 | 1562.9 | 0 | 0 | 0 | 395126.3336 | 0
5834 | 303.4149 | 0 | 0 | 0 | 0 | 1590.85 | 0 | 0 | 0 | 361063.7186 | 0
5835 | 303.4149 | 0 | 0 | 0 | 0 | 1577.5 | 0 | 0 | 0 | 361063.7186 | 0
5836 | 323.0428 | 0 | 0 | 0 | 0 | 1566.6 | 0 | 0 | 0 | 384420.9403 | 0
5837 | 232.2637 | 0 | 0 | 0 | 0 | 1554.45 | 0 | 0 | 0 | 276393.79 | 0
5838 | 282.1513 | 0 | 0 | 0 | 0 | 1543.35 | 0 | 0 | 0 | 335760.0618 | 0
5839 | 262.5234 | 272.7112 | 272.7112 | 265.4736 | 262.5234 | 1507.35 | 420050.622 | 94508.4222 | 42870.0704 | 0 | 129331.956
5840 | 251.6319 | 463.9188 | 261.3965 | 451.6066 | 251.6319 | 1269.95 | 338918.8839 | 90587.5004 | 41091.4967 | 0 | 183703.9018
5841 | 470.5752 | 1303.8142 | 488.8366 | 1269.2117 | 470.5752 | 1283.55 | 641000.5668 | 169407.0829 | 76844.9351 | 0 | 337143.6237
5842 | 1198.9713 | 2011.9072 | 1245.4968 | 1958.5123 | 1198.9713 | 1366.55 | 1731785.9385 | 431629.6802 | 195792.0188 | 0 | 759488.3915
5843 | 1601.2271 | 2733.3031 | 1663.3622 | 2660.7627 | 1601.2271 | 1207.5 | 2039548.8444 | 576441.7556 | 261480.3853 | 0 | 1268972.476
5844 | 1241.291 | 3070.8803 | 1289.459 | 2989.3808 | 1241.291 | 1216 | 1598839.1937 | 446864.747 | 202702.8144 | 0 | 973172.1158
5845 | 1602.0439 | 3306.6121 | 1664.2109 | 3218.8564 | 1602.0439 | 1300.05 | 2205479.0533 | 576735.8065 | 261613.77 | 0 | 1121350.6327
5846 | 1542.9506 | 3206.9253 | 1602.8238 | 3121.8153 | 1542.9506 | 1444 | 2363597.417 | 555462.211 | 251963.8307 | 0 | 857880.5258
5847 | 1640.668 | 2266.192 | 1704.3337 | 2206.0485 | 1640.668 | 1586.95 | 2758619.9276 | 590640.4685 | 267921.0792 | 0 | 677677.9042
5848 | 1242.7375 | 2025.929 | 1290.9611 | 1972.1619 | 1242.7375 | 1607.95 | 2115638.6702 | 447385.5 | 202939.0338 | 0 | 487215.2369
5849 | 1329.2874 | 1122.8139 | 1122.8139 | 1093.0151 | 1093.0151 | 1600.55 | 1852440.6914 | 393485.4207 | 178489.3589 | 433087.2311 | 427369.1583
5850 | 1176.7039 | 215.2819 | 215.2819 | 209.5684 | 209.5684 | 1581.65 | 351110.8818 | 75444.6355 | 34222.5249 | 1772759.2581 | 85818.2272
5851 | 1489.1425 | 0 | 0 | 0 | 0 | 1579.15 | 0 | 0 | 0 | 5060106.181 | 0
5852 | 1527.7062 | 0 | 0 | 0 | 0 | 1605 | 0 | 0 | 0 | 5191145.7933 | 0
5853 | 1849.1134 | 0 | 0 | 0 | 0 | 1629.95 | 0 | 0 | 0 | 6283287.2788 | 0
5854 | 1687.1831 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1645.4 | 539401.8121 | 111351.8261 | 50510.4255 | 4682010.5411 | 108462.9204
5855 | 1236.5588 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1590.35 | 1008155.5539 | 215514.4963 | 97759.7701 | 2167609.4013 | 242512.8
5856 | 1050.9114 | 0 | 0 | 0 | 0 | 1571.95 | 0 | 0 | 0 | 1926320.6145 | 0
5857 | 1364.9581 | 0 | 0 | 0 | 0 | 1335.65 | 0 | 0 | 0 | 1624300.1247 | 0
5858 | 1355.1441 | 0 | 0 | 0 | 0 | 1528.85 | 0 | 0 | 0 | 1612621.5147 | 0
5859 | 1388.6752 | 0 | 0 | 0 | 0 | 1510.15 | 0 | 0 | 0 | 1652523.4345 | 0
5860 | 1544.0628 | 0 | 0 | 0 | 0 | 1515.45 | 0 | 0 | 0 | 1837434.7725 | 0
5861 | 1248.0084 | 0 | 0 | 0 | 0 | 1519.4 | 0 | 0 | 0 | 1485130.0127 | 0
5862 | 1493.3574 | 0 | 0 | 0 | 0 | 1540.05 | 0 | 0 | 0 | 1777095.2834 | 0
5863 | 1527.7062 | 396.3861 | 396.3861 | 385.8662 | 385.8662 | 1521.6 | 627092.6883 | 138911.8344 | 63011.9515 | 2092992.7756 | 180693.5936
5864 | 1240.9649 | 1289.1203 | 1289.1203 | 1254.9078 | 1240.9649 | 1407.45 | 1861874.2811 | 446747.3474 | 202649.5607 | 0 | 735333.7242
5865 | 1314.0022 | 1477.6904 | 1364.9915 | 1438.4733 | 1314.0022 | 1037.5 | 1448374.7661 | 473040.783 | 214576.5552 | 0 | 1264727.0934
5866 | 1895.8186 | 3364.6907 | 1969.3858 | 3275.3936 | 1895.8186 | 927.2 | 1869672.8718 | 682494.7057 | 309587.1818 | 0 | 2033834.223
5867 | 1738.3935 | 3183.3112 | 1805.8519 | 3098.8278 | 1738.3935 | 1063.45 | 1963871.7024 | 625821.6704 | 283879.6633 | 0 | 1628092.4596
5868 | 1628.6735 | 3609.5743 | 1691.8732 | 3513.7782 | 1628.6735 | 1064.45 | 1843081.3775 | 586322.4492 | 265962.3777 | 0 | 1523705.4649
5869 | 1331.8493 | 4286.8698 | 1383.5321 | 4173.0986 | 1331.8493 | 1058.5 | 1501479.6052 | 479465.7361 | 217490.9853 | 0 | 1253936.0849
5870 | 1502.9147 | 3869.4293 | 1561.2342 | 3766.7367 | 1502.9147 | 1068.5 | 1707003.4308 | 541049.3086 | 245425.978 | 0 | 1399965.0859
5871 | 1067.9509 | 3254.7643 | 1109.3926 | 3168.3847 | 1067.9509 | 332.25 | 377271.3781 | 384462.3226 | 174396.3813 | 0 | 1781075.1068
5872 | 1186.9605 | 2368.5922 | 1233.0197 | 2305.7311 | 1186.9605 | 327.55 | 416841.458 | 427305.7724 | 193830.6462 | 0 | 1985132.0531
5873 | 1465.9979 | 1245.2693 | 1245.2693 | 1212.2205 | 1212.2205 | 1068.1 | 1389881.2294 | 436399.3808 | 197955.608 | 465173.9777 | 1105772.0382
5874 | 1552.9578 | 211.2659 | 211.2659 | 205.659 | 205.659 | 1274.6 | 279738.6522 | 74037.2384 | 33584.114 | 2469598.6295 | 146029.5486
5875 | 1503.1713 | 0 | 0 | 0 | 0 | 1414 | 0 | 0 | 0 | 5107776.2133 | 0
5876 | 1143.3262 | 0 | 0 | 0 | 0 | 1347.45 | 0 | 0 | 0 | 3885022.3868 | 0
5877 | 1723.9854 | 0 | 0 | 0 | 0 | 1409 | 0 | 0 | 0 | 5858102.4232 | 0
5878 | 1668.373 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1412.6 | 464816.8981 | 111351.8261 | 50510.4255 | 4618093.8655 | 179670.3876
5879 | 1373.1364 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1339.1 | 853558.3652 | 215514.4963 | 97759.7701 | 2631700.059 | 391252.8
5880 | 1233.2875 | 0 | 0 | 0 | 0 | 1208.65 | 0 | 0 | 0 | 2260615.9435 | 0
5881 | 1690.4544 | 0 | 0 | 0 | 0 | 567.5 | 0 | 0 | 0 | 2011640.7182 | 0
5882 | 1819.6715 | 0 | 0 | 0 | 0 | 301.8 | 0 | 0 | 0 | 2165409.0945 | 0
5883 | 1252.9154 | 0 | 0 | 0 | 0 | 292.85 | 0 | 0 | 0 | 1490969.3177 | 0
5884 | 1363.3224 | 0 | 0 | 0 | 0 | 535.45 | 0 | 0 | 0 | 1622353.6893 | 0
5885 | 1499.0822 | 0 | 0 | 0 | 0 | 879.8 | 0 | 0 | 0 | 1783907.8061 | 0
5886 | 1406.6674 | 0 | 0 | 0 | 0 | 626.8 | 0 | 0 | 0 | 1673934.2215 | 0
5887 | 1239.0123 | 403.2048 | 403.2048 | 392.504 | 392.504 | 629.45 | 262966.2589 | 141301.4242 | 64095.896 | 1551649.7669 | 526566.6805
5888 | 1144.3567 | 1188.7624 | 1188.7624 | 1157.2133 | 1144.3567 | 297.55 | 361195.7904 | 411968.3951 | 186873.4414 | 0 | 1948208.8722
5889 | 1160.5057 | 2062.8813 | 1205.5391 | 2008.1336 | 1160.5057 | 325.05 | 400441.3777 | 417782.0617 | 189510.5852 | 0 | 1943789.0674
5890 | 1535.5758 | 3446.75 | 1595.1636 | 3355.2751 | 1535.5758 | 339.05 | 555074.6215 | 552807.2898 | 250759.529 | 0 | 2550514.6333
5891 | 1778.9231 | 4013.1282 | 1847.9537 | 3906.6219 | 1778.9231 | 346.25 | 655479.5298 | 640412.3279 | 290498.1476 | 0 | 2941894.1312
5892 | 1434.3111 | 4252.1073 | 1489.9691 | 4139.2587 | 1434.3111 | 349.85 | 533730.2411 | 516351.9906 | 234223.0002 | 0 | 2366828.4369
5893 | 1226.9442 | 4211.9512 | 1274.5563 | 4100.1683 | 1226.9442 | 361.05 | 471132.4412 | 441699.9059 | 200359.9851 | 0 | 2010900.1687
5894 | 1067.315 | 3882.4289 | 1108.7319 | 3779.3913 | 1067.315 | 385.3 | 437848.9983 | 384233.4119 | 174292.5449 | 0 | 1723393.5838
5895 | 1327.1212 | 3268.9045 | 1378.6196 | 3182.1496 | 1327.1212 | 390.7 | 551650.4242 | 477763.6277 | 216718.89 | 0 | 2135736.1278
5896 | 1593.7705 | 2401.2315 | 1655.6158 | 2337.5041 | 1593.7705 | 380.95 | 648823.33 | 573757.3926 | 260262.7284 | 0 | 2580394.1847
5897 | 1265.787 | 851.4625 | 851.4625 | 828.8652 | 828.8652 | 367.55 | 325268.5448 | 298391.4695 | 135353.686 | 800877.696 | 1324458.9234
5898 | 1411.0786 | 159.3589 | 159.3589 | 155.1296 | 155.1296 | 342.55 | 56651.3411 | 55846.65 | 25332.661 | 2302154.5163 | 251680.4676
5899 | 906.1208 | 0 | 0 | 0 | 0 | 692.4 | 0 | 0 | 0 | 3078998.3479 | 0
5900 | 1138.4192 | 0 | 0 | 0 | 0 | 1129.35 | 0 | 0 | 0 | 3868348.4688 | 0
5901 | 1154.7758 | 0 | 0 | 0 | 0 | 1134.45 | 0 | 0 | 0 | 3923928.1888 | 0
5902 | 1472.9116 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1108.2 | 364828.2983 | 111351.8261 | 50510.4255 | 3953916.2186 | 272778.4332
5903 | 1362.5046 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1108.6 | 705773.1994 | 215514.4963 | 97759.7701 | 2595573.2433 | 527708.8
5904 | 141.4846 | 0 | 0 | 0 | 0 | 988.8 | 0 | 0 | 0 | 259341.219 | 0
5905 | 99.7752 | 0 | 0 | 0 | 0 | 946.05 | 0 | 0 | 0 | 118732.5436 | 0
5906 | 96.5039 | 0 | 0 | 0 | 0 | 301.8 | 0 | 0 | 0 | 114839.6733 | 0
5907 | 105.5001 | 0 | 0 | 0 | 0 | 292.85 | 0 | 0 | 0 | 125545.0666 | 0
5908 | 94.8683 | 0 | 0 | 0 | 0 | 285.95 | 0 | 0 | 0 | 112893.2382 | 0
5909 | 100.5931 | 0 | 0 | 0 | 0 | 280.8 | 0 | 0 | 0 | 119705.7612 | 0
5910 | 91.5969 | 0 | 0 | 0 | 0 | 277.3 | 0 | 0 | 0 | 109000.3679 | 0
5911 | 86.69 | 90.054 | 90.054 | 87.664 | 86.69 | 279.95 | 25666.1586 | 31208.3886 | 14156.4718 | 0 | 149111.0802
5912 | 88.3635 | 944.9695 | 91.7929 | 919.8905 | 88.3635 | 297.55 | 27820.2483 | 31810.843 | 14429.7519 | 0 | 150434.3603
5913 | 674.8497 | 2538.5365 | 701.0363 | 2471.1651 | 674.8497 | 325.05 | 231499.2395 | 242945.8969 | 110202.9582 | 0 | 1130339.5276
5914 | 1069.3668 | 2191.93 | 1110.8635 | 2133.7573 | 1069.3668 | 339.05 | 385663.6135 | 384972.035 | 174627.5926 | 0 | 1776164.7267
5915 | 1034.0283 | 4012.0281 | 1074.1532 | 3905.551 | 1034.0283 | 346.25 | 383075.0385 | 372250.2002 | 168856.8269 | 0 | 1710024.3574
5916 | 1101.8888 | 4252.716 | 1144.6475 | 4139.8512 | 1101.8888 | 349.85 | 411638.1455 | 396679.9651 | 179938.4397 | 0 | 1818281.7901
5917 | 1309.4418 | 4199.23 | 1360.2546 | 4087.7848 | 1309.4418 | 361.05 | 502896.8666 | 471399.0304 | 213831.8379 | 0 | 2146109.5578
5918 | 1334.591 | 3764.6928 | 1386.3795 | 3664.7799 | 1334.591 | 385.3 | 546764.111 | 480452.7751 | 217938.7172 | 0 | 2154964.1555
5919 | 1249.9334 | 2748.2598 | 1298.4374 | 2675.3224 | 1249.9334 | 847.7 | 1126811.8177 | 449976.0172 | 204114.1211 | 0 | 1440298.2349
5920 | 1409.4378 | 2275.1039 | 1464.1309 | 2214.7239 | 1409.4378 | 380.95 | 571084.9178 | 507397.612 | 230161.1945 | 0 | 2281950.2879
5921 | 1475.0421 | 1187.6499 | 1187.6499 | 1156.1303 | 1156.1303 | 617.05 | 762613.4917 | 416206.9102 | 188796.079 | 584565.2833 | 1565048.5583
5922 | 1347.0834 | 159.6664 | 159.6664 | 155.4289 | 155.4289 | 1112 | 184422.5989 | 55954.4073 | 25381.5409 | 2184302.6709 | 135101.208
5923 | 1438.5628 | 0 | 0 | 0 | 0 | 1685.9 | 0 | 0 | 0 | 4888236.3196 | 0
5924 | 1652.8342 | 0 | 0 | 0 | 0 | 1816.95 | 0 | 0 | 0 | 5616330.6456 | 0
5925 | 1743.6133 | 0 | 0 | 0 | 0 | 1806.2 | 0 | 0 | 0 | 5924798.0885 | 0
5926 | 1660.1947 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1865.25 | 611066.5425 | 111351.8261 | 50510.4255 | 4590304.0055 | 41216.5215
5927 | 1413.2101 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1865.65 | 1183341.7201 | 215514.4963 | 97759.7701 | 2767870.3726 | 79535.2
5928 | 139.8489 | 0 | 0 | 0 | 0 | 1819.3 | 0 | 0 | 0 | 256343.0546 | 0
5929 | 107.1357 | 0 | 0 | 0 | 0 | 1429 | 0 | 0 | 0 | 127491.5017 | 0
5930 | 98.9574 | 0 | 0 | 0 | 0 | 900.8 | 0 | 0 | 0 | 117759.326 | 0
5931 | 102.2287 | 0 | 0 | 0 | 0 | 292.85 | 0 | 0 | 0 | 121652.1963 | 0
5932 | 100.5931 | 0 | 0 | 0 | 0 | 285.95 | 0 | 0 | 0 | 119705.7612 | 0
5933 | 103.8644 | 0 | 0 | 0 | 0 | 280.8 | 0 | 0 | 0 | 123598.6315 | 0
5934 | 97.3218 | 0 | 0 | 0 | 0 | 626.8 | 0 | 0 | 0 | 115812.8909 | 0
5935 | 94.8683 | 12.2652 | 12.2652 | 11.9397 | 11.9397 | 1070.85 | 13525.9674 | 4298.2764 | 1949.746 | 152008.1432 | 10859.9052
5936 | 87.886 | 620.8583 | 91.2964 | 604.381 | 87.886 | 505.05 | 46888.8125 | 31638.9761 | 14351.7911 | 0 | 131385.2425
5937 | 953.4016 | 990.3975 | 990.3975 | 964.1129 | 953.4016 | 1300.5 | 1312886.7603 | 343224.5588 | 155690.4735 | 0 | 666903.9995
5938 | 1414.2467 | 3122.7084 | 1469.1265 | 3039.8334 | 1414.2467 | 1360.55 | 2037389.162 | 509128.7944 | 230946.4781 | 0 | 904340.021
5939 | 1289.2178 | 3980.8909 | 1339.2458 | 3875.2403 | 1289.2178 | 1261.25 | 1722014.3793 | 464118.4224 | 210529.2733 | 0 | 952409.6793
5940 | 1489.7845 | 3428.4525 | 1547.5957 | 3337.4632 | 1489.7845 | 1513.85 | 2399452.5679 | 536322.4153 | 243281.8067 | 0 | 724258.7284
5941 | 1378.1088 | 3087.7588 | 1431.5862 | 3005.8114 | 1378.1088 | 1530.1 | 2242255.1437 | 496119.1655 | 225045.1659 | 0 | 647573.3218
5942 | 1448.9237 | 3437.4236 | 1505.1481 | 3346.1963 | 1448.9237 | 1894.3 | 2915822.9892 | 521612.518 | 236609.2338 | 0 | 153151.231
5943 | 1588.6233 | 2310.5293 | 1650.2702 | 2249.2091 | 1588.6233 | 1899.7 | 3202706.85 | 571904.3945 | 259422.1878 | 0 | 159338.9188
5944 | 1511.5071 | 865.3192 | 865.3192 | 842.3541 | 842.3541 | 1889.95 | 1687500.2873 | 303247.4625 | 137556.4184 | 1226557.4645 | 90740.0768
5945 | 1311.4301 | 459.1984 | 459.1984 | 447.0116 | 447.0116 | 1876.55 | 888175.518 | 160924.1647 | 72996.9891 | 1584479.1681 | 54016.2882
5946 | 1754.8452 | 76.3501 | 76.3501 | 74.3238 | 74.3238 | 1851.55 | 145777.4136 | 26756.5616 | 12137.0736 | 3080395.7571 | 10799.8859
5947 | 1257.345 | 0 | 0 | 0 | 0 | 1845.85 | 0 | 0 | 0 | 4272458.1877 | 0
5948 | 847.2718 | 0 | 0 | 0 | 0 | 1847.45 | 0 | 0 | 0 | 2879029.4649 | 0
5949 | 1282.3573 | 0 | 0 | 0 | 0 | 1852.55 | 0 | 0 | 0 | 4357450.0001 | 0
5950 | 1299.5317 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1865.25 | 609370.6264 | 111351.8261 | 50510.4255 | 3364771.1927 | 41216.5215
5951 | 1363.3224 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1865.65 | 1179898.7762 | 215514.4963 | 97759.7701 | 2598352.2263 | 79535.2
5952 | 1331.4271 | 0 | 0 | 0 | 0 | 1849.3 | 0 | 0 | 0 | 2440505.8065 | 0
5953 | 1392.7643 | 0 | 0 | 0 | 0 | 1782.4 | 0 | 0 | 0 | 1657389.5229 | 0
5954 | 954.4075 | 0 | 0 | 0 | 0 | 1635.25 | 0 | 0 | 0 | 1135744.9047 | 0
5955 | 1391.9465 | 0 | 0 | 0 | 0 | 1229.35 | 0 | 0 | 0 | 1656416.3052 | 0
5956 | 1367.4116 | 0 | 0 | 0 | 0 | 285.95 | 0 | 0 | 0 | 1627219.7778 | 0
5957 | 1018.1982 | 0 | 0 | 0 | 0 | 280.8 | 0 | 0 | 0 | 1211655.8747 | 0
5958 | 1299.5317 | 0 | 0 | 0 | 0 | 526.8 | 0 | 0 | 0 | 1546442.7194 | 0
5959 | 1066.4502 | 316.8957 | 316.8957 | 308.4855 | 308.4855 | 1351.95 | 444439.5198 | 111054.7655 | 50375.6756 | 1389349.3284 | 195685.178
5960 | 879.7304 | 982.2211 | 913.8677 | 956.1534 | 879.7304 | 1009.6 | 943450.1507 | 316702.9488 | 143659.9765 | 0 | 871285.0013
5961 | 1118.7892 | 2268.0619 | 1162.2033 | 2207.8688 | 1118.7892 | 1564.6 | 1854789.0788 | 402764.1286 | 182698.2839 | 0 | 487120.8377
5962 | 1147.7987 | 3497.4686 | 1192.3391 | 3404.6477 | 1147.7987 | 1466.55 | 1782426.8792 | 413207.5302 | 187435.5269 | 0 | 612293.2138
5963 | 1167.7466 | 3995.6991 | 1213.0601 | 3889.6554 | 1167.7466 | 1246.25 | 1545243.4162 | 420388.7717 | 190693.0178 | 0 | 880188.9907
5964 | 1009.8492 | 4241.7161 | 1049.0359 | 4129.1433 | 1009.8492 | 1517.9 | 1621670.9254 | 363545.7098 | 164908.3734 | 0 | 486848.2964
5965 | 1123.4907 | 4201.9382 | 1167.0878 | 4090.421 | 1123.4907 | 1433.55 | 1702968.9415 | 404456.6686 | 183466.0388 | 0 | 636401.3331
5966 | 1352.7826 | 2617.0992 | 1405.2774 | 2547.6429 | 1352.7826 | 1759.35 | 2520010.0465 | 487001.7526 | 220909.4061 | 0 | 325547.1438
5967 | 1227.347 | 467.165 | 467.165 | 454.7667 | 454.7667 | 1899.65 | 916336.2604 | 163716.0239 | 74263.4075 | 1416139.5632 | 44670.4011
5968 | 1201.4218 | 131.0369 | 131.0369 | 127.5593 | 127.5593 | 1889.95 | 255365.4147 | 45921.3338 | 20830.4272 | 1968389.9544 | 13740.953
5969 | 1209.5909 | 33.3487 | 33.3487 | 32.4637 | 32.4637 | 1876.55 | 64494.0369 | 11686.9288 | 5301.3208 | 2157674.0912 | 3922.8706
5970 | 1315.1216 | 0 | 0 | 0 | 0 | 1851.55 | 0 | 0 | 0 | 2410617.8543 | 0
5971 | 1232.4093 | 0 | 0 | 0 | 0 | 1845.85 | 0 | 0 | 0 | 4187726.9067 | 0
5972 | 1067.268 | 0 | 0 | 0 | 0 | 1847.45 | 0 | 0 | 0 | 3626576.6912 | 0
5973 | 1498.2644 | 0 | 0 | 0 | 0 | 1852.55 | 0 | 0 | 0 | 5091102.2987 | 0
5974 | 1077.8998 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1865.25 | 608954.8748 | 111351.8261 | 50510.4255 | 2611665.9931 | 41216.5215
5975 | 1290.5356 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1865.65 | 1180517.8591 | 215514.4963 | 97759.7701 | 2351022.476 | 79535.2
5976 | 956.861 | 0 | 0 | 0 | 0 | 1848.8 | 0 | 0 | 0 | 1753926.1628 | 0
5977 | 1195.6673 | 0 | 0 | 0 | 0 | 1023.4 | 0 | 0 | 0 | 2191658.1627 | 0
5978 | 1304.4387 | 0 | 0 | 0 | 0 | 1571.35 | 0 | 0 | 0 | 2391036.0931 | 0
5979 | 1028.83 | 0 | 0 | 0 | 0 | 1178.35 | 0 | 0 | 0 | 1885845.3955 | 0
5980 | 1461.462 | 0 | 0 | 0 | 0 | 998.95 | 0 | 0 | 0 | 2678859.8735 | 0
5981 | 1392.7643 | 0 | 0 | 0 | 0 | 991.9 | 0 | 0 | 0 | 2552936.9711 | 0
5982 | 1118.7913 | 0 | 0 | 0 | 0 | 988.4 | 0 | 0 | 0 | 2050744.4364 | 0
5983 | 1271.7255 | 165.438 | 165.438 | 161.0473 | 161.0473 | 1081.4 | 184864.8937 | 57977.0399 | 26299.0295 | 2035873.045 | 144809.0226
5984 | 186.0829 | 193.3029 | 193.3029 | 188.1727 | 186.0829 | 1009.6 | 199040.0457 | 66989.8367 | 30387.3343 | 0 | 184296.4841
5985 | 155.6841 | 1216.8445 | 161.7253 | 1184.5501 | 155.6841 | 1448.55 | 238914.2672 | 56046.2913 | 25423.2205 | 0 | 85852.0204
5986 | 185.2027 | 2236.0895 | 192.3898 | 2176.745 | 185.2027 | 1425.55 | 279563.0371 | 66672.9685 | 30243.5993 | 0 | 106389.6854
5987 | 174.4073 | 2981.7145 | 181.1748 | 2902.5814 | 174.4073 | 1186.65 | 219269.7768 | 62786.6409 | 28480.7179 | 0 | 141854.2065
5988 | 189.5525 | 2342.6003 | 196.9075 | 2280.4289 | 189.5525 | 1101.8 | 221891.259 | 68238.9083 | 30953.927 | 0 | 170256.0762
5989 | 199.8194 | 1146.908 | 207.5729 | 1116.4697 | 199.8194 | 361.05 | 76762.2476 | 71934.9678 | 32630.5007 | 0 | 327493.9319
5990 | 201.4499 | 2387.2336 | 209.2672 | 2323.8777 | 201.4499 | 1408.8 | 301294.3605 | 72521.9652 | 32896.7692 | 0 | 119097.1829
5991 | 132.424 | 1774.4717 | 137.5627 | 1727.3782 | 132.424 | 1756.9 | 246535.4141 | 47672.6538 | 21624.8455 | 0 | 32192.2837
5992 | 181.7586 | 218.8471 | 188.8111 | 213.039 | 181.7586 | 1743.65 | 335376.9145 | 65433.0975 | 29681.18 | 0 | 46593.8182
5993 | 119.9634 | 637.3753 | 124.6181 | 620.4597 | 119.9634 | 1827.4 | 231973.4006 | 43186.8159 | 19590.0196 | 0 | 20705.679
5994 | 101.4733 | 105.4408 | 105.4106 | 102.6424 | 101.4733 | 1844 | 197843.5096 | 36530.3758 | 16570.5843 | 0 | 15829.788
5995 | 112.5998 | 116.9694 | 116.9694 | 113.8651 | 112.5998 | 1838.35 | 219148.1409 | 40535.943 | 18387.5541 | 0 | 18201.7644
5996 | 110.407 | 114.6913 | 114.6913 | 111.6475 | 110.407 | 1847.4 | 215648.1238 | 39746.5327 | 18029.4689 | 0 | 16848.1082
5997 | 102.2287 | 106.196 | 106.196 | 103.3776 | 102.2287 | 1819.85 | 197181.9624 | 36802.3451 | 16693.9527 | 0 | 18416.5069
5998 | 93.2326 | 96.8509 | 96.8509 | 94.2805 | 93.2326 | 1857.7 | 183044.3772 | 33563.7387 | 15224.8848 | 0 | 13267.0001
5999 | 102.2287 | 106.196 | 106.196 | 103.3776 | 102.2287 | 1719.35 | 185692.2801 | 36802.3451 | 16693.9527 | 0 | 28690.4949
6000 | 95.6861 | 99.3991 | 99.3991 | 96.7611 | 95.6861 | 1239.8 | 125433.4994 | 34446.995 | 15625.5397 | 0 | 72740.4972
6001 | 100.5931 | 0 | 0 | 0 | 0 | 326.05 | 0 | 0 | 0 | 119705.7612 | 0
6002 | 92.4148 | 0 | 0 | 0 | 0 | 336 | 0 | 0 | 0 | 109973.5855 | 0
6003 | 98.9574 | 0 | 0 | 0 | 0 | 325.8 | 0 | 0 | 0 | 117759.326 | 0
6004 | 93.2326 | 94.4647 | 94.4647 | 91.9577 | 91.9577 | 316.55 | 30967.6447 | 33104.774 | 15016.6933 | 1517.1333 | 151399.3923
6005 | 98.9574 | 102.797 | 102.797 | 100.0688 | 98.9574 | 308.3 | 32515.14 | 35624.6701 | 16159.7462 | 0 | 167405.5569
6006 | 91.5969 | 95.1514 | 95.1514 | 92.6261 | 91.5969 | 648.05 | 63419.9143 | 32974.9012 | 14957.7816 | 0 | 123834.4936
6007 | 94.8683 | 98.5493 | 98.5493 | 95.9339 | 94.8683 | 1009 | 102082.2572 | 34152.5763 | 15491.9881 | 0 | 94014.453
6008 | 88.6732 | 626.3172 | 92.1139 | 609.6951 | 88.6732 | 548.75 | 51811.9085 | 31922.3541 | 14480.3345 | 0 | 128686.9901
6009 | 877.3751 | 2562.2961 | 911.4213 | 2494.2941 | 877.3751 | 1109.7 | 1034814.5799 | 315855.0228 | 143275.3478 | 0 | 781127.0188
6010 | 1234.046 | 1495.1423 | 1281.9328 | 1455.4621 | 1234.046 | 1083.6 | 1419248.5584 | 444256.5647 | 201519.7139 | 0 | 1130879.7663
6011 | 1673.4272 | 2873.6248 | 1738.365 | 2797.3604 | 1673.4272 | 950.65 | 1688971.4624 | 602433.7801 | 273270.6564 | 0 | 1756010.7977
6012 | 1423.6773 | 2075.5475 | 1478.9224 | 2020.4636 | 1423.6773 | 348 | 525662.0965 | 512523.8107 | 232486.4953 | 0 | 2351914.8203
6013 | 1772.2558 | 827.623 | 827.623 | 805.6584 | 805.6584 | 354.75 | 303918.321 | 290037.0064 | 131564.0087 | 1771773.0782 | 1297470.474
6014 | 1493.8665 | 645.105 | 645.105 | 627.9843 | 627.9843 | 365.6 | 244032.4501 | 226074.3425 | 102549.8337 | 1587162.0638 | 1004665.68
6015 | 1557.6541 | 182.2936 | 182.2936 | 177.4556 | 177.4556 | 359.45 | 67725.5772 | 63884.0302 | 28978.5059 | 2529903.8608 | 284965.1755
6016 | 1584.9707 | 215.6185 | 215.6185 | 209.8961 | 209.8961 | 346.2 | 77356.4463 | 75562.586 | 34276.0286 | 2520511.7672 | 339783.1328
6017 | 1772.4797 | 192.0927 | 192.0927 | 186.9946 | 186.9946 | 1326.95 | 264272.7702 | 67318.0644 | 30536.222 | 2906194.0651 | 123194.399
6018 | 1755.7039 | 26.6246 | 26.6246 | 25.918 | 25.918 | 1590.95 | 43827.8521 | 9330.4671 | 4232.4036 | 3170697.6569 | 10377.5985
6019 | 1611.083 | 0 | 0 | 0 | 0 | 1830.4 | 0 | 0 | 0 | 5474459.9389 | 0
6020 | 1745.249 | 0 | 0 | 0 | 0 | 1817.15 | 0 | 0 | 0 | 5930356.0612 | 0
6021 | 1431.2023 | 0 | 0 | 0 | 0 | 1671.1 | 0 | 0 | 0 | 4863225.446 | 0
6022 | 1315.8883 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1712.65 | 562919.8131 | 111351.8261 | 50510.4255 | 3420350.9127 | 87892.8939
6023 | 1081.1711 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1369.85 | 872782.0774 | 215514.4963 | 97759.7701 | 1639602.0681 | 373048.8
6024 | 1571.0512 | 0 | 0 | 0 | 0 | 679.85 | 0 | 0 | 0 | 2879736.8881 | 0
6025 | 1019.8339 | 0 | 0 | 0 | 0 | 1010.05 | 0 | 0 | 0 | 1213602.3101 | 0
6026 | 1302.803 | 0 | 0 | 0 | 0 | 276.3 | 0 | 0 | 0 | 1550335.5902 | 0
6027 | 1215.2952 | 0 | 0 | 0 | 0 | 270.65 | 0 | 0 | 0 | 1446201.3094 | 0
6028 | 1135.9657 | 0 | 0 | 0 | 0 | 266.45 | 0 | 0 | 0 | 1351799.2056 | 0
6029 | 1096.7099 | 0 | 0 | 0 | 0 | 263.3 | 0 | 0 | 0 | 1305084.762 | 0
6030 | 1092.6207 | 0 | 0 | 0 | 0 | 262.05 | 0 | 0 | 0 | 1300218.6746 | 0
6031 | 1315.8883 | 405.7592 | 405.7592 | 394.9906 | 394.9906 | 265.5 | 111697.1955 | 142196.6102 | 64501.9624 | 1688005.5042 | 670620.142
6032 | 1094.9209 | 868.5 | 868.5 | 845.4505 | 845.4505 | 276.45 | 247922.1259 | 304362.1676 | 138062.061 | 457279.2717 | 1426353.1028
6033 | 1387.202 | 1414.1083 | 1414.1083 | 1376.5786 | 1376.5786 | 294.1 | 428981.3327 | 495568.3032 | 224795.2887 | 19472.7268 | 2298630.3081
6034 | 1405.6574 | 2979.5808 | 1460.2042 | 2900.5044 | 1405.6574 | 306.3 | 456447.3801 | 506036.6615 | 229543.8523 | 0 | 2380761.9265
6035 | 1365.2484 | 2948.639 | 1418.2261 | 2870.3837 | 1365.2484 | 320.05 | 464033.5812 | 491489.4305 | 222945.0667 | 0 | 2293549.0798
6036 | 1221.3717 | 4317.4034 | 1268.767 | 4202.8219 | 1221.3717 | 320.45 | 415951.111 | 439693.8098 | 199449.9976 | 0 | 2051354.8287
6037 | 1267.0966 | 4285.1776 | 1316.2653 | 4171.4513 | 1267.0966 | 314.5 | 423859.2406 | 456154.7627 | 206916.8687 | 0 | 2135691.2569
6038 | 1528.0967 | 3960.3278 | 1587.3944 | 3855.2229 | 1528.0967 | 325.1 | 527110.2262 | 550114.83 | 249538.1993 | 0 | 2559409.2466
6039 | 1700.6118 | 3344.5389 | 1766.6038 | 3255.7766 | 1700.6118 | 332.25 | 600418.947 | 612220.2595 | 277709.9122 | 0 | 2836195.3828
6040 | 1411.0387 | 1747.3028 | 1465.793 | 1700.9304 | 1411.0387 | 327.55 | 491749.0085 | 507973.9367 | 230422.6218 | 0 | 2359891.6956
6041 | 1480.8333 | 320.2375 | 320.2375 | 311.7386 | 311.7386 | 322.7 | 107241.5293 | 112225.8975 | 50906.9141 | 2142950.6488 | 511818.0312
6042 | 1727.6442 | 46.8148 | 46.8148 | 45.5723 | 45.5723 | 1364.65 | 66328.8561 | 16406.041 | 7441.9625 | 3083237.6842 | 28342.3281
6043 | 1863.8394 | 0 | 0 | 0 | 0 | 1829.45 | 0 | 0 | 0 | 6333326.3933 | 0
6044 | 874.2602 | 0 | 0 | 0 | 0 | 1826.9 | 0 | 0 | 0 | 2970736.0019 | 0
6045 | 1106.5238 | 0 | 0 | 0 | 0 | 1791.8 | 0 | 0 | 0 | 3759968.0185 | 0
6046 | 1191.5782 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1823.05 | 598818.0662 | 111351.8261 | 50510.4255 | 2997945.0434 | 54124.4043
6047 | 1427.931 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1788.4 | 1135010.6491 | 215514.4963 | 97759.7701 | 2817892.12 | 125267.2
6048 | 771.2136 | 0 | 0 | 0 | 0 | 1306.35 | 0 | 0 | 0 | 1413634.5055 | 0
6049 | 615.8259 | 0 | 0 | 0 | 0 | 1421.95 | 0 | 0 | 0 | 732832.8305 | 0
6050 | 593.7445 | 0 | 0 | 0 | 0 | 900.8 | 0 | 0 | 0 | 706555.9561 | 0
6051 | 716.419 | 0 | 0 | 0 | 0 | 642.4 | 0 | 0 | 0 | 852538.5917 | 0
6052 | 741.7717 | 0 | 0 | 0 | 0 | 285.95 | 0 | 0 | 0 | 882708.3363 | 0
6053 | 516.8685 | 0 | 0 | 0 | 0 | 280.8 | 0 | 0 | 0 | 615073.5045 | 0
6054 | 739.3182 | 0 | 0 | 0 | 0 | 632.85 | 0 | 0 | 0 | 879788.6837 | 0
6055 | 691.8841 | 215.8023 | 215.8023 | 210.0751 | 210.0751 | 1081.4 | 241980.6351 | 75627.0219 | 34305.2574 | 883155.9466 | 188892.6366
6056 | 788.801 | 794.5932 | 794.5932 | 773.5051 | 773.5051 | 996.55 | 818254.1049 | 278461.8393 | 126313.3843 | 28037.4031 | 759755.1434
6057 | 672.9677 | 699.0824 | 699.0824 | 680.5291 | 672.9677 | 1225.05 | 873909.8928 | 242268.3657 | 109895.6226 | 0 | 521516.3056
6058 | 848.4842 | 881.4102 | 881.4102 | 858.0181 | 848.4842 | 1320.1 | 1190501.0338 | 305454.312 | 138557.4699 | 0 | 576884.2716
6059 | 583.859 | 2773.67 | 606.5155 | 2700.0583 | 583.859 | 595.75 | 371837.7417 | 210189.2336 | 95344.1718 | 0 | 819883.9756
6060 | 720.5879 | 2524.0535 | 748.5502 | 2457.0665 | 720.5879 | 349.85 | 270108.6359 | 259411.6341 | 117671.9996 | 0 | 1189078.0778
6061 | 820.5103 | 3339.2576 | 852.3507 | 3250.6355 | 820.5103 | 361.05 | 316060.7615 | 295383.7183 | 133989.3367 | 0 | 1344775.4031
6062 | 864.1732 | 2897.1205 | 897.707 | 2820.2325 | 864.1732 | 1284.35 | 1182329.6312 | 311102.3679 | 141119.4908 | 0 | 618445.5822
6063 | 828.4586 | 3329.5115 | 860.6071 | 3241.1481 | 828.4586 | 1674.75 | 1478580.6371 | 298245.1006 | 135287.2915 | 0 | 269456.1638
6064 | 969.7735 | 1787.5534 | 1007.4048 | 1740.1127 | 969.7735 | 1889.85 | 1946060.7131 | 349118.4543 | 158364.01 | 0 | 106820.5493
6065 | 882.8525 | 1224.4225 | 917.1108 | 1191.927 | 882.8525 | 1876.55 | 1757722.67 | 317826.8924 | 144169.8098 | 0 | 108988.1385
6066 | 889.7008 | 176.012 | 176.012 | 171.3407 | 171.3407 | 1851.55 | 336015.6156 | 61682.6515 | 27979.9361 | 1316754.0326 | 24897.5886
6067 | 815.3764 | 0 | 0 | 0 | 0 | 1845.85 | 0 | 0 | 0 | 2770649.012 | 0
6068 | 857.0857 | 0 | 0 | 0 | 0 | 1847.45 | 0 | 0 | 0 | 2912377.2966 | 0
6069 | 776.1206 | 0 | 0 | 0 | 0 | 1852.55 | 0 | 0 | 0 | 2637257.6856 | 0
6070 | 704.9694 | 347.3649 | 347.3649 | 338.146 | 338.146 | 1865.25 | 670888.3539 | 121732.5623 | 55219.2428 | 1246465.7762 | 45058.9178
6071 | 563.4848 | 585.3509 | 585.3509 | 569.816 | 563.4848 | 1865.65 | 1118866.5006 | 202854.5262 | 92017.067 | 0 | 75704.1822
6072 | 704.9694 | 0 | 0 | 0 | 0 | 1849.25 | 0 | 0 | 0 | 1292208.8481 | 0
6073 | 1049.2758 | 0 | 0 | 0 | 0 | 1556 | 0 | 0 | 0 | 1248638.1425 | 0
6074 | 1127.7874 | 0 | 0 | 0 | 0 | 1434.8 | 0 | 0 | 0 | 1342067.0298 | 0
6075 | 815.3764 | 0 | 0 | 0 | 0 | 1093.35 | 0 | 0 | 0 | 970297.9177 | 0
6076 | 836.64 | 0 | 0 | 0 | 0 | 997.05 | 0 | 0 | 0 | 995601.5745 | 0
6077 | 796.5663 | 0 | 0 | 0 | 0 | 985.85 | 0 | 0 | 0 | 947913.9135 | 0
6078 | 758.1283 | 0 | 0 | 0 | 0 | 882.35 | 0 | 0 | 0 | 902172.6878 | 0
6079 | 855.4501 | 201.6559 | 201.6559 | 196.3041 | 196.3041 | 1081.4 | 226320.4 | 70669.4604 | 32056.4525 | 1208214.6353 | 176509.9086
6080 | 639.7638 | 664.5888 | 664.5888 | 646.951 | 639.7638 | 447.05 | 305671.4185 | 230314.964 | 104473.4267 | 0 | 993521.176
6081 | 302.7034 | 1140.1017 | 314.4493 | 1109.844 | 302.7034 | 1313.5 | 423920.2457 | 108973.2159 | 49431.4616 | 0 | 207805.8687
6082 | 287.4345 | 1624.2948 | 298.5878 | 1581.1869 | 287.4345 | 784 | 238988.664 | 103476.4177 | 46938.0528 | 0 | 349520.3441
6083 | 226.1197 | 2887.7827 | 234.8945 | 2811.1425 | 226.1197 | 346.25 | 82834.1107 | 81403.1071 | 36925.3539 | 0 | 373945.5233
6084 | 306.2691 | 2688.1078 | 318.1537 | 2616.7669 | 306.2691 | 349.85 | 113941.7533 | 110256.8817 | 50013.7466 | 0 | 505389.9816
6085 | 908.0488 | 3252.3979 | 943.2846 | 3166.0811 | 908.0488 | 361.05 | 348210.2358 | 326897.5664 | 148284.3683 | 0 | 1488246.5734
6086 | 1146.5832 | 2993.5247 | 1191.0759 | 2914.0782 | 1146.5832 | 385.3 | 471180.7798 | 412769.9502 | 187237.0357 | 0 | 1851387.885
6087 | 858.2665 | 182.6894 | 182.6894 | 177.8409 | 177.8409 | 995.7 | 188951.7612 | 64022.7312 | 29041.4222 | 1247220.029 | 174827.5397
6088 | 1394.3683 | 93.0863 | 93.0863 | 90.6158 | 90.6158 | 1889.85 | 182403.661 | 32621.6866 | 14797.5595 | 2389778.2899 | 9770.1948
6089 | 1415.3466 | 38.1397 | 38.1397 | 37.1275 | 37.1275 | 1876.55 | 74095.3436 | 13365.9033 | 6062.9222 | 2526275.6524 | 4486.4199
6090 | 1274.8271 | 0 | 0 | 0 | 0 | 1851.55 | 0 | 0 | 0 | 2336758.0761 | 0
6091 | 1217.7058 | 0 | 0 | 0 | 0 | 1845.85 | 0 | 0 | 0 | 4137764.2133 | 0
6092 | 1113.8843 | 0 | 0 | 0 | 0 | 1847.45 | 0 | 0 | 0 | 3784978.8922 | 0
6093 | 1204.6634 | 0 | 0 | 0 | 0 | 1852.55 | 0 | 0 | 0 | 4093446.3351 | 0
6094 | 1071.3572 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1865.25 | 613376.6706 | 111351.8261 | 50510.4255 | 2589434.1057 | 41216.5215
6095 | 1266.8185 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1865.6 | 1194661.0788 | 215514.4963 | 97759.7701 | 2270431.8823 | 79564.8
6096 | 1126.9696 | 0 | 0 | 0 | 0 | 1658.45 | 0 | 0 | 0 | 2065735.2585 | 0
6097 | 1026.3765 | 0 | 0 | 0 | 0 | 1190.5 | 0 | 0 | 0 | 1221388.0505 | 0
6098 | 914.3338 | 0 | 0 | 0 | 0 | 1486.8 | 0 | 0 | 0 | 1088057.2438 | 0
6099 | 758.1283 | 0 | 0 | 0 | 0 | 1094.3 | 0 | 0 | 0 | 902172.6878 | 0
6100 | 830.0973 | 0 | 0 | 0 | 0 | 998 | 0 | 0 | 0 | 987815.834 | 0
6101 | 926.6013 | 0 | 0 | 0 | 0 | 993.8 | 0 | 0 | 0 | 1102655.5073 | 0
6102 | 1324.0666 | 0 | 0 | 0 | 0 | 1302.25 | 0 | 0 | 0 | 1575639.2469 | 0
6103 | 1107.3417 | 326.6127 | 326.6127 | 317.9446 | 317.9446 | 1382.95 | 468960.7349 | 114460.0402 | 51920.346 | 1446964.9153 | 192037.684
6104 | 949.5925 | 986.4417 | 986.4417 | 960.2621 | 949.5925 | 297.55 | 302073.725 | 341853.3034 | 155068.4568 | 0 | 1616633.7676
6105 | 1070.4841 | 1410.5545 | 1112.0239 | 1373.1192 | 1070.4841 | 1395.05 | 1592081.4241 | 385374.2846 | 174810.0574 | 0 | 647589.3708
6106 | 1490.9918 | 2033.8395 | 1548.8485 | 1979.8625 | 1490.9918 | 1442.05 | 2287352.7088 | 536757.0509 | 243478.9622 | 0 | 831898.8793
6107 | 1371.7788 | 2658.2369 | 1425.0105 | 2587.6888 | 1371.7788 | 952.25 | 1389172.1286 | 493840.3644 | 224011.4764 | 0 | 1437281.2272
6108 | 1488.1212 | 3632.2307 | 1545.8672 | 3535.8332 | 1488.1212 | 349.85 | 555466.5593 | 535723.641 | 243010.196 | 0 | 2455623.2394
6109 | 1658.559 | 1940.4187 | 1722.919 | 1888.9211 | 1658.559 | 361.05 | 640587.3944 | 597081.2468 | 270842.6878 | 0 | 2718295.3042
6110 | 1466.1104 | 947.7327 | 947.7327 | 922.5804 | 922.5804 | 385.3 | 379825.5061 | 332128.9533 | 150657.3835 | 996290.3619 | 1433664.6801
6111 | 1663.649 | 1728.2065 | 1728.2065 | 1682.3408 | 1663.649 | 390.7 | 695660.0599 | 598913.6357 | 271673.8797 | 0 | 2677310.3164
6112 | 1239.8362 | 1155.182 | 1155.182 | 1124.5241 | 1124.5241 | 737.45 | 887983.5308 | 404828.6913 | 183634.7925 | 211367.0911 | 1389734.2368
6113 | 1491.3363 | 870.5817 | 870.5817 | 847.477 | 847.477 | 1876.5 | 1701875.7905 | 305091.7132 | 138392.991 | 1180194.1661 | 102449.425
6114 | 1536.6216 | 129.8059 | 129.8059 | 126.3609 | 126.3609 | 1851.55 | 249332.0126 | 45489.9407 | 20634.7426 | 2585007.7871 | 18361.4836
6115 | 1553.0947 | 0 | 0 | 0 | 0 | 1845.85 | 0 | 0 | 0 | 5277415.9367 | 0
6116 | 1250.4619 | 0 | 0 | 0 | 0 | 1847.45 | 0 | 0 | 0 | 4249069.5498 | 0
6117 | 1401.7604 | 0 | 0 | 0 | 0 | 1852 | 0 | 0 | 0 | 4763181.9513 | 0
6118 | 1464.7333 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1865.15 | 616950.2078 | 111351.8261 | 50510.4255 | 3926126.3586 | 41247.1089
6119 | 1255.3689 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1844.3 | 1181389.3992 | 215514.4963 | 97759.7701 | 2231526.0804 | 92174.4
6120 | 1278.2681 | 0 | 0 | 0 | 0 | 1239.8 | 0 | 0 | 0 | 2343065.464 | 0
6121 | 1221.8379 | 0 | 0 | 0 | 0 | 941 | 0 | 0 | 0 | 1453987.0498 | 0
6122 | 1106.5238 | 0 | 0 | 0 | 0 | 1449.8 | 0 | 0 | 0 | 1316763.3732 | 0
6123 | 1113.0665 | 0 | 0 | 0 | 0 | 1452.85 | 0 | 0 | 0 | 1324549.1136 | 0
6124 | 1459.8264 | 0 | 0 | 0 | 0 | 1175.85 | 0 | 0 | 0 | 1737193.3636 | 0
6125 | 963.4036 | 0 | 0 | 0 | 0 | 1121.2 | 0 | 0 | 0 | 1146450.2979 | 0
6126 | 978.9424 | 0 | 0 | 0 | 0 | 1117.7 | 0 | 0 | 0 | 1164941.4318 | 0
6127 | 1391.9465 | 444.65 | 444.65 | 432.8492 | 432.8492 | 1366.95 | 629804.2025 | 155825.7179 | 70684.277 | 1758025.2752 | 268218.8536
6128 | 1243.5472 | 1291.8025 | 1291.8025 | 1257.5188 | 1243.5472 | 1048.55 | 1390940.8709 | 447676.9747 | 203071.2499 | 0 | 1183172.7932
6129 | 1089.836 | 2113.6581 | 1132.1268 | 2057.5628 | 1089.836 | 325.1 | 378649.7282 | 392340.9686 | 177970.2227 | 0 | 1825366.3566
6130 | 1125.3411 | 2747.9866 | 1169.0096 | 2675.0565 | 1125.3411 | 339.05 | 408003.1916 | 405122.791 | 183768.1993 | 0 | 1869135.2768
6131 | 1443.0721 | 3334.0407 | 1499.07 | 3245.5571 | 1443.0721 | 346.25 | 533060.9351 | 519505.9517 | 235653.672 | 0 | 2386480.4655
6132 | 1395.4795 | 4165.8335 | 1449.6313 | 4055.2746 | 1395.4795 | 349.85 | 520217.1579 | 502372.62 | 227881.8024 | 0 | 2302750.4969
6133 | 1267.3981 | 4119.882 | 1316.5791 | 4010.5426 | 1267.3981 | 361.05 | 485889.4955 | 456263.3297 | 206966.1159 | 0 | 2077202.1783
6134 | 1171.6916 | 3740.4336 | 1217.1592 | 3641.1645 | 1171.6916 | 385.3 | 483002.4463 | 421808.9742 | 191337.2375 | 0 | 1891930.4184
6135 | 1207.4389 | 3110.6697 | 1254.2934 | 3028.1142 | 1207.4389 | 390.7 | 503451.9253 | 434678.0184 | 197174.7789 | 0 | 1943131.4861
6136 | 1296.1408 | 2239.1 | 1346.4374 | 2179.6755 | 1296.1408 | 736.5 | 1014832.2858 | 466610.6772 | 211659.7877 | 0 | 1637673.8629
6137 | 1213.9294 | 1116.7047 | 1116.7047 | 1087.068 | 1087.068 | 1860.2 | 2142076.0636 | 391344.4735 | 177518.2015 | 232537.0562 | 148757.4054
6138 | 1030.8817 | 140.6168 | 140.6168 | 136.8849 | 136.8849 | 1851.55 | 268134.6885 | 49278.5545 | 22353.2999 | 1638696.245 | 19890.8155
6139 | 1441.0183 | 0 | 0 | 0 | 0 | 1845.85 | 0 | 0 | 0 | 4896580.2276 | 0
6140 | 967.4928 | 0 | 0 | 0 | 0 | 1847.45 | 0 | 0 | 0 | 3287540.4026 | 0
6141 | 1176.0394 | 0 | 0 | 0 | 0 | 1852.45 | 0 | 0 | 0 | 3996181.8234 | 0
6142 | 1427.1132 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1865.15 | 611494.7182 | 111351.8261 | 50510.4255 | 3798293.0039 | 41247.1089
6143 | 1197.303 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1638.3 | 1042678.5068 | 215514.4963 | 97759.7701 | 2034218.0774 | 214126.4
6144 | 1134.3301 | 0 | 0 | 0 | 0 | 1091.3 | 0 | 0 | 0 | 2079226.9981 | 0
6145 | 1411.5744 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 2587415.8605 | 0
6146 | 1233.2875 | 0 | 0 | 0 | 0 | 301.8 | 0 | 0 | 0 | 2260615.9435 | 0
6147 | 1411.5744 | 0 | 0 | 0 | 0 | 292.85 | 0 | 0 | 0 | 2587415.8605 | 0
6148 | 1032.9192 | 0 | 0 | 0 | 0 | 285.95 | 0 | 0 | 0 | 1893340.8056 | 0
6149 | 981.3959 | 0 | 0 | 0 | 0 | 280.8 | 0 | 0 | 0 | 1798898.6284 | 0
6150 | 1022.2874 | 0 | 0 | 0 | 0 | 277.3 | 0 | 0 | 0 | 1873852.7382 | 0
6151 | 1038.644 | 429.9125 | 429.9125 | 418.5028 | 418.5028 | 279.95 | 125056.719 | 150661.0149 | 68341.5104 | 1136718.7148 | 704618.4825
6152 | 236.2455 | 787.9116 | 245.4135 | 767.0008 | 236.2455 | 297.55 | 74910.0532 | 85048.3794 | 38578.8899 | 0 | 402196.1488
6153 | 185.3969 | 1263.8119 | 192.5913 | 1230.2711 | 185.3969 | 325.05 | 64087.5815 | 66742.893 | 30275.3178 | 0 | 310530.5794
6154 | 160.3938 | 2489.7345 | 166.617 | 2423.6583 | 160.3938 | 339.05 | 57790.3932 | 57741.7754 | 26192.3109 | 0 | 266406.1162
6155 | 207.2309 | 3028.3527 | 215.2725 | 2947.9819 | 207.2309 | 346.25 | 76208.3147 | 74603.1378 | 33840.8122 | 0 | 342708.1644
6156 | 198.151 | 3529.363 | 205.8402 | 3435.6957 | 198.151 | 349.85 | 73656.338 | 71334.3535 | 32358.0554 | 0 | 326978.8429
6157 | 199.0353 | 3428.3341 | 206.7585 | 3337.348 | 199.0353 | 361.05 | 76275.3421 | 71652.6938 | 32502.4581 | 0 | 326208.8404
6158 | 150.5308 | 3259.0754 | 156.3723 | 3172.5813 | 150.5308 | 385.3 | 61658.857 | 54191.0851 | 24581.6783 | 0 | 243062.0698
6159 | 152.6909 | 1930.8555 | 158.6151 | 1879.6116 | 152.6909 | 390.7 | 63438.0862 | 54968.7187 | 24934.4216 | 0 | 245725.4416
6160 | 170.769 | 1682.6871 | 177.3956 | 1638.0295 | 170.769 | 1093.95 | 198294.7074 | 61476.8454 | 27886.5801 | 0 | 154725.266
6161 | 138.479 | 521.3429 | 143.8526 | 507.5067 | 138.479 | 1860.2 | 273530.5494 | 49852.4567 | 22613.6283 | 0 | 19359.3707
6162 | 137.6387 | 142.98 | 142.98 | 139.1854 | 137.6387 | 1481.7 | 216588.1659 | 49549.9414 | 22476.404 | 0 | 71337.7754
6163 | 108.4667 | 112.676 | 112.676 | 109.6857 | 108.4667 | 1470.45 | 169223.7482 | 39048.0242 | 17712.6176 | 0 | 57438.5589
6164 | 0 | 0 | 0 | 0 | 0 | 1439.3 | 0 | 0 | 0 | 0 | 0
6165 | 0 | 0 | 0 | 0 | 0 | 1404.5 | 0 | 0 | 0 | 0 | 0
6166 | 87.5078 | 90.9037 | 90.9037 | 88.4912 | 87.5078 | 1799.8 | 166891.2402 | 31502.8074 | 14290.0235 | 0 | 17519.0612
6167 | 89.1435 | 92.6022 | 92.6022 | 90.1446 | 89.1435 | 1107.65 | 104671.8502 | 32091.6449 | 14557.1267 | 0 | 79546.756
6168 | 92.4148 | 96.0011 | 96.0011 | 93.4533 | 92.4148 | 340.3 | 33445.0689 | 33269.32 | 15091.3332 | 0 | 153380.8065
6169 | 86.69 | 18.9925 | 18.9925 | 18.4884 | 18.4884 | 326.05 | 6451.1076 | 6655.8303 | 3019.1586 | 81159.8457 | 29458.1721
6170 | 89.1435 | 92.6022 | 92.6022 | 90.1446 | 89.1435 | 336 | 32107.2328 | 32091.6449 | 14557.1267 | 0 | 148333.952
6171 | 82.6008 | 85.8063 | 85.8063 | 83.5291 | 82.6008 | 325.8 | 28837.8493 | 29736.2948 | 13488.7137 | 0 | 138290.2912
6172 | 88.3256 | 91.7535 | 91.7535 | 89.3184 | 88.3256 | 316.55 | 30006.105 | 31797.2262 | 14423.5751 | 0 | 148691.7789
6173 | 83.4186 | 86.6561 | 86.6561 | 84.3562 | 83.4186 | 308.3 | 27522.7054 | 30030.7136 | 13622.2654 | 0 | 141119.3283
6174 | 88.3256 | 91.7535 | 91.7535 | 89.3184 | 88.3256 | 298.55 | 28197.5984 | 31797.2262 | 14423.5751 | 0 | 150281.6402
6175 | 70.3334 | 73.0623 | 73.0623 | 71.1232 | 70.3334 | 292.6 | 21968.4439 | 25320.0134 | 11485.4394 | 0 | 120087.197
6176 | 96.5407 | 752.9122 | 100.2872 | 732.9303 | 96.5407 | 299.25 | 30880.9663 | 34754.6626 | 15765.1011 | 0 | 164191.6457
6177 | 784.7098 | 1922.2864 | 815.1594 | 1871.2699 | 784.7098 | 314 | 262777.2432 | 282495.537 | 128143.1144 | 0 | 1323020.7651
6178 | 1340.7248 | 2564.837 | 1392.7515 | 2496.7676 | 1340.7248 | 327.25 | 467001.656 | 482660.9158 | 218940.3543 | 0 | 2242697.3523
6179 | 1486.7248 | 3111.3906 | 1544.416 | 3028.816 | 1486.7248 | 342.65 | 542789.9105 | 535220.9212 | 242782.1567 | 0 | 2464023.3158
6180 | 1306.7255 | 3166.521 | 1357.4321 | 3082.4833 | 1306.7255 | 347.95 | 485640.2748 | 470421.1919 | 213388.2795 | 0 | 2158775.9168
6181 | 1510.7833 | 3375.2262 | 1569.4086 | 3285.6496 | 1510.7833 | 354.75 | 572049.1372 | 543881.9851 | 246710.9116 | 0 | 2485616.2112
6182 | 1642.3118 | 3085.0621 | 1706.0415 | 3003.1862 | 1642.3118 | 365.6 | 639092.9817 | 591232.2502 | 268189.5179 | 0 | 2684194.4157
6183 | 1547.9905 | 2539.8911 | 1608.0594 | 2472.4838 | 1547.9905 | 359.45 | 592537.0508 | 557276.5663 | 252786.8424 | 0 | 2539555.7524
6184 | 1693.5468 | 1929.3243 | 1759.2647 | 1878.1211 | 1693.5468 | 346.2 | 624034.4326 | 609676.8494 | 276556.1931 | 0 | 2800787.7045
6185 | 1585.4113 | 1024.275 | 1024.275 | 997.0913 | 997.0913 | 1517.35 | 1605070.4348 | 358952.8632 | 162825.0071 | 1078390.5681 | 471066.4
6186 | 1638.605 | 141.5278 | 141.5278 | 137.7717 | 137.7717 | 1794.15 | 261949.6789 | 49597.8218 | 22498.123 | 2751027.3745 | 27760.5193
6187 | 1627.7258 | 0 | 0 | 0 | 0 | 1813.6 | 0 | 0 | 0 | 5531012.3024 | 0
6188 | 1555.5125 | 0 | 0 | 0 | 0 | 1062.7 | 0 | 0 | 0 | 5285631.3153 | 0
6189 | 1476.183 | 0 | 0 | 0 | 0 | 687.65 | 0 | 0 | 0 | 5016069.6743 | 0
6190 | 1661.8303 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1488.45 | 489676.0859 | 111351.8261 | 50510.4255 | 4595861.9782 | 156469.8447
6191 | 1613.5784 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1318.25 | 838843.3103 | 215514.4963 | 97759.7701 | 3448721.9342 | 403596
6192 | 1260.2759 | 0 | 0 | 0 | 0 | 521.45 | 0 | 0 | 0 | 2310085.655 | 0
6193 | 1171.9502 | 0 | 0 | 0 | 0 | 289.15 | 0 | 0 | 0 | 1394620.7785 | 0
6194 | 1521.1636 | 0 | 0 | 0 | 0 | 276.3 | 0 | 0 | 0 | 1810184.6804 | 0
6195 | 1377.2255 | 0 | 0 | 0 | 0 | 270.65 | 0 | 0 | 0 | 1638898.389 | 0
6196 | 1270.9077 | 0 | 0 | 0 | 0 | 266.45 | 0 | 0 | 0 | 1512380.1047 | 0
6197 | 1565.3264 | 0 | 0 | 0 | 0 | 263.3 | 0 | 0 | 0 | 1862738.4303 | 0
6198 | 1360.8689 | 0 | 0 | 0 | 0 | 262.05 | 0 | 0 | 0 | 1619434.0374 | 0
6199 | 1170.3146 | 300.4493 | 300.4493 | 292.4756 | 292.4756 | 265.5 | 82715.9951 | 105291.2089 | 47761.2623 | 1609078.8753 | 496566.536
6200 | 1033.4007 | 1073.5019 | 1073.5019 | 1045.0117 | 1033.4007 | 276.45 | 303020.8171 | 372024.234 | 168754.3261 | 0 | 1781117.6903
6201 | 1230.7481 | 1345.4713 | 1278.5069 | 1309.7633 | 1230.7481 | 294.1 | 382507.6442 | 443069.321 | 200981.167 | 0 | 2099533.2077
6202 | 1537.052 | 2339.0964 | 1596.6969 | 2277.018 | 1537.052 | 306.3 | 500338.4818 | 553338.7157 | 251000.5896 | 0 | 2603304.9521
6203 | 1548.9034 | 3030.2568 | 1609.0078 | 2949.8355 | 1548.9034 | 320.05 | 527691.7519 | 557605.2114 | 252935.9195 | 0 | 2602080.208
6204 | 1590.8468 | 3426.6429 | 1652.5794 | 3335.7017 | 1590.8468 | 320.45 | 543332.0799 | 572704.8455 | 259785.2813 | 0 | 2671906.7312
6205 | 1238.0554 | 3394.8544 | 1286.0974 | 3304.7568 | 1238.0554 | 314.5 | 414330.6678 | 445699.9526 | 202174.4507 | 0 | 2086742.4172
6206 | 1441.5264 | 3066.4976 | 1497.4641 | 2985.1144 | 1441.5264 | 325.1 | 497577.9925 | 518949.5004 | 235401.2595 | 0 | 2414412.5506
6207 | 1346.8708 | 2763.8959 | 1399.136 | 2690.5436 | 1346.8708 | 332.25 | 476011.7255 | 484873.4729 | 219943.9948 | 0 | 2246243.7067
6208 | 1554.022 | 1767.5346 | 1614.3254 | 1720.6252 | 1554.022 | 327.55 | 542281.6921 | 559447.9049 | 253771.7857 | 0 | 2599024.0237
6209 | 1638.7226 | 620.6152 | 620.6152 | 604.1444 | 604.1444 | 322.7 | 207938.3386 | 217491.9874 | 98656.782 | 1896381.7409 | 991896.5145
6210 | 1543.6519 | 78.0412 | 78.0412 | 75.9701 | 75.9701 | 688.75 | 55836.1612 | 27349.2264 | 12405.913 | 2690260.7423 | 97508.4837
6211 | 1296.4209 | 0 | 0 | 0 | 0 | 1356.4 | 0 | 0 | 0 | 4405238.14 | 0
6212 | 1246.3728 | 0 | 0 | 0 | 0 | 1419.45 | 0 | 0 | 0 | 4235174.6181 | 0
6213 | 1571.8691 | 0 | 0 | 0 | 0 | 1576.6 | 0 | 0 | 0 | 5341211.0353 | 0
6214 | 1827.8498 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1661.05 | 546617.5186 | 111351.8261 | 50510.4255 | 5159996.1304 | 103675.9923
6215 | 1962.7917 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1654.05 | 1052213.1842 | 215514.4963 | 97759.7701 | 4635348.9451 | 204802.4
6216 | 1447.5589 | 0 | 0 | 0 | 0 | 722.3 | 0 | 0 | 0 | 2653375.4765 | 0
6217 | 1347.7837 | 0 | 0 | 0 | 0 | 713.45 | 0 | 0 | 0 | 1603862.5566 | 0
6218 | 1417.2992 | 0 | 0 | 0 | 0 | 301.8 | 0 | 0 | 0 | 1686586.0492 | 0
6219 | 1479.4543 | 0 | 0 | 0 | 0 | 292.85 | 0 | 0 | 0 | 1760550.5849 | 0
6220 | 1595.5861 | 0 | 0 | 0 | 0 | 285.95 | 0 | 0 | 0 | 1898747.4804 | 0
6221 | 1610.3071 | 0 | 0 | 0 | 0 | 280.8 | 0 | 0 | 0 | 1916265.3966 | 0
6222 | 1157.2293 | 0 | 0 | 0 | 0 | 277.3 | 0 | 0 | 0 | 1377102.8622 | 0
6223 | 1109.7952 | 231.2909 | 231.2909 | 225.1526 | 225.1526 | 279.95 | 67582.3424 | 81054.9292 | 36767.4165 | 1621549.8506 | 379081.8195
6224 | 994.4167 | 848.5466 | 848.5466 | 826.0267 | 826.0267 | 297.55 | 263245.1181 | 297369.5959 | 134890.1528 | 308659.0319 | 1376521.0548
6225 | 1024.9954 | 1064.7697 | 1064.7697 | 1036.5113 | 1024.9954 | 325.05 | 354968.1103 | 368998.3451 | 167381.7493 | 0 | 1716815.3753
6226 | 1252.2468 | 1994.6391 | 1300.8401 | 1941.7025 | 1252.2468 | 339.05 | 450982.8138 | 450808.8541 | 204491.9052 | 0 | 2079919.3507
6227 | 1666.1761 | 3225.1293 | 1730.8326 | 3139.5361 | 1666.1761 | 346.25 | 613487.6214 | 599823.3895 | 272086.5542 | 0 | 2755438.6956
6228 | 1295.9036 | 3590.5133 | 1346.1902 | 3495.223 | 1295.9036 | 349.85 | 482748.4674 | 466525.2956 | 211621.0577 | 0 | 2138435.3239
6229 | 1418.6527 | 3345.585 | 1473.7024 | 3256.795 | 1418.6527 | 361.05 | 543980.6124 | 510714.9756 | 231665.9875 | 0 | 2325100.8591
6230 | 1542.1992 | 3365.4448 | 1602.0447 | 3276.1278 | 1542.1992 | 385.3 | 632978.2255 | 555191.7138 | 251841.1302 | 0 | 2490189.0563
6231 | 1525.4623 | 2684.3764 | 1584.6572 | 2613.1345 | 1525.4623 | 1329.65 | 2154697.1461 | 549166.4338 | 249107.9962 | 0 | 1022593.6635
6232 | 1140.3677 | 2088.7777 | 1184.6197 | 2033.3427 | 1140.3677 | 1561 | 1891965.3306 | 410532.3677 | 186222.0435 | 0 | 500621.415
6233 | 1753.2821 | 1159.2323 | 1159.2323 | 1128.4669 | 1128.4669 | 1640.65 | 1968135.6386 | 406248.1018 | 184278.6529 | 1145286.2111 | 396936.5726
6234 | 1615.8908 | 119.8822 | 119.8822 | 116.7006 | 116.7006 | 1615.65 | 200061.9304 | 42012.2212 | 19057.2103 | 2748015.5902 | 43905.0692
6235 | 1178.4929 | 0 | 0 | 0 | 0 | 1796.75 | 0 | 0 | 0 | 4004518.7825 | 0
6236 | 1647.9272 | 0 | 0 | 0 | 0 | 1798.35 | 0 | 0 | 0 | 5599656.7309 | 0
6237 | 1432.0201 | 0 | 0 | 0 | 0 | 1718.25 | 0 | 0 | 0 | 4866004.4323 | 0
6238 | 1643.0203 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1805.35 | 591209.0395 | 111351.8261 | 50510.4255 | 4531945.2992 | 59538.3741
6239 | 1400.1248 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1698.6 | 1077905.3208 | 215514.4963 | 97759.7701 | 2723406.598 | 178428.8
6240 | 1198.1208 | 0 | 0 | 0 | 0 | 1279.25 | 0 | 0 | 0 | 2196155.4081 | 0
6241 | 1325.7023 | 0 | 0 | 0 | 0 | 667.5 | 0 | 0 | 0 | 1577585.6811 | 0
6242 | 1425.4775 | 0 | 0 | 0 | 0 | 301.8 | 0 | 0 | 0 | 1696318.225 | 0
6243 | 1218.5665 | 0 | 0 | 0 | 0 | 292.85 | 0 | 0 | 0 | 1450094.1802 | 0
6244 | 1399.3069 | 0 | 0 | 0 | 0 | 285.95 | 0 | 0 | 0 | 1665175.2634 | 0
6245 | 1315.0705 | 0 | 0 | 0 | 0 | 280.8 | 0 | 0 | 0 | 1564933.8533 | 0
6246 | 733.5934 | 0 | 0 | 0 | 0 | 277.3 | 0 | 0 | 0 | 872976.1606 | 0
6247 | 983.0315 | 463.2197 | 463.2197 | 450.9261 | 450.9261 | 629.45 | 303272.8739 | 162333.3819 | 73636.2258 | 975349.3231 | 604944.3234
6248 | 877.8811 | 1077.0411 | 911.947 | 1048.457 | 877.8811 | 653.1 | 611628.9601 | 316037.1943 | 143357.9829 | 0 | 1182418.0474
6249 | 945.2549 | 2370.6937 | 981.9354 | 2307.7768 | 945.2549 | 1115.95 | 1121952.2288 | 340291.7799 | 154360.1324 | 0 | 835652.6334
6250 | 1289.4335 | 2157.9652 | 1339.4691 | 2100.694 | 1289.4335 | 1179.45 | 1617501.0707 | 464196.0751 | 210564.4974 | 0 | 1058044.6929
6251 | 942.1656 | 2944.3082 | 978.7255 | 2866.1679 | 942.1656 | 701.8 | 702824.3959 | 339179.613 | 153855.6411 | 0 | 1223119.3711
6252 | 1192.4164 | 4331.5675 | 1238.6884 | 4216.6101 | 1192.4164 | 349.85 | 444302.0243 | 429269.9137 | 194721.6025 | 0 | 1967665.967
6253 | 1457.5078 | 2719.4527 | 1514.0662 | 2647.2799 | 1457.5078 | 361.05 | 560436.7447 | 524702.8109 | 238011.025 | 0 | 2388782.4219
6254 | 1298.3816 | 1815.4734 | 1348.7643 | 1767.2917 | 1298.3816 | 385.3 | 533973.2052 | 467417.3846 | 212025.7192 | 0 | 2096496.8083
6255 | 1441.2678 | 773.3974 | 773.3974 | 752.8719 | 752.8719 | 1141.7 | 916104.5648 | 271033.87 | 122943.9749 | 1261829.666 | 632520.7518
6256 | 1536.8077 | 96.6286 | 96.6286 | 94.0641 | 94.0641 | 1161.95 | 116155.6648 | 33863.0793 | 15360.669 | 2644548.9307 | 77163.4537
6257 | 1458.4473 | 20.6816 | 20.6816 | 20.1327 | 20.1327 | 1356 | 28995.348 | 7247.7671 | 3287.6677 | 2636430.6686 | 12691.308
6258 | 1564.8337 | 0 | 0 | 0 | 0 | 1534.1 | 0 | 0 | 0 | 2868340.1153 | 0
6259 | 1103.6522 | 0 | 0 | 0 | 0 | 1609.95 | 0 | 0 | 0 | 3750210.3013 | 0
6260 | 1320.7953 | 0 | 0 | 0 | 0 | 1358.45 | 0 | 0 | 0 | 4488062.3411 | 0
6261 | 1423.8418 | 0 | 0 | 0 | 0 | 739 | 0 | 0 | 0 | 4838214.5723 | 0
6262 | 1526.8884 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1196.65 | 393059.9395 | 111351.8261 | 50510.4255 | 4137329.2932 | 245723.8779
6263 | 1557.9659 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 752.1 | 477719.1975 | 215514.4963 | 97759.7701 | 3259750.8902 | 738756.8
6264 | 1416.4814 | 0 | 0 | 0 | 0 | 340.3 | 0 | 0 | 0 | 2596410.353 | 0
6265 | 1565.3264 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 1862738.4303 | 0
6266 | 1530.9776 | 0 | 0 | 0 | 0 | 301.8 | 0 | 0 | 0 | 1821863.2916 | 0
6267 | 1518.7101 | 0 | 0 | 0 | 0 | 292.85 | 0 | 0 | 0 | 1807265.0285 | 0
6268 | 1445.1054 | 0 | 0 | 0 | 0 | 285.95 | 0 | 0 | 0 | 1719675.4474 | 0
6269 | 1521.9814 | 0 | 0 | 0 | 0 | 280.8 | 0 | 0 | 0 | 1811157.8981 | 0
6270 | 1328.1557 | 0 | 0 | 0 | 0 | 277.3 | 0 | 0 | 0 | 1580505.3342 | 0
6271 | 1128.6053 | 165.6748 | 165.6748 | 161.2779 | 161.2779 | 279.95 | 48215.0469 | 58060.0421 | 26336.6802 | 1773111.042 | 271537.4133
6272 | 1388.3388 | 620.0594 | 620.0594 | 603.6034 | 603.6034 | 297.55 | 191159.3084 | 217297.2234 | 98568.435 | 1438420.0333 | 1005867.0458
6273 | 1708.9138 | 1481.5402 | 1481.5402 | 1442.2209 | 1442.2209 | 680.6 | 1042980.2264 | 519199.5406 | 235514.6805 | 488848.0527 | 1862614.1322
6274 | 1431.3986 | 1991.9538 | 1486.943 | 1939.0884 | 1431.3986 | 695.55 | 1058864.68 | 515303.492 | 233747.3896 | 0 | 1867187.8894
6275 | 1533.1581 | 2508.9275 | 1592.6518 | 2442.3419 | 1533.1581 | 545.75 | 891398.0436 | 551936.9142 | 250364.7169 | 0 | 2229595.1597
6276 | 1365.5684 | 2575.8016 | 1418.5596 | 2507.4412 | 1365.5684 | 599.35 | 872246.5997 | 491604.6218 | 222997.3187 | 0 | 1912683.3711
6277 | 1628.745 | 3282.1337 | 1691.948 | 3195.0277 | 1628.745 | 361.05 | 625400.3405 | 586348.2108 | 265974.0634 | 0 | 2669431.6669
6278 | 1656.7966 | 266.8274 | 266.8274 | 259.7459 | 259.7459 | 385.3 | 106487.694 | 93508.5363 | 42416.5111 | 2560793.863 | 410540.7044
6279 | 1559.5597 | 169.0811 | 169.0811 | 164.5937 | 164.5937 | 390.7 | 68427.807 | 59253.7449 | 26878.1571 | 2556972.5921 | 259277.5416
6280 | 1548.5916 | 75.5159 | 75.5159 | 73.5118 | 73.5118 | 776.4 | 60614.4416 | 26464.2336 | 12004.4704 | 2703821.2861 | 88046.5852
6281 | 1862.9184 | 139.553 | 139.553 | 135.8494 | 135.8494 | 1389.05 | 200402.207 | 48905.7727 | 22184.2019 | 3165717.4467 | 81241.0763
6282 | 1641.6575 | 9.6578 | 9.6578 | 9.4015 | 9.4015 | 1672.5 | 16656.3388 | 3384.5241 | 1535.2577 | 2991925.4059 | 3013.655
6283 | 1998.0095 | 0 | 0 | 0 | 0 | 1835.8 | 0 | 0 | 0 | 6789236.4101 | 0
6284 | 1726.4389 | 0 | 0 | 0 | 0 | 1417.5 | 0 | 0 | 0 | 5866439.3822 | 0
6285 | 1521.9814 | 0 | 0 | 0 | 0 | 1252.55 | 0 | 0 | 0 | 5171692.8889 | 0
6286 | 1737.8885 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1353.75 | 443448.7036 | 111351.8261 | 50510.4255 | 4854307.6738 | 197671.0725
6287 | 1565.3264 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 713.15 | 452984.874 | 215514.4963 | 97759.7701 | 3284761.7639 | 761815.2
6288 | 1698.6327 | 0 | 0 | 0 | 0 | 340.3 | 0 | 0 | 0 | 3113593.7098 | 0
6289 | 692.7019 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 824315.2822 | 0
6290 | 512.7793 | 0 | 0 | 0 | 0 | 301.8 | 0 | 0 | 0 | 610207.4166 | 0
6291 | 606.0119 | 0 | 0 | 0 | 0 | 292.85 | 0 | 0 | 0 | 721154.2197 | 0
6292 | 754.857 | 0 | 0 | 0 | 0 | 285.95 | 0 | 0 | 0 | 898279.8175 | 0
6293 | 802.2911 | 0 | 0 | 0 | 0 | 280.8 | 0 | 0 | 0 | 954726.4366 | 0
6294 | 671.4383 | 0 | 0 | 0 | 0 | 277.3 | 0 | 0 | 0 | 799011.6253 | 0
6295 | 609.2833 | 407.7527 | 407.7527 | 396.9311 | 396.9311 | 279.95 | 118185.3461 | 142895.2121 | 64818.8559 | 389241.4434 | 668299.6268
6296 | 469.188 | 351.9834 | 351.9834 | 342.642 | 342.642 | 297.55 | 108233.0254 | 123351.1053 | 55953.4319 | 231958.8676 | 570991.5153
6297 | 557.6649 | 886.6396 | 579.305 | 863.1087 | 557.6649 | 325.05 | 192007.1854 | 200759.3687 | 91066.6803 | 0 | 934060.846
6298 | 672.0078 | 2054.708 | 698.0841 | 2000.1772 | 672.0078 | 339.05 | 241886.4733 | 241922.7917 | 109738.8663 | 0 | 1116171.2802
6299 | 802.2369 | 4128.0906 | 833.3676 | 4018.5333 | 802.2369 | 346.25 | 295791.6702 | 288805.2991 | 131005.2926 | 0 | 1326699.3427
6300 | 773.4902 | 4347.7895 | 803.5051 | 4232.4015 | 773.4902 | 349.85 | 288635.9014 | 278456.4797 | 126310.9531 | 0 | 1276374.8887
6301 | 936.0094 | 4280.4885 | 972.3316 | 4166.8866 | 936.0094 | 361.05 | 359858.1457 | 336963.3758 | 152850.3313 | 0 | 1534072.5688
6302 | 851.9365 | 3878.0638 | 884.9952 | 3775.1421 | 851.9365 | 385.3 | 349066.535 | 306697.1272 | 139121.2246 | 0 | 1375621.8091
6303 | 657.248 | 2689.2494 | 682.7523 | 2617.8782 | 657.248 | 390.7 | 272784.8785 | 236609.2691 | 107328.5935 | 0 | 1057709.1576
6304 | 682.6487 | 764.1832 | 709.139 | 743.9022 | 682.6487 | 380.95 | 276248.6752 | 245753.5478 | 111476.5399 | 0 | 1105242.4486
6305 | 686.5273 | 262.4571 | 262.4571 | 255.4917 | 255.4917 | 1306.5 | 353731.0239 | 91977 | 41721.7892 | 790088.3196 | 173435.3345
6306 | 776.4017 | 24.8451 | 24.8451 | 24.1857 | 24.1857 | 1476.55 | 37805.1775 | 8706.8585 | 3949.5277 | 1378811.8872 | 12392.1553
6307 | 785.1463 | 0 | 0 | 0 | 0 | 1791.75 | 0 | 0 | 0 | 2667927.2694 | 0
6308 | 546.3104 | 0 | 0 | 0 | 0 | 1448.55 | 0 | 0 | 0 | 1856362.6281 | 0
6309 | 724.5973 | 0 | 0 | 0 | 0 | 1396.1 | 0 | 0 | 0 | 2462181.5693 | 0
6310 | 823.5547 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1466.25 | 479681.5151 | 111351.8261 | 50510.4255 | 1747401.3579 | 163260.2475
6311 | 729.5043 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1237.65 | 783297.6676 | 215514.4963 | 97759.7701 | 444638.1013 | 451311.2
6312 | 745.043 | 0 | 0 | 0 | 0 | 735.75 | 0 | 0 | 0 | 1365663.8755 | 0
6313 | 1741.9777 | 0 | 0 | 0 | 0 | 1069.95 | 0 | 0 | 0 | 3193045.0654 | 0
6314 | 1703.5397 | 0 | 0 | 0 | 0 | 1092.7 | 0 | 0 | 0 | 3122588.2023 | 0
6315 | 1585.7722 | 0 | 0 | 0 | 0 | 649.35 | 0 | 0 | 0 | 2906720.3674 | 0
6316 | 1660.1947 | 0 | 0 | 0 | 0 | 285.95 | 0 | 0 | 0 | 3043136.8466 | 0
6317 | 1616.0319 | 0 | 0 | 0 | 0 | 280.8 | 0 | 0 | 0 | 2962186.4085 | 0
6318 | 1492.5396 | 0 | 0 | 0 | 0 | 1028.3 | 0 | 0 | 0 | 2735824.997 | 0
6319 | 1496.6287 | 342.9645 | 342.9645 | 333.8624 | 333.8624 | 1267.9 | 447827.2511 | 120190.4687 | 54519.7321 | 2131350.6057 | 239250.28
6320 | 112.7164 | 567.2892 | 117.0899 | 552.2336 | 112.7164 | 1137.95 | 135749.7155 | 40577.8977 | 18406.5853 | 0 | 97167.1575
6321 | 91.689 | 1017.3046 | 95.248 | 990.3059 | 91.689 | 1412.55 | 137243.0776 | 33008.0233 | 14972.8061 | 0 | 53862.6758
6322 | 0 | 1928.7155 | 0 | 1877.5285 | 0 | 1140.5 | 0 | 0 | 0 | 0 | 0
6323 | 0 | 2583.8855 | 0 | 2515.3106 | 0 | 346.25 | 0 | 0 | 0 | 0 | 0
6324 | 0 | 2659.0171 | 0 | 2588.4482 | 0 | 349.85 | 0 | 0 | 0 | 0 | 0
6325 | 0 | 1067.4415 | 0 | 1039.1122 | 0 | 361.05 | 0 | 0 | 0 | 0 | 0
6326 | 89.7711 | 498.805 | 93.2556 | 485.5669 | 89.7711 | 1226.4 | 117041.7795 | 32317.6113 | 14659.6276 | 0 | 69446.9559
6327 | 73.0251 | 612.365 | 75.8587 | 596.1132 | 73.0251 | 1505.7 | 116813.8995 | 26289.0192 | 11924.9912 | 0 | 36096.2838
6328 | 78.3215 | 468.4542 | 81.3613 | 456.0217 | 78.3215 | 1410 | 117128.8389 | 28195.7487 | 12789.9049 | 0 | 46209.6992
6329 | 73.0629 | 363.8466 | 75.8972 | 354.1903 | 73.0629 | 1822.45 | 140826.8932 | 26302.636 | 11931.168 | 0 | 12972.314
6330 | 85.2782 | 88.5872 | 88.5872 | 86.2361 | 85.2782 | 1846.5 | 166268.3611 | 30700.1483 | 13925.9284 | 0 | 13090.173
6331 | 79.3551 | 82.4344 | 82.4344 | 80.2466 | 79.3551 | 1845.85 | 154486.4863 | 28567.8204 | 12958.6807 | 0 | 12232.5732
6332 | 88.3256 | 91.7535 | 91.7535 | 89.3184 | 88.3256 | 1668.4 | 155515.856 | 31797.2262 | 14423.5751 | 0 | 29288.7783
6333 | 80.9652 | 84.1068 | 84.1068 | 81.8747 | 80.9652 | 1592.65 | 136023.7662 | 29147.4573 | 13221.6105 | 0 | 32981.0927
6334 | 88.3256 | 91.7535 | 91.7535 | 89.3184 | 88.3256 | 1761.15 | 164168.8171 | 31797.2262 | 14423.5751 | 0 | 21096.5763
6335 | 80.9652 | 84.1068 | 84.1068 | 81.8747 | 80.9652 | 1548.2 | 132464.1134 | 29147.4573 | 13221.6105 | 0 | 36579.987
6336 | 85.8721 | 89.2042 | 89.2042 | 86.8368 | 85.8721 | 1369.35 | 124319.4297 | 30913.9699 | 14022.9202 | 0 | 54155.1768
6337 | 76.876 | 0 | 0 | 0 | 0 | 723.9 | 0 | 0 | 0 | 91482.4516 | 0
6338 | 83.4186 | 23.1903 | 23.1903 | 22.5748 | 22.5748 | 336 | 8035.724 | 8126.9352 | 3686.4681 | 72404.1565 | 36556.416
6339 | 77.6938 | 80.7089 | 80.7089 | 78.5669 | 77.6938 | 325.8 | 26826.7949 | 27969.7823 | 12687.404 | 0 | 130075.0264
6340 | 81.783 | 84.9566 | 84.9566 | 82.7019 | 81.783 | 316.55 | 27399.4041 | 29441.8761 | 13355.1621 | 0 | 137677.573
6341 | 78.5117 | 81.5586 | 81.5586 | 79.3941 | 78.5117 | 308.3 | 25621.6938 | 28264.201 | 12820.9556 | 0 | 132818.1914
6342 | 83.4186 | 86.6561 | 86.6561 | 84.3562 | 83.4186 | 298.55 | 26352.5397 | 30030.7136 | 13622.2654 | 0 | 141932.6602
6343 | 68.6977 | 71.3638 | 71.3638 | 69.4699 | 68.6977 | 690.45 | 50096.9248 | 24731.1759 | 11218.3362 | 0 | 89963.0872
6344 | 80.819 | 631.0604 | 83.9552 | 614.3124 | 80.819 | 657.15 | 56084.9024 | 29094.83 | 13197.7381 | 0 | 108527.7567
6345 | 556.7111 | 1803.1988 | 578.314 | 1755.3429 | 556.7111 | 1029.8 | 607021.6457 | 200416.0028 | 90910.9257 | 0 | 540121.1276
6346 | 1538.6406 | 1920.8674 | 1598.3476 | 1869.8886 | 1538.6406 | 685.15 | 1118620.2178 | 553910.6239 | 251260.0136 | 0 | 2023081.6218
6347 | 1710.5127 | 2283.4372 | 1776.889 | 2222.8361 | 1710.5127 | 342.65 | 622094.8039 | 615784.5666 | 279326.7215 | 0 | 2834918.1985
6348 | 1592.0899 | 3073.9728 | 1653.8707 | 2992.3913 | 1592.0899 | 347.95 | 588718.7763 | 573152.3622 | 259988.2799 | 0 | 2630212.111
6349 | 1586.6892 | 3085.1857 | 1648.2601 | 3003.3066 | 1586.6892 | 354.75 | 598314.9766 | 571208.0944 | 259106.3384 | 0 | 2610500.3257
6350 | 1637.1595 | 3263.1797 | 1700.6896 | 3176.5767 | 1637.1595 | 1285.1 | 2236580.9831 | 589377.4121 | 267348.1428 | 0 | 1170405.3108
6351 | 1737.0911 | 1804.4994 | 1804.4994 | 1756.609 | 1737.0911 | 1487.45 | 2745563.6216 | 625352.8082 | 283666.9822 | 0 | 890346.0607
6352 | 1235.9792 | 1449.8338 | 1283.9409 | 1411.356 | 1235.9792 | 1483.75 | 1949298.6774 | 444952.4969 | 201835.3965 | 0 | 638074.2403
6353 | 1637.9753 | 725.7599 | 725.7599 | 706.4986 | 706.4986 | 1780.9 | 1335252.1789 | 254339.5056 | 115371.2257 | 1707396.6746 | 151519.4814
6354 | 1283.7711 | 59.1579 | 59.1579 | 57.5878 | 57.5878 | 1755.5 | 107019.5259 | 20731.6208 | 9404.0936 | 2247593.9107 | 13782.465
6355 | 1342.5199 | 0 | 0 | 0 | 0 | 1830.45 | 0 | 0 | 0 | 4561882.6304 | 0
6356 | 1375.5899 | 0 | 0 | 0 | 0 | 1509.6 | 0 | 0 | 0 | 4674254.402 | 0
6357 | 1208.7526 | 0 | 0 | 0 | 0 | 1466.2 | 0 | 0 | 0 | 4107341.2634 | 0
6358 | 1334.6984 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1390.5 | 454447.2307 | 111351.8261 | 50510.4255 | 3484267.5883 | 186430.203
6359 | 1426.2953 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1268.3 | 804047.7279 | 215514.4963 | 97759.7701 | 2812334.1473 | 433166.4
6360 | 1445.9232 | 0 | 0 | 0 | 0 | 1077.7 | 0 | 0 | 0 | 2650377.3118 | 0
6361 | 1568.5977 | 0 | 0 | 0 | 0 | 700.5 | 0 | 0 | 0 | 1866631.2999 | 0
6362 | 1526.8884 | 0 | 0 | 0 | 0 | 1099 | 0 | 0 | 0 | 1816997.2043 | 0
6363 | 1723.1676 | 0 | 0 | 0 | 0 | 270.65 | 0 | 0 | 0 | 2050569.4214 | 0
6364 | 1466.369 | 0 | 0 | 0 | 0 | 266.45 | 0 | 0 | 0 | 1744979.104 | 0
6365 | 1491.7217 | 0 | 0 | 0 | 0 | 263.3 | 0 | 0 | 0 | 1775148.848 | 0
6366 | 1755.8808 | 0 | 0 | 0 | 0 | 262.05 | 0 | 0 | 0 | 2089498.1234 | 0
6367 | 1216.9309 | 27.0058 | 27.0058 | 26.2891 | 26.2891 | 265.5 | 7418.241 | 9464.0716 | 4293.008 | 2182446.4017 | 0
6368 | 1615.258 | 374.995 | 374.995 | 365.0428 | 365.0428 | 276.45 | 106839.97 | 131415.4248 | 59611.4968 | 2291644.3634 | 541828.9664
6369 | 1535.5124 | 1121.3357 | 1121.3357 | 1091.5761 | 1091.5761 | 294.1 | 339640.1038 | 392967.3851 | 178254.3722 | 813735.3358 | 1822730.2674
6370 | 1473.9411 | 1184.4971 | 1184.4971 | 1153.0612 | 1153.0612 | 306.3 | 373553.4436 | 415102.0344 | 188294.895 | 588172.8024 | 1911628.379
6371 | 1908.6882 | 1982.7542 | 1982.7542 | 1930.1329 | 1908.6882 | 320.05 | 645750.797 | 687127.7527 | 311688.7834 | 0 | 3206500.7449
6372 | 2013.4594 | 2091.5908 | 2091.5908 | 2036.0811 | 2013.4594 | 320.45 | 682290.7147 | 724845.3721 | 328797.9146 | 0 | 3381705.0634
6373 | 2035.7422 | 859.4229 | 859.4229 | 836.6143 | 836.6143 | 314.5 | 279038.4182 | 301181.1445 | 136619.1136 | 2198001.3945 | 1380284.6035
6374 | 1841.9829 | 1913.4607 | 1913.4607 | 1862.6785 | 1841.9829 | 325.1 | 637836.8455 | 663113.8544 | 300795.8123 | 0 | 3085135.6518
6375 | 1628.7921 | 1238.4807 | 1238.4807 | 1205.6121 | 1205.6121 | 332.25 | 426802.2931 | 434020.3483 | 196876.4524 | 775688.8987 | 1968126.7848
6376 | 1389.4705 | 1359.9003 | 1359.9003 | 1323.8093 | 1323.8093 | 327.55 | 462666.9102 | 476571.3557 | 216178.0622 | 120356.9314 | 2167172.4172
6377 | 1931.9585 | 574.2201 | 574.2201 | 558.9806 | 558.9806 | 322.7 | 191072.8795 | 201233.0204 | 91281.534 | 2516668.5213 | 917744.7588
6378 | 1367.8348 | 51.7117 | 51.7117 | 50.3393 | 50.3393 | 1352.55 | 71835.7274 | 18122.148 | 8220.4077 | 2414969.2606 | 31903.0988
6379 | 1384.0595 | 0 | 0 | 0 | 0 | 1775.4 | 0 | 0 | 0 | 4703034.2761 | 0
6380 | 1184.2177 | 0 | 0 | 0 | 0 | 1304.3 | 0 | 0 | 0 | 4023971.6834 | 0
6381 | 1696.1792 | 0 | 0 | 0 | 0 | 315.5 | 0 | 0 | 0 | 5763616.9012 | 0
6382 | 1602.9466 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 319.1 | 104944.9602 | 111351.8261 | 50510.4255 | 4395774.9889 | 514143.6066
6383 | 1638.9311 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 312.1 | 199030.6932 | 215514.4963 | 97759.7701 | 3534870.5005 | 999236.8
6384 | 1551.4233 | 0 | 0 | 0 | 0 | 297.8 | 0 | 0 | 0 | 2843758.9144 | 0
6385 | 1701.0862 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 2024292.5471 | 0
6386 | 1653.652 | 0 | 0 | 0 | 0 | 301.8 | 0 | 0 | 0 | 1967845.9276 | 0
6387 | 1684.7296 | 0 | 0 | 0 | 0 | 292.85 | 0 | 0 | 0 | 2004828.1954 | 0
6388 | 1203.0278 | 0 | 0 | 0 | 0 | 285.95 | 0 | 0 | 0 | 1431603.0463 | 0
6389 | 1548.9698 | 0 | 0 | 0 | 0 | 280.8 | 0 | 0 | 0 | 1843274.0787 | 0
6390 | 1546.5163 | 0 | 0 | 0 | 0 | 277.3 | 0 | 0 | 0 | 1840354.4256 | 0
6391 | 1351.055 | 0 | 0 | 0 | 0 | 279.95 | 0 | 0 | 0 | 2476483.7783 | 0
6392 | 1371.2114 | 118.6159 | 118.6159 | 115.4679 | 115.4679 | 297.55 | 36436.9393 | 41568.4506 | 18855.9111 | 2301777.8386 | 83302.581
6393 | 1665.9839 | 856.0925 | 856.0925 | 833.3723 | 833.3723 | 1115.95 | 983899.8007 | 300014.017 | 136089.6916 | 1526177.1043 | 721158.4832
6394 | 1480.4755 | 1535.8832 | 1535.8832 | 1495.1217 | 1480.4755 | 339.05 | 531867.4567 | 532971.1937 | 241761.6554 | 0 | 2430792.0203
6395 | 1901.1918 | 1974.9673 | 1974.9673 | 1922.5527 | 1901.1918 | 346.25 | 697125.6822 | 684429.0368 | 310464.6159 | 0 | 3144095.888
6396 | 1801.945 | 1871.869 | 1871.869 | 1822.1906 | 1801.945 | 349.85 | 668387.0124 | 648700.2162 | 294257.6258 | 0 | 2973479.5417
6397 | 1608.8247 | 1671.255 | 1671.255 | 1626.9009 | 1608.8247 | 361.05 | 615161.0993 | 579176.906 | 262721.0799 | 0 | 2636783.306
6398 | 1764.516 | 1305.9178 | 1305.9178 | 1271.2595 | 1271.2595 | 385.3 | 519127.9707 | 457653.4058 | 207596.6699 | 904139.3064 | 2009281.0096
6399 | 1869.6654 | 939.3143 | 939.3143 | 914.3854 | 914.3854 | 390.7 | 378700.0365 | 329178.7346 | 149319.1316 | 1751028.3776 | 1440392.6999
6400 | 1735.3911 | 1074.7277 | 1074.7277 | 1046.205 | 1046.205 | 776.4 | 859398.6636 | 376633.7889 | 170845.2715 | 1263278.1245 | 1253056.9464
6401 | 1870.3575 | 368.4422 | 368.4422 | 358.664 | 358.664 | 1446.6 | 549103.9946 | 129119.0304 | 58569.8269 | 2770934.3039 | 194286.0118
6402 | 1742.4091 | 27.5834 | 27.5834 | 26.8513 | 26.8513 | 1755.2 | 49805.7027 | 9666.4804 | 4384.8229 | 3144617.3346 | 6434.0784
6403 | 1712.774 | 0 | 0 | 0 | 0 | 1845.85 | 0 | 0 | 0 | 5820006.001 | 0
6404 | 1736.2529 | 0 | 0 | 0 | 0 | 1557.95 | 0 | 0 | 0 | 5899787.2149 | 0
6405 | 1571.8691 | 0 | 0 | 0 | 0 | 1252.55 | 0 | 0 | 0 | 5341211.0353 | 0
6406 | 1566.1442 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1265.25 | 412539.7804 | 111351.8261 | 50510.4255 | 4270720.6172 | 224740.9215
6407 | 1353.5085 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 752.1 | 475750.2441 | 215514.4963 | 97759.7701 | 2565004.397 | 738756.8
6408 | 390.9227 | 0 | 0 | 0 | 0 | 340.3 | 0 | 0 | 0 | 716561.2871 | 0
6409 | 403.1901 | 0 | 0 | 0 | 0 | 318 | 0 | 0 | 0 | 479796.2622 | 0
6410 | 386.8335 | 0 | 0 | 0 | 0 | 301.8 | 0 | 0 | 0 | 460331.9108 | 0
6411 | 365.57 | 0 | 0 | 0 | 0 | 292.85 | 0 | 0 | 0 | 435028.2539 | 0
6412 | 375.3839 | 0 | 0 | 0 | 0 | 285.95 | 0 | 0 | 0 | 446706.8648 | 0
6413 | 388.4692 | 0 | 0 | 0 | 0 | 280.8 | 0 | 0 | 0 | 462278.346 | 0
6414 | 406.4615 | 0 | 0 | 0 | 0 | 277.3 | 0 | 0 | 0 | 483689.1325 | 0
6415 | 362.2986 | 237.7783 | 237.7783 | 231.4677 | 231.4677 | 635.5 | 156082.6238 | 83328.3887 | 37798.683 | 239813.0311 | 309156.1295
6416 | 452.8416 | 470.4134 | 470.4134 | 457.9289 | 452.8416 | 693 | 332032.9554 | 163022.9801 | 73949.0351 | 0 | 591863.187
6417 | 1718.3751 | 1785.0561 | 1785.0561 | 1737.6817 | 1718.3751 | 1077 | 1961688.8618 | 618615.0349 | 280610.6533 | 0 | 1586060.125
6418 | 1870.1756 | 1999.2525 | 1942.7477 | 1946.1934 | 1870.1756 | 339.05 | 671474.9053 | 673263.2052 | 305399.6706 | 0 | 3106268.113
6419 | 1892.5228 | 2313.2333 | 1965.9619 | 2251.8413 | 1892.5228 | 346.25 | 693740.4608 | 681308.1979 | 309048.9687 | 0 | 3129759.5342
6420 | 1967.7386 | 2044.0966 | 2044.0966 | 1989.8474 | 1967.7386 | 349.85 | 729249.4801 | 708385.8913 | 321331.7113 | 0 | 3247063.8293
6421 | 1715.3512 | 2769.9781 | 1781.9148 | 2696.4643 | 1715.3512 | 361.05 | 655187.471 | 617526.4216 | 280116.8462 | 0 | 2811374.8017
6422 | 1757.0441 | 2517.5308 | 1825.2257 | 2450.7169 | 1757.0441 | 385.3 | 719479.5465 | 632535.89 | 286925.3079 | 0 | 2837099.1712
6423 | 1950.1113 | 1100.0516 | 1100.0516 | 1070.8569 | 1070.8569 | 390.7 | 444230.9772 | 385508.472 | 174870.9263 | 1611673.3505 | 1686874.6972
6424 | 1726.1516 | 1518.1716 | 1518.1716 | 1477.8801 | 1477.8801 | 1346.4 | 2111984.4658 | 532036.8508 | 241337.8271 | 455081.6518 | 945508.8712
6425 | 2137.608 | 1036.6825 | 1036.6825 | 1009.1695 | 1009.1695 | 1577.8 | 1687535.7823 | 363301.0137 | 164797.3765 | 2068427.7822 | 417058.4484
6426 | 1644.1407 | 74.5581 | 74.5581 | 72.5794 | 72.5794 | 1552.8 | 118930.8715 | 26128.5844 | 11852.2162 | 2880671.8208 | 31770.8768
6427 | 1812.7762 | 0 | 0 | 0 | 0 | 1845.85 | 0 | 0 | 0 | 6159813.4562 | 0
6428 | 1637.2954 | 0 | 0 | 0 | 0 | 1762.45 | 0 | 0 | 0 | 5563529.9119 | 0
6429 | 1228.3805 | 0 | 0 | 0 | 0 | 1570.1 | 0 | 0 | 0 | 4174036.9254 | 0
6430 | 1411.5744 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1566.5 | 511701.3813 | 111351.8261 | 50510.4255 | 3745492.2703 | 132596.379
6431 | 1350.2371 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1378.15 | 872001.2039 | 215514.4963 | 97759.7701 | 2553888.4516 | 368135.2
6432 | 369.6591 | 0 | 0 | 0 | 0 | 1092.25 | 0 | 0 | 0 | 677585.1501 | 0
6433 | 112.8605 | 0 | 0 | 0 | 0 | 1196.2 | 0 | 0 | 0 | 134304.0248 | 0
6434 | 119.4032 | 0 | 0 | 0 | 0 | 1210.8 | 0 | 0 | 0 | 142089.7653 | 0
6435 | 113.6784 | 0 | 0 | 0 | 0 | 1196.85 | 0 | 0 | 0 | 135277.2423 | 0
6436 | 116.1318 | 0 | 0 | 0 | 0 | 1175.85 | 0 | 0 | 0 | 138196.895 | 0
6437 | 112.8605 | 0 | 0 | 0 | 0 | 1180.25 | 0 | 0 | 0 | 134304.0248 | 0
6438 | 116.9497 | 0 | 0 | 0 | 0 | 1251.8 | 0 | 0 | 0 | 139170.1125 | 0
6439 | 100.5931 | 104.4965 | 104.4965 | 101.7232 | 100.5931 | 1254.95 | 133561.1299 | 36213.5076 | 16426.8494 | 0 | 74946.8146
6440 | 225.1445 | 349.2046 | 233.8807 | 339.9369 | 225.1445 | 995.75 | 237098.4604 | 81052.0128 | 36766.0936 | 0 | 226101.3439
6441 | 1240.0192 | 2421.9182 | 1288.1376 | 2357.6418 | 1240.0192 | 681.55 | 894691.556 | 446406.9257 | 202495.1416 | 0 | 1634903.3643
6442 | 1266.4219 | 3521.1419 | 1315.5641 | 3427.6927 | 1266.4219 | 339.05 | 453598.3452 | 455911.8674 | 206806.6888 | 0 | 2103463.3784
6443 | 1701.8192 | 4024.3171 | 1767.8577 | 3917.5139 | 1701.8192 | 346.25 | 622014.1844 | 612654.8954 | 277907.0678 | 0 | 2814383.4259
6444 | 1591.6166 | 4251.8943 | 1653.3793 | 4139.0514 | 1591.6166 | 349.85 | 589657.7767 | 572981.9674 | 259910.9869 | 0 | 2626406.0929
6445 | 1439.8744 | 4175.0944 | 1495.7479 | 4064.2897 | 1439.8744 | 361.05 | 550848.4483 | 518354.7743 | 235131.4851 | 0 | 2359882.1036
6446 | 1622.9691 | 3775.1608 | 1685.9479 | 3674.9701 | 1622.9691 | 385.3 | 662018.3412 | 584268.8785 | 265030.8552 | 0 | 2620608.2171
6447 | 1764.8544 | 3134.13 | 1833.3387 | 3050.9519 | 1764.8544 | 390.7 | 729969.4568 | 635347.5894 | 288200.726 | 0 | 2840180.2101
6448 | 1749.6223 | 2215.8516 | 1817.5156 | 2157.0441 | 1749.6223 | 737.45 | 1364213.2469 | 629864.0399 | 285713.327 | 0 | 2208985.6765
6449 | 1578.746 | 915.375 | 915.375 | 891.0815 | 891.0815 | 1383.6 | 1302300.922 | 320789.3232 | 145513.6013 | 1260489.0738 | 537643.8048
6450 | 1433.9206 | 49.5531 | 49.5531 | 48.238 | 48.238 | 1552.8 | 78937.6534 | 17365.663 | 7877.2577 | 2539956.241 | 21115.8896
6451 | 1471.9558 | 0 | 0 | 0 | 0 | 1796.7 | 0 | 0 | 0 | 5001705.7914 | 0
6452 | 1491.7217 | 0 | 0 | 0 | 0 | 1687.5 | 0 | 0 | 0 | 5068870.408 | 0
6453 | 1544.0628 | 0 | 0 | 0 | 0 | 1531.25 | 0 | 0 | 0 | 5246725.5099 | 0
6454 | 1414.8457 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1377.75 | 449404.6133 | 111351.8261 | 50510.4255 | 3756608.2156 | 190330.0965
6455 | 1431.2023 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1256.1 | 795220.1876 | 215514.4963 | 97759.7701 | 2829008.0619 | 440388.8
6456 | 482.5196 | 0 | 0 | 0 | 0 | 1230.2 | 0 | 0 | 0 | 884458.4924 | 0
6457 | 426.0894 | 0 | 0 | 0 | 0 | 1118.5 | 0 | 0 | 0 | 507046.3542 | 0
6458 | 399.101 | 0 | 0 | 0 | 0 | 1170.45 | 0 | 0 | 0 | 474930.1744 | 0
6459 | 440.8103 | 0 | 0 | 0 | 0 | 923.85 | 0 | 0 | 0 | 524564.2704 | 0
6460 | 390.1049 | 0 | 0 | 0 | 0 | 997.05 | 0 | 0 | 0 | 464224.7811 | 0
6461 | 392.5583 | 0 | 0 | 0 | 0 | 992.85 | 0 | 0 | 0 | 467144.4338 | 0
6462 | 495.6049 | 0 | 0 | 0 | 0 | 1176.75 | 0 | 0 | 0 | 589769.8477 | 0
6463 | 433.4498 | 315.4351 | 315.4351 | 307.0637 | 307.0637 | 1188.95 | 386739.4363 | 110542.9186 | 50143.4961 | 231665.867 | 243775.6764
6464 | 442.7905 | 481.0809 | 459.9724 | 468.3132 | 442.7905 | 572.05 | 267459.9078 | 159404.5735 | 72307.6857 | 0 | 632282.6686
6465 | 1681.4818 | 2383.1718 | 1746.7315 | 2319.9238 | 1681.4818 | 1224.5 | 2178392.9168 | 605333.4368 | 274585.9729 | 0 | 1303989.1119
6466 | 1826.7294 | 2022.0553 | 1897.6148 | 1968.391 | 1826.7294 | 1248.05 | 2408412.4003 | 657622.5768 | 298304.9078 | 0 | 1373609.1573
6467 | 1832.1434 | 1923.1205 | 1903.2399 | 1872.082 | 1832.1434 | 1059.25 | 2051994.5171 | 659571.629 | 299189.0195 | 0 | 1723588.9167
6468 | 1642.4999 | 2152.1105 | 1706.2368 | 2094.9947 | 1642.4999 | 794.8 | 1382432.9189 | 591299.9665 | 268220.2348 | 0 | 1979540.8879
6469 | 1936.4576 | 1648.1302 | 1648.1302 | 1604.3897 | 1604.3897 | 361.05 | 613349.9659 | 577580.3061 | 261996.8444 | 608680.4181 | 2583745.6728
6470 | 1870.011 | 1942.5763 | 1942.5763 | 1891.0214 | 1870.011 | 741.8 | 1466542.4706 | 673203.9535 | 305372.7934 | 0 | 2352847.8176
6471 | 1945.9424 | 2148.0488 | 2021.4538 | 2091.0407 | 1945.9424 | 1119.7 | 2301923.7904 | 700539.2633 | 317772.3936 | 0 | 1713013.093
6472 | 1509.5259 | 1421.6729 | 1421.6729 | 1383.9424 | 1383.9424 | 1549.95 | 2269846.771 | 498219.2772 | 225997.7999 | 230194.4482 | 609667.8834
6473 | 1569.9972 | 557.0632 | 557.0632 | 542.279 | 542.279 | 1821.5 | 1043805.5415 | 195220.4572 | 88554.1685 | 1883807.4518 | 94749.228
6474 | 1518.9095 | 37.8437 | 37.8437 | 36.8393 | 36.8393 | 1851.5 | 71866.7885 | 13262.1505 | 6015.8588 | 2716634.5795 | 5354.91
6475 | 1387.3227 | 0 | 0 | 0 | 0 | 1845.85 | 0 | 0 | 0 | 4714122.4293 | 0
6476 | 1625.028 | 0 | 0 | 0 | 0 | 1629.55 | 0 | 0 | 0 | 5521845.1236 | 0
6477 | 1559.6016 | 0 | 0 | 0 | 0 | 1431.05 | 0 | 0 | 0 | 5299526.2436 | 0
6478 | 1286.4464 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1462.4 | 476986.4645 | 111351.8261 | 50510.4255 | 3320307.418 | 164437.8624
6479 | 1165.4076 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1265.65 | 801569.9136 | 215514.4963 | 97759.7701 | 1925837.6237 | 434735.2
6480 | 1319.1596 | 0 | 0 | 0 | 0 | 1239.75 | 0 | 0 | 0 | 2418019.5725 | 0
6481 | 1503.1713 | 0 | 0 | 0 | 0 | 1150 | 0 | 0 | 0 | 2755313.0662 | 0
6482 | 924.9656 | 0 | 0 | 0 | 0 | 1020.8 | 0 | 0 | 0 | 1695461.9573 | 0
6483 | 1193.2138 | 0 | 0 | 0 | 0 | 1181.85 | 0 | 0 | 0 | 2187160.9156 | 0
6484 | 1166.2254 | 0 | 0 | 0 | 0 | 834.95 | 0 | 0 | 0 | 2137691.204 | 0
6485 | 1228.3805 | 0 | 0 | 0 | 0 | 1169.8 | 0 | 0 | 0 | 2251621.4492 | 0
6486 | 1238.1945 | 0 | 0 | 0 | 0 | 1166.3 | 0 | 0 | 0 | 2269610.436 | 0
6487 | 1037.0083 | 103.6665 | 103.6665 | 100.9152 | 100.9152 | 1168.95 | 124814.7857 | 36329.4825 | 16479.4569 | 1715858.6025 | 82091.95
6488 | 344.9167 | 358.3014 | 358.3014 | 348.7923 | 344.9167 | 572.05 | 208633.3059 | 124170.0083 | 56324.8954 | 0 | 492523.7871
6489 | 280.4042 | 291.285 | 291.285 | 283.5545 | 280.4042 | 1224.5 | 364239.6503 | 100945.5204 | 45790.0097 | 0 | 217453.302
6490 | 270.3306 | 632.8014 | 280.8201 | 616.0072 | 270.3306 | 1313.55 | 376096.8565 | 97319.0173 | 44144.9876 | 0 | 185568.4428
6491 | 287.6502 | 2094.6916 | 298.8122 | 2039.0996 | 287.6502 | 790.75 | 241383.9159 | 103554.0706 | 46973.277 | 0 | 347840.9998
6492 | 303.9311 | 2385.7553 | 315.726 | 2322.4387 | 303.9311 | 349.85 | 113062.6489 | 109415.2121 | 49631.9559 | 0 | 501531.9784
6493 | 295.44 | 2141.2051 | 306.9045 | 2084.3787 | 295.44 | 635.55 | 199595.6821 | 106358.4093 | 48245.3562 | 0 | 403113.1433
6494 | 282.4089 | 2726.289 | 293.3678 | 2653.9348 | 282.4089 | 740.85 | 222226.5353 | 101667.2144 | 46117.3781 | 0 | 355595.2027
6495 | 273.0489 | 1677.5533 | 283.6446 | 1633.032 | 273.0489 | 390.7 | 113468.9066 | 98297.5917 | 44588.8798 | 0 | 439417.5396
6496 | 209.159 | 869.1742 | 217.2743 | 846.1068 | 209.159 | 1259.95 | 280043.7689 | 75297.2301 | 34155.6602 | 0 | 154788.0975
6497 | 292.731 | 268.7731 | 268.7731 | 261.64 | 261.64 | 1538.9 | 426673.5451 | 94190.3922 | 42725.8084 | 56989.7777 | 118090.4766
6498 | 235.0545 | 14.4892 | 14.4892 | 14.1047 | 14.1047 | 1644.05 | 24501.2037 | 5077.6963 | 2303.2994 | 405001.0232 | 4914.2457
6499 | 209.7018 | 0 | 0 | 0 | 0 | 1829.5 | 0 | 0 | 0 | 384383.4122 | 0
6500 | 305.8684 | 0 | 0 | 0 | 0 | 1691 | 0 | 0 | 0 | 560656.7393 | 0
6501 | 293.6009 | 202.9388 | 202.9388 | 197.5529 | 197.5529 | 1596.1 | 332367.1494 | 71119.0557 | 32260.3939 | 176055.9812 | 78905.0962
6502 | 298.5079 | 310.0915 | 310.0915 | 301.8619 | 298.5079 | 1586.3 | 499639.1044 | 107462.8477 | 48746.3418 | 0 | 123492.7225
6503 | 235.535 | 244.6749 | 244.6749 | 238.1813 | 235.535 | 1528.05 | 379928.9265 | 84792.6031 | 38462.8669 | 0 | 111160.7432
6504 | 168.473 | 175.0106 | 175.0106 | 170.3659 | 168.473 | 1492.95 | 265517.8591 | 60650.2647 | 27511.634 | 0 | 85424.2132
6505 | 199.5505 | 0 | 0 | 0 | 0 | 1635.05 | 0 | 0 | 0 | 237465.0871 | 0
6506 | 243.7133 | 0 | 0 | 0 | 0 | 1399.5 | 0 | 0 | 0 | 290018.836 | 0
6507 | 191.3722 | 0 | 0 | 0 | 0 | 1279.8 | 0 | 0 | 0 | 227732.9115 | 0
6508 | 152.1164 | 0 | 0 | 0 | 0 | 1225.55 | 0 | 0 | 0 | 181018.468 | 0
6509 | 135.7598 | 0 | 0 | 0 | 0 | 1275.3 | 0 | 0 | 0 | 161554.1167 | 0
6510 | 197.097 | 0 | 0 | 0 | 0 | 1324.55 | 0 | 0 | 0 | 234545.4345 | 0
6511 | 122.6745 | 127.4354 | 127.4354 | 124.0533 | 122.6745 | 1260.1 | 162701.1431 | 44162.8141 | 20032.7432 | 0 | 90766.8505
6512 | 195.7169 | 300.3133 | 203.3107 | 292.3431 | 195.7169 | 1198.25 | 246763.5916 | 70458.0897 | 31960.5724 | 0 | 156916.0372
6513 | 885.4685 | 1485.764 | 919.8294 | 1446.3326 | 885.4685 | 758.5 | 708965.4389 | 318768.6644 | 144597.0081 | 0 | 1099309.158
6514 | 1487.9546 | 2621.8715 | 1545.6947 | 2552.2885 | 1487.9546 | 327.25 | 515480.95 | 535663.6531 | 242982.9849 | 0 | 2488976.0438
6515 | 1782.3192 | 1849.6324 | 1849.6324 | 1800.5441 | 1782.3192 | 342.65 | 647796.0198 | 641634.9019 | 291052.7208 | 0 | 2930972.0971
6516 | 1685.3849 | 2928.6139 | 1750.7859 | 2850.8901 | 1685.3849 | 347.95 | 622969.831 | 606738.5503 | 275223.348 | 0 | 2784340.0613
6517 | 1718.2943 | 3267.7442 | 1784.972 | 3181.0201 | 1718.2943 | 629.25 | 1146870.471 | 618585.9613 | 280597.4652 | 0 | 2355351.9624
6518 | 1671.8876 | 3001.1661 | 1736.7652 | 2921.5168 | 1671.8876 | 914.6 | 1622166.854 | 601879.5367 | 273019.2454 | 0 | 1814666.8032
6519 | 1697.546 | 2133.2333 | 1763.4188 | 2076.6185 | 1697.546 | 1088.45 | 1962160.4204 | 611116.5571 | 277209.2605 | 0 | 1547398.049
6520 | 1755.8511 | 1067.0395 | 1067.0395 | 1038.7208 | 1038.7208 | 1385.2 | 1526503.6369 | 373939.4937 | 169623.1092 | 1314499.866 | 625096.6704
6521 | 1623.5477 | 241.5927 | 241.5927 | 235.181 | 235.181 | 1710.5 | 425374.0149 | 84665.1611 | 38405.0578 | 2544876.1959 | 66644.637
6522 | 1905.103 | 11.1422 | 11.1422 | 10.8465 | 10.8465 | 1826.85 | 20868.3432 | 3904.7441 | 1771.2353 | 3472172.2171 | 1838.3335
6523 | 1574.8582 | 0 | 0 | 0 | 0 | 1830.45 | 0 | 0 | 0 | 5351368.2282 | 0
6524 | 1257.8224 | 0 | 0 | 0 | 0 | 1833.55 | 0 | 0 | 0 | 4274080.4235 | 0
6525 | 1468.0047 | 0 | 0 | 0 | 0 | 1807.7 | 0 | 0 | 0 | 4988279.8177 | 0
6526 | 1599.6753 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1846.8 | 602306.6138 | 111351.8261 | 50510.4255 | 4384659.0435 | 46859.8968
6527 | 1683.9117 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1844.45 | 1163614.6025 | 215514.4963 | 97759.7701 | 3687714.7288 | 92085.6
6528 | 1453.2837 | 0 | 0 | 0 | 0 | 1830.45 | 0 | 0 | 0 | 2663869.0533 | 0
6529 | 1407.4852 | 0 | 0 | 0 | 0 | 1565.65 | 0 | 0 | 0 | 1674907.4392 | 0
6530 | 1535.8845 | 0 | 0 | 0 | 0 | 1464 | 0 | 0 | 0 | 1827702.5978 | 0
6531 | 1660.1947 | 0 | 0 | 0 | 0 | 1442 | 0 | 0 | 0 | 1975631.668 | 0
6532 | 1321.6131 | 0 | 0 | 0 | 0 | 1436.6 | 0 | 0 | 0 | 1572719.5938 | 0
6533 | 1273.3611 | 0 | 0 | 0 | 0 | 1411.8 | 0 | 0 | 0 | 1515299.7566 | 0
6534 | 1310.1635 | 0 | 0 | 0 | 0 | 1429.2 | 0 | 0 | 0 | 1559094.5483 | 0
6535 | 1068.0858 | 0 | 0 | 0 | 0 | 1375 | 0 | 0 | 0 | 1957801.3411 | 0
6536 | 1296.3319 | 42.244 | 42.244 | 41.1229 | 41.1229 | 1005.45 | 43416.4195 | 14804.2441 | 6715.3696 | 2300798.1662 | 40033.6211
6537 | 1701.5656 | 127.2806 | 127.2806 | 123.9026 | 123.9026 | 294.1 | 38358.5662 | 44604.9479 | 20233.3 | 2891856.266 | 206894.9638
6538 | 1384.2118 | 1867.4468 | 1437.926 | 1817.8858 | 1384.2118 | 306.3 | 447889.5903 | 498316.2653 | 226041.7948 | 0 | 2344439.607
6539 | 1713.281 | 2761.4786 | 1779.7644 | 2688.1904 | 1713.281 | 320.05 | 578150.6739 | 616781.174 | 279778.7937 | 0 | 2878226.4815
6540 | 1435.638 | 2453.4875 | 1491.3476 | 2388.3733 | 1435.638 | 320.45 | 485796.2906 | 516829.685 | 234439.6877 | 0 | 2411225.8264
6541 | 1436.8198 | 2663.2045 | 1492.5754 | 2592.5245 | 1436.8198 | 314.5 | 476994.0173 | 517255.1204 | 234632.6699 | 0 | 2421759.7375
6542 | 1416.2125 | 2728.2285 | 1471.1678 | 2655.8228 | 1416.2125 | 696.5 | 1041211.3905 | 509836.5036 | 231267.5029 | 0 | 1846033.0068
6543 | 1458.112 | 2688.6054 | 1514.6937 | 2617.2512 | 1458.112 | 978.75 | 1507377.3539 | 524920.3128 | 238109.6863 | 0 | 1489096.8596
6544 | 1580.7302 | 1750.0889 | 1642.0709 | 1703.6425 | 1580.7302 | 782.05 | 1300055.0377 | 569062.8857 | 258133.2479 | 0 | 1925250.3934
6545 | 1546.2679 | 478.2065 | 478.2065 | 465.5152 | 465.5152 | 1417.7 | 694604.937 | 167585.4557 | 76018.6247 | 1981019.797 | 265334.8941
6546 | 1753.4948 | 24.762 | 24.762 | 24.1048 | 24.1048 | 1607.85 | 40803.8624 | 8677.7349 | 3936.317 | 3169971.758 | 9252.7793
6547 | 1580.4767 | 0 | 0 | 0 | 0 | 1829.05 | 0 | 0 | 0 | 5370459.8606 | 0
6548 | 1247.1906 | 0 | 0 | 0 | 0 | 1826.5 | 0 | 0 | 0 | 4237953.6044 | 0
6549 | 1584.9543 | 0 | 0 | 0 | 0 | 1808.15 | 0 | 0 | 0 | 5385674.8099 | 0
6550 | 1818.0358 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1828.1 | 596207.1083 | 111351.8261 | 50510.4255 | 5126648.2978 | 52579.7406
6551 | 1714.1715 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1821.1 | 1148560.469 | 215514.4963 | 97759.7701 | 3790537.2098 | 105908.8
6552 | 1513.8031 | 0 | 0 | 0 | 0 | 1751.35 | 0 | 0 | 0 | 2774801.1336 | 0
6553 | 1295.9329 | 0 | 0 | 0 | 0 | 1584.5 | 0 | 0 | 0 | 1542160.1343 | 0
6554 | 1429.5663 | 0 | 0 | 0 | 0 | 1379.8 | 0 | 0 | 0 | 1701183.8411 | 0
6555 | 1403.1504 | 0 | 0 | 0 | 0 | 1267.35 | 0 | 0 | 0 | 1669748.9224 | 0
6556 | 223.7582 | 0 | 0 | 0 | 0 | 1185.4 | 0 | 0 | 0 | 266272.2534 | 0
6557 | 344.1836 | 0 | 0 | 0 | 0 | 1170.25 | 0 | 0 | 0 | 409578.5008 | 0
6558 | 855.4089 | 0 | 0 | 0 | 0 | 1176.75 | 0 | 0 | 0 | 1017936.6353 | 0
6559 | 1351.1431 | 351.5752 | 351.5752 | 342.2445 | 342.2445 | 1284.95 | 466307.2718 | 123208.0357 | 55888.534 | 1849311.0245 | 239545.3252
6560 | 1327.7543 | 1379.2782 | 1379.2782 | 1342.6729 | 1327.7543 | 1272.05 | 1786280.4622 | 477991.5592 | 216822.2823 | 0 | 966538.7653
6561 | 1082.8362 | 1124.8562 | 1124.8562 | 1095.0031 | 1082.8362 | 1300.05 | 1495474.0687 | 389821.0406 | 176827.1554 | 0 | 757931.215
6562 | 962.5079 | 2595.9616 | 999.8589 | 2527.0662 | 962.5079 | 1238.05 | 1269292.7999 | 346502.8523 | 157177.5438 | 0 | 733382.912
6563 | 1672.8606 | 3696.7228 | 1737.7749 | 3598.6138 | 1672.8606 | 620.75 | 1105205.511 | 602229.8016 | 273178.1294 | 0 | 2307292.9274
6564 | 1223.3853 | 2889.1009 | 1270.8581 | 2812.4257 | 1223.3853 | 823.85 | 1073642.2637 | 440418.7123 | 199778.8214 | 0 | 1438884.6347
6565 | 988.9209 | 3669.1996 | 1027.2958 | 3571.8211 | 988.9209 | 760.05 | 798677.7608 | 356011.5268 | 161490.7842 | 0 | 1226212.4795
6566 | 879.0094 | 3493.92 | 913.1187 | 3401.1933 | 879.0094 | 1098.3 | 1023870.2306 | 316443.386 | 143542.2359 | 0 | 792602.781
6567 | 1120.1603 | 2821.9474 | 1163.6275 | 2747.0544 | 1120.1603 | 1279.7 | 1522572.3542 | 403257.7202 | 182922.1825 | 0 | 806851.4886
6568 | 1590.8052 | 1797.8802 | 1652.5368 | 1750.1654 | 1590.8052 | 1437.45 | 2430117.4371 | 572689.8738 | 259778.49 | 0 | 894907.4681
6569 | 1557.5416 | 605.0259 | 605.0259 | 588.9688 | 588.9688 | 1766.55 | 1104475.173 | 212028.7677 | 96178.6049 | 1775393.8853 | 134586.2595
6570 | 1465.6696 | 23.0885 | 23.0885 | 22.4757 | 22.4757 | 1802 | 42942.0615 | 8091.2588 | 3670.2849 | 2645374.3824 | 4356
6571 | 966.144 | 0 | 0 | 0 | 0 | 1845.85 | 0 | 0 | 0 | 3282957.2906 | 0
6572 | 1198.0387 | 0 | 0 | 0 | 0 | 1847.45 | 0 | 0 | 0 | 4070935.4177 | 0
6573 | 1423.3507 | 0 | 0 | 0 | 0 | 1852.55 | 0 | 0 | 0 | 4836545.8383 | 0
6574 | 1421.0199 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1865.25 | 608118.417 | 111351.8261 | 50510.4255 | 3777588.2186 | 41216.5215
6575 | 1225.2315 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1865.55 | 1175347.8973 | 215514.4963 | 97759.7701 | 2129119.2903 | 79594.4
6576 | 1382.173 | 0 | 0 | 0 | 0 | 1818.85 | 0 | 0 | 0 | 2533523.153 | 0
6577 | 1511.9217 | 0 | 0 | 0 | 0 | 1599.95 | 0 | 0 | 0 | 1799186.823 | 0
6578 | 1197.2617 | 0 | 0 | 0 | 0 | 1679.1 | 0 | 0 | 0 | 1424741.467 | 0
6579 | 1518.9141 | 0 | 0 | 0 | 0 | 1480.45 | 0 | 0 | 0 | 1807507.8314 | 0
6580 | 1238.4395 | 0 | 0 | 0 | 0 | 1414.65 | 0 | 0 | 0 | 1473742.9574 | 0
6581 | 1274.9556 | 0 | 0 | 0 | 0 | 1415.4 | 0 | 0 | 0 | 1517197.1105 | 0
6582 | 1134.3297 | 0 | 0 | 0 | 0 | 1421.25 | 0 | 0 | 0 | 1349852.3954 | 0
6583 | 1236.1086 | 206.2807 | 206.2807 | 200.8061 | 200.8061 | 1498.5 | 316486.8927 | 72290.1877 | 32791.6323 | 1897709.6093 | 98573.837
6584 | 895.8243 | 833.1817 | 833.1817 | 811.0695 | 811.0695 | 1437.05 | 1225081.3556 | 291985.0099 | 132447.6447 | 155355.5821 | 446933.3234
6585 | 1078.1882 | 1074.5625 | 1074.5625 | 1046.0442 | 1046.0442 | 1421.4 | 1568819.4765 | 376575.9058 | 170819.0151 | 58919.967 | 592437.7976
6586 | 1521.983 | 1581.0432 | 1581.0432 | 1539.0831 | 1521.983 | 1261.9 | 2032527.0689 | 547913.8976 | 248539.8319 | 0 | 1123375.6523
6587 | 1177.4916 | 1803.0077 | 1223.1832 | 1755.1569 | 1177.4916 | 1162.9 | 1450399.0807 | 423896.9666 | 192284.374 | 0 | 985678.1966
6588 | 1060.1419 | 2288.4588 | 1101.2805 | 2227.7244 | 1060.1419 | 1030.7 | 1158190.0855 | 381651.0696 | 173121.1657 | 0 | 1027595.5049
6589 | 943.5293 | 2721.1854 | 980.1424 | 2648.9666 | 943.5293 | 983.75 | 983079.7335 | 339670.5356 | 154078.3291 | 0 | 958861.6162
6590 | 1025.0301 | 2746.7805 | 1064.806 | 2673.8824 | 1025.0301 | 1258.25 | 1365506.978 | 369010.8292 | 167387.4122 | 0 | 760316.0626
6591 | 930.0669 | 2392.0765 | 966.157 | 2328.5921 | 930.0669 | 1478.8 | 1453583.9866 | 334824.0729 | 151879.9198 | 0 | 484750.8523
6592 | 968.8011 | 1105.575 | 1006.3951 | 1076.2336 | 968.8011 | 1539.25 | 1573690.7727 | 348768.404 | 158205.2233 | 0 | 446375.1171
6593 | 1132.6778 | 89.1294 | 89.1294 | 86.764 | 86.764 | 1843.95 | 168920.1553 | 31235.0402 | 14168.5613 | 1917159.9561 | 13253.1705
6594 | 1010.9393 | 0 | 0 | 0 | 0 | 1908.65 | 0 | 0 | 0 | 1853051.8029 | 0
6595 | 1250.7879 | 0 | 0 | 0 | 0 | 1910.95 | 0 | 0 | 0 | 4250177.359 | 0
6596 | 1191.8232 | 0 | 0 | 0 | 0 | 1863.8 | 0 | 0 | 0 | 4049815.1283 | 0
6597 | 1114.1294 | 0 | 0 | 0 | 0 | 1845.45 | 0 | 0 | 0 | 3785811.5347 | 0
6598 | 1338.6645 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1838.25 | 601213.3034 | 111351.8261 | 50510.4255 | 3497744.4097 | 49475.1195
6599 | 1141.3222 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1805.7 | 1145679.9253 | 215514.4963 | 97759.7701 | 1843995.4108 | 115025.6
6600 | 156.1646 | 0 | 0 | 0 | 0 | 1607.6 | 0 | 0 | 0 | 286249.6649 | 0
6601 | 101.7789 | 0 | 0 | 0 | 0 | 1444.45 | 0 | 0 | 0 | 121116.893 | 0
6602 | 103.3328 | 0 | 0 | 0 | 0 | 1269.6 | 0 | 0 | 0 | 122966.0059 | 0
6603 | 99.4481 | 0 | 0 | 0 | 0 | 1180.45 | 0 | 0 | 0 | 118343.2237 | 0
6604 | 104.8867 | 0 | 0 | 0 | 0 | 1160.35 | 0 | 0 | 0 | 124815.1187 | 0
6605 | 98.6711 | 0 | 0 | 0 | 0 | 1179.7 | 0 | 0 | 0 | 117418.6673 | 0
6606 | 101.002 | 0 | 0 | 0 | 0 | 1185.55 | 0 | 0 | 0 | 120192.3366 | 0
6607 | 84.2832 | 3.9568 | 3.9568 | 3.8518 | 3.8518 | 1284 | 5248.0056 | 1386.6465 | 628.9983 | 147430.8098 | 2699.32
6608 | 99.5365 | 55.1481 | 55.1481 | 53.6845 | 53.6845 | 908.6 | 51691.0593 | 19326.4081 | 8766.6734 | 84046.7105 | 57351.9786
6609 | 1023.3432 | 157.8921 | 157.8921 | 153.7017 | 153.7017 | 1250.1 | 203559.4237 | 55332.6188 | 25099.4907 | 1594052.7504 | 112822.455
6610 | 1312.2971 | 335.5485 | 335.5485 | 326.6432 | 326.6432 | 1128.5 | 389833.7545 | 117591.5532 | 53340.8351 | 1806703.6769 | 278648.181
6611 | 985.1178 | 1023.3453 | 1023.3453 | 996.1862 | 985.1178 | 1009.7 | 1049826.6865 | 354642.4063 | 160869.736 | 0 | 975562.1527
6612 | 1098.0768 | 1438.8921 | 1140.6876 | 1400.7047 | 1098.0768 | 984.8 | 1141840.644 | 395307.6613 | 179315.9475 | 0 | 1114767.6049
6613 | 1289.3435 | 2448.2893 | 1339.3756 | 2383.313 | 1289.3435 | 891.95 | 1213752.0703 | 464163.6524 | 210549.7901 | 0 | 1428657.0419
6614 | 1274.6729 | 1600.553 | 1324.1364 | 1558.0752 | 1274.6729 | 1134.15 | 1532564.0137 | 458882.2598 | 208154.0918 | 0 | 1103675.5686
6615 | 1148.4205 | 451.3035 | 451.3035 | 439.3262 | 439.3262 | 1408.8 | 656050.3132 | 158157.4245 | 71741.9651 | 1299769.8698 | 254235.5096
6616 | 1234.0498 | 251.5995 | 251.5995 | 244.9222 | 244.9222 | 1682.25 | 436722.6245 | 88172.0042 | 39995.8008 | 1813070.7552 | 76177.7027
6617 | 1363.2866 | 152.055 | 152.055 | 148.0196 | 148.0196 | 1897.95 | 296927.3911 | 53287.0513 | 24171.5986 | 2227584.4861 | 14785.8204
6618 | 1689.6706 | 0 | 0 | 0 | 0 | 1892.65 | 0 | 0 | 0 | 3097166.1878 | 0
6619 | 1542.9749 | 0 | 0 | 0 | 0 | 1910.95 | 0 | 0 | 0 | 5243028.8733 | 0
6620 | 1457.536 | 0 | 0 | 0 | 0 | 1863.3 | 0 | 0 | 0 | 4952707.4197 | 0
6621 | 1491.7213 | 0 | 0 | 0 | 0 | 1789.95 | 0 | 0 | 0 | 5068869.0012 | 0
6622 | 1543.7762 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1760.6 | 574523.6174 | 111351.8261 | 50510.4255 | 4194713.8949 | 73226.2356
6623 | 1860.7669 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1591.2 | 1007080.4456 | 215514.4963 | 97759.7701 | 4288668.6882 | 242009.6
6624 | 186.4652 | 0 | 0 | 0 | 0 | 1474.55 | 0 | 0 | 0 | 341790.6445 | 0
6625 | 104.1097 | 0 | 0 | 0 | 0 | 1208 | 0 | 0 | 0 | 123890.5623 | 0
6626 | 112.656 | 0 | 0 | 0 | 0 | 1419.8 | 0 | 0 | 0 | 134060.6831 | 0
6627 | 107.2175 | 0 | 0 | 0 | 0 | 1405.45 | 0 | 0 | 0 | 127588.7881 | 0
6628 | 107.2175 | 0 | 0 | 0 | 0 | 1373.45 | 0 | 0 | 0 | 127588.7881 | 0
6629 | 104.8867 | 0 | 0 | 0 | 0 | 1315.2 | 0 | 0 | 0 | 124815.1187 | 0
6630 | 107.2175 | 0 | 0 | 0 | 0 | 1380.05 | 0 | 0 | 0 | 127588.7881 | 0
6631 | 100.2454 | 104.136 | 104.136 | 101.3723 | 100.2454 | 1396.5 | 148860.8529 | 36088.3512 | 16370.0771 | 0 | 60498.111
6632 | 123.1185 | 890.7678 | 127.8966 | 867.1273 | 123.1185 | 1079.3 | 140834.1744 | 44322.6528 | 20105.2478 | 0 | 113355.1845
6633 | 971.1397 | 1784.3362 | 1008.8248 | 1736.9809 | 971.1397 | 1433.9 | 1477273.1525 | 349610.2942 | 158587.114 | 0 | 549762.1877
6634 | 1916.0218 | 2219.4354 | 1990.3728 | 2160.5328 | 1916.0218 | 1422.9 | 2888676.2657 | 689767.8534 | 312886.3624 | 0 | 1105736.1894
6635 | 1454.101 | 2939.0747 | 1510.527 | 2861.0733 | 1454.101 | 963.8 | 1482683.119 | 523476.356 | 237454.6915 | 0 | 1506739.4448
6636 | 1405.6336 | 3078.2195 | 1460.1793 | 2996.5252 | 1405.6336 | 360.8 | 537031.8717 | 506028.1115 | 229539.9739 | 0 | 2304114.6676
6637 | 1449.3753 | 3588.1542 | 1505.6187 | 3492.9265 | 1449.3753 | 342.95 | 525506.9737 | 521775.0947 | 236682.9804 | 0 | 2401687.2796
6638 | 1617.9573 | 2887.1023 | 1680.7414 | 2810.4801 | 1617.9573 | 359.25 | 616933.1869 | 582464.6107 | 264212.4193 | 0 | 2654663.3612
6639 | 1296.6671 | 1677.2167 | 1346.9849 | 1632.7043 | 1296.6671 | 1217.2 | 1672772.3841 | 466800.1531 | 211745.7361 | 0 | 1015030.9996
6640 | 1542.1261 | 649.5106 | 649.5106 | 632.2729 | 632.2729 | 1490.75 | 999872.0535 | 227618.2563 | 103250.1702 | 1667760.9316 | 315174.3158
6641 | 1368.5009 | 513.0574 | 513.0574 | 499.4411 | 499.4411 | 1722.45 | 909916.3229 | 179798.7932 | 81558.7304 | 1592986.5433 | 135687.5338
6642 | 1900.383 | 11.1298 | 11.1298 | 10.8344 | 10.8344 | 1851.15 | 21140.5382 | 3900.3755 | 1769.2537 | 3463542.6654 | 1578.7031
6643 | 1656.3215 | 0 | 0 | 0 | 0 | 1909.95 | 0 | 0 | 0 | 5628180.4162 | 0
6644 | 1599.7157 | 0 | 0 | 0 | 0 | 1832.8 | 0 | 0 | 0 | 5435833.9962 | 0
6645 | 1535.2298 | 0 | 0 | 0 | 0 | 1601.45 | 0 | 0 | 0 | 5216711.0133 | 0
6646 | 1731.7952 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1507.55 | 491707.8037 | 111351.8261 | 50510.4255 | 4833602.5929 | 150627.6513
6647 | 1424.1277 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1173.1 | 741399.9994 | 215514.4963 | 97759.7701 | 2804968.493 | 489524.8
6648 | 1595.0541 | 0 | 0 | 0 | 0 | 618.1 | 0 | 0 | 0 | 2923734.1378 | 0
6649 | 1460.6438 | 0 | 0 | 0 | 0 | 803.1 | 0 | 0 | 0 | 2677360.0487 | 0
6650 | 1355.7571 | 0 | 0 | 0 | 0 | 275.1 | 0 | 0 | 0 | 2485102.812 | 0
6651 | 1222.1238 | 0 | 0 | 0 | 0 | 271.45 | 0 | 0 | 0 | 2240152.8502 | 0
6652 | 1309.9178 | 0 | 0 | 0 | 0 | 269.95 | 0 | 0 | 0 | 2401079.2779 | 0
6653 | 1102.4753 | 0 | 0 | 0 | 0 | 270.7 | 0 | 0 | 0 | 2020837.1864 | 0
6654 | 1162.2995 | 0 | 0 | 0 | 0 | 276.55 | 0 | 0 | 0 | 2130495.0183 | 0
6655 | 1174.1449 | 482.2215 | 482.2215 | 469.4236 | 469.4236 | 838.5 | 417445.9372 | 168992.4886 | 76656.8705 | 1291754.2024 | 533702.281
6656 | 224.0097 | 817.1082 | 232.7016 | 795.4226 | 224.0097 | 313.7 | 74160.7957 | 80643.5027 | 36580.7889 | 0 | 377747.6074
6657 | 279.8454 | 1343.9401 | 290.7043 | 1308.2727 | 279.8454 | 350.4 | 103745.8536 | 100744.3308 | 45698.7478 | 0 | 461632.9115
6658 | 322.6469 | 2861.3586 | 335.1672 | 2785.4197 | 322.6469 | 362.9 | 123639.5845 | 116152.8796 | 52688.2368 | 0 | 528205.22
6659 | 279.4598 | 2655.3273 | 290.3044 | 2584.8563 | 279.4598 | 368.9 | 108846.7565 | 100605.5308 | 45635.7866 | 0 | 455826.8925
6660 | 226.3163 | 2928.7957 | 235.0981 | 2851.0671 | 226.3163 | 360.8 | 86244.5432 | 81473.8554 | 36957.4461 | 0 | 370977.6218
6661 | 249.9566 | 3388.8221 | 259.6555 | 3298.8846 | 249.9566 | 342.95 | 90490.2374 | 89984.3586 | 40817.9049 | 0 | 414190.5038
6662 | 247.4402 | 3478.9166 | 257.0418 | 3386.588 | 247.4402 | 359.25 | 93979.8482 | 89078.4875 | 40406.9917 | 0 | 405987.5787
6663 | 268.3642 | 1413.1443 | 278.7778 | 1375.6402 | 268.3642 | 376.8 | 106724.7324 | 96611.0974 | 43823.8672 | 0 | 435608.7035
6664 | 198.7923 | 1256.453 | 206.5061 | 1223.1075 | 198.7923 | 1261.65 | 265001.1765 | 71565.2132 | 32462.7759 | 0 | 146778.2643
6665 | 292.6697 | 85.0791 | 85.0791 | 82.8212 | 82.8212 | 1694.95 | 148312.1847 | 29815.6297 | 13524.7009 | 384652.311 | 24730.0984
6666 | 221.6323 | 0 | 0 | 0 | 0 | 1807.05 | 0 | 0 | 0 | 406252.0041 | 0
6667 | 210.0695 | 0 | 0 | 0 | 0 | 1910.95 | 0 | 0 | 0 | 385057.4237 | 0
6668 | 235.4123 | 0 | 0 | 0 | 0 | 1666.3 | 0 | 0 | 0 | 431510.6887 | 0
6669 | 195.0115 | 69.9396 | 69.9396 | 68.0834 | 68.0834 | 1547.45 | 111280.4475 | 24510.0414 | 11118.0271 | 232659.0884 | 30468.8338
6670 | 287.4671 | 298.6221 | 298.6221 | 290.6968 | 287.4671 | 1507.55 | 457773.238 | 103488.1657 | 46943.3818 | 0 | 141563.1241
6671 | 260.2743 | 270.3739 | 270.3739 | 263.1983 | 260.2743 | 1446.7 | 398022.3559 | 93698.7446 | 42502.7917 | 0 | 144009.6042
6672 | 282.8055 | 293.7792 | 293.7792 | 285.9824 | 282.8055 | 1381.2 | 413617.3132 | 101809.9792 | 46182.1378 | 0 | 174999.734
6673 | 230.7506 | 0 | 0 | 0 | 0 | 1410.7 | 0 | 0 | 0 | 274593.2612 | 0
6674 | 185.6882 | 0 | 0 | 0 | 0 | 1406.35 | 0 | 0 | 0 | 220968.988 | 0
6675 | 236.1892 | 0 | 0 | 0 | 0 | 1282.4 | 0 | 0 | 0 | 281065.1563 | 0
6676 | 198.1192 | 0 | 0 | 0 | 0 | 925.85 | 0 | 0 | 0 | 235761.891 | 0
6677 | 229.1968 | 0 | 0 | 0 | 0 | 926.25 | 0 | 0 | 0 | 272744.1484 | 0
6678 | 285.1363 | 0 | 0 | 0 | 0 | 1053.85 | 0 | 0 | 0 | 339312.2118 | 0
6679 | 164.7109 | 171.1026 | 171.1026 | 166.5616 | 164.7109 | 1417.95 | 247285.9126 | 59295.922 | 26897.2891 | 0 | 95869.9761
6680 | 199.3876 | 981.7068 | 207.1242 | 955.6529 | 199.3876 | 635.4 | 133979.1643 | 71779.5316 | 32559.9931 | 0 | 272084.3022
6681 | 1165.9822 | 1837.4461 | 1211.2266 | 1788.6813 | 1165.9822 | 341.9 | 421357.7072 | 419753.5942 | 190404.8942 | 0 | 1933315.0958
6682 | 1779.2506 | 2918.0327 | 1848.2944 | 2840.5897 | 1779.2506 | 348.35 | 654440.4812 | 640530.212 | 290551.6212 | 0 | 2938699.2353
6683 | 1668.8448 | 3350.5889 | 1733.6041 | 3261.6661 | 1668.8448 | 356.1 | 626990.1805 | 600784.1136 | 272522.3493 | 0 | 2743413.901
6684 | 1306.7683 | 3308.51 | 1357.4768 | 3220.704 | 1306.7683 | 349.85 | 483173.0247 | 470436.5736 | 213395.2569 | 0 | 2156363.6442
6685 | 1367.4141 | 3070.5012 | 1420.4762 | 2989.0117 | 1367.4141 | 334.65 | 483567.485 | 492269.0803 | 223298.7245 | 0 | 2277223.0914
6686 | 1211.3632 | 1401.7839 | 1258.3696 | 1364.5813 | 1211.3632 | 352 | 451634.5384 | 436090.7394 | 197815.6048 | 0 | 1996326.4959
6687 | 1187.0499 | 168.6022 | 168.6022 | 164.1276 | 164.1276 | 689.6 | 119622.8003 | 59085.9203 | 26802.0299 | 1875016.5753 | 210523.6224
6688 | 1289.3338 | 292.6604 | 292.6604 | 284.8933 | 284.8933 | 1495.95 | 450249.1527 | 102561.6014 | 46523.0819 | 1841139.308 | 140562.9114
6689 | 1473.5876 | 183.724 | 183.724 | 178.8481 | 178.8481 | 1673 | 316284.3374 | 64385.3198 | 29205.8965 | 2373257.4292 | 57246.255
6690 | 1450.7679 | 1.07 | 1.07 | 1.0416 | 1.0416 | 1770.3 | 1945.8956 | 374.9661 | 170.0888 | 2657348.4041 | 234.294
6691 | 1377.5454 | 0 | 0 | 0 | 0 | 1880.55 | 0 | 0 | 0 | 4680899.2216 | 0
6692 | 1000.6964 | 0 | 0 | 0 | 0 | 1729.4 | 0 | 0 | 0 | 3400366.289 | 0
6693 | 1480.0672 | 0 | 0 | 0 | 0 | 1530.45 | 0 | 0 | 0 | 5029268.4645 | 0
6694 | 1346.4339 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1493.05 | 488937.3491 | 111351.8261 | 50510.4255 | 3524144.7663 | 155062.8243
6695 | 1285.8327 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1446.55 | 916684.0262 | 215514.4963 | 97759.7701 | 2335042.0932 | 327642.4
6696 | 1184.8307 | 0 | 0 | 0 | 0 | 1412.8 | 0 | 0 | 0 | 2171794.7208 | 0
6697 | 1309.9178 | 0 | 0 | 0 | 0 | 1110.65 | 0 | 0 | 0 | 1558802.1499 | 0
6698 | 1500.2676 | 0 | 0 | 0 | 0 | 1404.75 | 0 | 0 | 0 | 1785318.4761 | 0
6699 | 1316.9102 | 0 | 0 | 0 | 0 | 1406.4 | 0 | 0 | 0 | 1567123.1582 | 0
6700 | 1187.9385 | 0 | 0 | 0 | 0 | 1404.55 | 0 | 0 | 0 | 1413646.79 | 0
6701 | 966.5111 | 0 | 0 | 0 | 0 | 1403.55 | 0 | 0 | 0 | 1150148.2054 | 0
6702 | 1231.447 | 0 | 0 | 0 | 0 | 1392.45 | 0 | 0 | 0 | 1465421.9502 | 0
6703 | 1040.3999 | 427.3632 | 427.3632 | 416.0212 | 416.0212 | 1125 | 498060.2281 | 149767.6491 | 67936.2697 | 1144485.9969 | 356318.375
6704 | 1049.4094 | 1090.1311 | 1090.1311 | 1061.1996 | 1049.4094 | 266.95 | 296564.6556 | 377787.3948 | 171368.5599 | 0 | 1818679.0127
6705 | 1392.0499 | 1539.0422 | 1446.0681 | 1498.1969 | 1392.0499 | 275.1 | 404420.536 | 501137.946 | 227321.7405 | 0 | 2401146.7863
6706 | 1491.899 | 2582.0385 | 1549.7918 | 2513.5126 | 1491.899 | 284.7 | 448220.9089 | 537083.6515 | 243627.1119 | 0 | 2559054.4096
6707 | 1479.7011 | 2849.7146 | 1537.1215 | 2774.0848 | 1479.7011 | 300.8 | 469124.3937 | 532692.3967 | 241635.19 | 0 | 2514308.1125
6708 | 1376.6976 | 3423.2896 | 1430.1204 | 3332.4374 | 1376.6976 | 295.55 | 429694.6584 | 495611.1187 | 224814.7102 | 0 | 2346512.1425
6709 | 1804.4341 | 3295.2985 | 1874.4546 | 3207.8431 | 1804.4341 | 283.35 | 539271.4929 | 649596.2648 | 294664.0835 | 0 | 3097581.7445
6710 | 1768.6143 | 3206.4817 | 1837.2446 | 3121.3835 | 1768.6143 | 285 | 533322.8217 | 636701.1502 | 288814.7162 | 0 | 3033173.5348
6711 | 1995.8376 | 2175.7132 | 2073.286 | 2117.9709 | 1995.8376 | 289.5 | 613523.5153 | 718501.5526 | 325920.2876 | 0 | 3413880.2935
6712 | 1636.7689 | 1868.9604 | 1700.2834 | 1819.3592 | 1636.7689 | 295.8 | 513819.4011 | 589236.7921 | 267284.356 | 0 | 2789381.5031
6713 | 1880.17 | 277.497 | 277.497 | 270.1323 | 270.1323 | 879.9 | 252427.2599 | 97247.64 | 44112.61 | 2951199.0483 | 296174.6018
6714 | 1605.2708 | 0 | 0 | 0 | 0 | 1638.15 | 0 | 0 | 0 | 2942461.4167 | 0
6715 | 1176.8108 | 0 | 0 | 0 | 0 | 1850.05 | 0 | 0 | 0 | 3998803.0338 | 0
6716 | 1179.3922 | 0 | 0 | 0 | 0 | 1662.4 | 0 | 0 | 0 | 4007574.5563 | 0
6717 | 1017.789 | 0 | 0 | 0 | 0 | 1447.05 | 0 | 0 | 0 | 3458447.0798 | 0
6718 | 1282.7249 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1432.05 | 470464.1935 | 111351.8261 | 50510.4255 | 3307661.8222 | 173721.1383
6719 | 1643.2243 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1414.2 | 901781.8966 | 215514.4963 | 97759.7701 | 3549458.6276 | 346793.6
6720 | 1414.8044 | 0 | 0 | 0 | 0 | 861.25 | 0 | 0 | 0 | 2593336.5147 | 0
6721 | 1612.9237 | 0 | 0 | 0 | 0 | 850.1 | 0 | 0 | 0 | 1919379.1602 | 0
6722 | 1513.4756 | 0 | 0 | 0 | 0 | 275.1 | 0 | 0 | 0 | 1801035.9354 | 0
6723 | 1312.2486 | 0 | 0 | 0 | 0 | 271.45 | 0 | 0 | 0 | 1561575.8197 | 0
6724 | 926.8872 | 0 | 0 | 0 | 0 | 269.95 | 0 | 0 | 0 | 1102995.8273 | 0
6725 | 1116.4602 | 0 | 0 | 0 | 0 | 270.7 | 0 | 0 | 0 | 1328587.5975 | 0
6726 | 923.0026 | 0 | 0 | 0 | 0 | 276.55 | 0 | 0 | 0 | 1098373.0451 | 0
6727 | 974.5728 | 0 | 0 | 0 | 0 | 289.5 | 0 | 0 | 0 | 1786391.9457 | 0
6728 | 1109.3055 | 106.0142 | 106.0142 | 103.2006 | 103.2006 | 313.7 | 34293.0672 | 37152.2236 | 16852.6614 | 1844190.3087 | 170346.6534
6729 | 1453.1366 | 431.9412 | 431.9412 | 420.4778 | 420.4778 | 907.9 | 404079.6625 | 151371.9943 | 68664.0185 | 1892863.6776 | 449489.7943
6730 | 1636.4299 | 421.4078 | 421.4078 | 410.2238 | 410.2238 | 809.5 | 351903.2552 | 147680.5805 | 66989.5522 | 2247635.7691 | 478040.513
6731 | 1700.6594 | 412.6787 | 412.6787 | 401.7264 | 401.7264 | 368.9 | 156801.4139 | 144621.5124 | 65601.9249 | 2380944.161 | 641395.8219
6732 | 1576.4513 | 731.2074 | 731.2074 | 711.8015 | 711.8015 | 360.8 | 271681.6299 | 256248.5563 | 116237.1923 | 1584902.9492 | 1142102.7648
6733 | 1782.2292 | 1677.3757 | 1677.3757 | 1632.8591 | 1632.8591 | 342.95 | 590441.5766 | 587829.2582 | 266645.8829 | 273795.44 | 2648494.4989
6734 | 1708.3705 | 2089.4758 | 1774.6629 | 2034.0222 | 1708.3705 | 359.25 | 649880.3921 | 615013.3868 | 278976.9058 | 0 | 2803008.929
6735 | 1688.8665 | 2265.2 | 1754.4031 | 2205.0828 | 1688.8665 | 935.8 | 1673759.6921 | 607991.9245 | 275791.8924 | 0 | 1797291.6835
6736 | 1513.6533 | 2024.0009 | 1572.3899 | 1970.2851 | 1513.6533 | 1687.75 | 2702337.8249 | 544915.1884 | 247179.5841 | 0 | 472638.2432
6737 | 1543.6956 | 846.9853 | 846.9853 | 824.5068 | 824.5068 | 1898.7 | 1652899.0551 | 296822.4366 | 134641.9553 | 1318273.0515 | 81755.7858
6738 | 1589.396 | 33.6978 | 33.6978 | 32.8035 | 32.8035 | 1908.65 | 65997.196 | 11809.2479 | 5356.8061 | 2853234.1747 | 2933.2485
6739 | 1404.3944 | 0 | 0 | 0 | 0 | 1910.95 | 0 | 0 | 0 | 4772132.2629 | 0
6740 | 1464.5285 | 0 | 0 | 0 | 0 | 1863.8 | 0 | 0 | 0 | 4976467.7445 | 0
6741 | 1266.4092 | 0 | 0 | 0 | 0 | 1812.45 | 0 | 0 | 0 | 4303258.5805 | 0
6742 | 1237.6625 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1837.7 | 599123.4589 | 111351.8261 | 50510.4255 | 3154539.736 | 49643.3502
6743 | 1469.1901 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1621.2 | 1025943.5996 | 215514.4963 | 97759.7701 | 2958090.5757 | 224249.6
6744 | 1402.3734 | 0 | 0 | 0 | 0 | 1474.55 | 0 | 0 | 0 | 2570550.4734 | 0
6745 | 1487.8366 | 0 | 0 | 0 | 0 | 1296.6 | 0 | 0 | 0 | 1770525.573 | 0
6746 | 1173.9536 | 0 | 0 | 0 | 0 | 1184.1 | 0 | 0 | 0 | 1397004.7733 | 0
6747 | 1220.5699 | 0 | 0 | 0 | 0 | 1180.45 | 0 | 0 | 0 | 1452478.1596 | 0
6748 | 1091.5981 | 0 | 0 | 0 | 0 | 818.95 | 0 | 0 | 0 | 1299001.7914 | 0
6749 | 1039.5433 | 0 | 0 | 0 | 0 | 991.8 | 0 | 0 | 0 | 1237056.5103 | 0
6750 | 1033.3278 | 0 | 0 | 0 | 0 | 1005.55 | 0 | 0 | 0 | 1229660.0594 | 0
6751 | 1125.2328 | 345.3122 | 345.3122 | 336.1478 | 336.1478 | 1198.5 | 425389.4928 | 121013.2099 | 54892.9366 | 1446392.7387 | 263723.1555
6752 | 1299.0474 | 958.9674 | 958.9674 | 933.5169 | 933.5169 | 1222.7 | 1200964.5268 | 336066.0974 | 152443.3158 | 670017.4063 | 710272.6437
6753 | 1556.2421 | 1445.8729 | 1445.8729 | 1407.5002 | 1407.5002 | 1527.25 | 2263682.9996 | 506700.0638 | 229844.7789 | 272644.0158 | 651319.9665
6754 | 1612.0778 | 775.047 | 775.047 | 754.4777 | 754.4777 | 1514.75 | 1206143.8808 | 271611.9731 | 123206.2089 | 1571980.9263 | 358365.8595
6755 | 0 | 1333.495 | 0 | 1298.1047 | 0 | 1277.9 | 0 | 0 | 0 | 0 | 0
6756 | 1493.2053 | 2580.096 | 1551.1484 | 2511.6216 | 1493.2053 | 1089.8 | 1716628.3473 | 537553.8932 | 243840.4188 | 0 | 1359115.4267
6757 | 1246.7915 | 2851.358 | 1295.1724 | 2775.6845 | 1246.7915 | 891.95 | 1172483.0854 | 448844.9566 | 203601.0595 | 0 | 1381507.3725
6758 | 1561.9623 | 2670.3016 | 1622.5746 | 2599.4333 | 1561.9623 | 1386.1 | 2286008.323 | 562306.4446 | 255068.4511 | 0 | 958888.6842
6759 | 1551.8563 | 1438.8526 | 1438.8526 | 1400.6662 | 1400.6662 | 1725.8 | 2550056.4269 | 504239.8494 | 228728.7983 | 277131.4071 | 375938.3454
6760 | 1685.1478 | 1465.5426 | 1465.5426 | 1426.6479 | 1426.6479 | 1891.25 | 2848660.1954 | 513593.2513 | 232971.6054 | 473830.3474 | 151866.0037
6761 | 1491.6931 | 701.1818 | 701.1818 | 682.5728 | 682.5728 | 1899.95 | 1369172.3815 | 245726.2066 | 111464.1376 | 1483117.5958 | 66846.8067
6762 | 1361.0005 | 19.3031 | 19.3031 | 18.7908 | 18.7908 | 1908.65 | 37788.2412 | 6764.6797 | 3068.5339 | 2460270.3986 | 1680.2919
6763 | 1278.8742 | 0 | 0 | 0 | 0 | 1910.95 | 0 | 0 | 0 | 4345614.6573 | 0
6764 | 1114.9063 | 0 | 0 | 0 | 0 | 1862.8 | 0 | 0 | 0 | 3788451.5734 | 0
6765 | 1342.5492 | 0 | 0 | 0 | 0 | 1845.95 | 0 | 0 | 0 | 4561982.1034 | 0
6766 | 1593.5002 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1837.7 | 599653.8094 | 111351.8261 | 50510.4255 | 4363676.1964 | 49643.3502
6767 | 1337.8875 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1759.2 | 1110823.6704 | 215514.4963 | 97759.7701 | 2511924.504 | 142553.6
6768 | 1203.4772 | 0 | 0 | 0 | 0 | 1576.7 | 0 | 0 | 0 | 2205973.7846 | 0
6769 | 923.0026 | 0 | 0 | 0 | 0 | 1466.1 | 0 | 0 | 0 | 1098373.0451 | 0
6770 | 1208.9158 | 0 | 0 | 0 | 0 | 1198.1 | 0 | 0 | 0 | 1438609.8127 | 0
6771 | 935.4336 | 0 | 0 | 0 | 0 | 1180.45 | 0 | 0 | 0 | 1113165.9481 | 0
6772 | 835.9855 | 0 | 0 | 0 | 0 | 1178.95 | 0 | 0 | 0 | 994822.7243 | 0
6773 | 948.6415 | 0 | 0 | 0 | 0 | 1179.7 | 0 | 0 | 0 | 1128883.4075 | 0
6774 | 1023.2276 | 0 | 0 | 0 | 0 | 1290.05 | 0 | 0 | 0 | 1217640.825 | 0
6775 | 855.543 | 8.2201 | 8.2201 | 8.0019 | 8.0019 | 1434.2 | 12096.9399 | 2880.6862 | 1306.7113 | 1553542.7501 | 4431.9114
6776 | 734.4698 | 548.3466 | 548.3466 | 533.7938 | 533.7938 | 1222.7 | 685142.9916 | 192165.7577 | 87168.5228 | 367839.1035 | 406140.8046
6777 | 1354.9452 | 1614.3628 | 1407.5233 | 1571.5185 | 1354.9452 | 1358.9 | 1941086.9575 | 487780.281 | 221262.5552 | 0 | 868655.3837
6778 | 1584.1702 | 2004.6875 | 1645.6433 | 1951.4842 | 1584.1702 | 1091.9 | 1825362.3743 | 570301.2551 | 258694.986 | 0 | 1438584.9159
6779 | 1585.9435 | 1934.5817 | 1647.4851 | 1883.2389 | 1585.9435 | 368.9 | 617389.7827 | 570939.665 | 258984.5758 | 0 | 2586832.4657
6780 | 1196.4829 | 2141.7962 | 1242.9122 | 2084.9541 | 1196.4829 | 909.8 | 1146992.6378 | 430733.8282 | 195385.6504 | 0 | 1304405.6096
6781 | 1424.9425 | 1633.6898 | 1480.2376 | 1590.3326 | 1424.9425 | 617.45 | 924098.7153 | 512979.3 | 232693.1102 | 0 | 1970054.2534
6782 | 1249.168 | 1767.0495 | 1297.6416 | 1720.1529 | 1249.168 | 813.75 | 1071451.1046 | 449700.4818 | 203989.1352 | 0 | 1481825.5459
6783 | 1398.008 | 2359.8517 | 1452.2573 | 2297.2225 | 1398.008 | 1498.3 | 2206517.631 | 503282.8782 | 228294.7056 | 0 | 701380.6111
6784 | 1407.3079 | 1796.4362 | 1461.9182 | 1748.7598 | 1407.3079 | 1687.75 | 2504402.0956 | 506630.8602 | 229813.3874 | 0 | 439431.9058
6785 | 1093.0432 | 646.8377 | 646.8377 | 629.671 | 629.671 | 1827.45 | 1213142.9202 | 226681.5692 | 102825.2785 | 849361.2857 | 106351.365
6786 | 1275.5441 | 16.0745 | 16.0745 | 15.6479 | 15.6479 | 1902.65 | 31380.436 | 5633.2286 | 2555.2951 | 2309389.7875 | 1491.1099
6787 | 1074.0238 | 0 | 0 | 0 | 0 | 1910.95 | 0 | 0 | 0 | 3649532.8826 | 0
6788 | 1001.4733 | 0 | 0 | 0 | 0 | 1827.8 | 0 | 0 | 0 | 3403006.3244 | 0
6789 | 1020.8968 | 0 | 0 | 0 | 0 | 1801.45 | 0 | 0 | 0 | 3469007.2245 | 0
6790 | 1296.7098 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1799.7 | 586281.4131 | 111351.8261 | 50510.4255 | 3355182.4682 | 61266.5622
6791 | 1046.5357 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1729.2 | 1092942.7166 | 215514.4963 | 97759.7701 | 1521911.0265 | 160313.6
6792 | 1089.2673 | 0 | 0 | 0 | 0 | 1706.7 | 0 | 0 | 0 | 1996627.0159 | 0
6793 | 1177.0613 | 0 | 0 | 0 | 0 | 1582.1 | 0 | 0 | 0 | 1400702.9994 | 0
6794 | 1226.0084 | 0 | 0 | 0 | 0 | 1419.8 | 0 | 0 | 0 | 1458950.0543 | 0
6795 | 1172.3997 | 0 | 0 | 0 | 0 | 1416.15 | 0 | 0 | 0 | 1395155.6609 | 0
6796 | 942.426 | 0 | 0 | 0 | 0 | 1414.65 | 0 | 0 | 0 | 1121486.9559 | 0
6797 | 939.3183 | 0 | 0 | 0 | 0 | 1415.4 | 0 | 0 | 0 | 1117788.7302 | 0
6798 | 1045.7588 | 0 | 0 | 0 | 0 | 1421.25 | 0 | 0 | 0 | 1244452.9613 | 0
6799 | 671.3979 | 271.3753 | 271.3753 | 264.1731 | 264.1731 | 1434.2 | 398906.3832 | 95102.3243 | 43139.471 | 746443.0661 | 146307.393
6800 | 872.0645 | 789.9331 | 789.9331 | 768.9687 | 768.9687 | 1458.4 | 1177960.7334 | 276828.7345 | 125572.5898 | 188974.6793 | 407663.4032
6801 | 485.7777 | 675.9596 | 504.6285 | 658.02 | 485.7777 | 1495.1 | 765571.7852 | 174879.9663 | 79327.4958 | 0 | 245269.1527
6802 | 364.5171 | 1810.1412 | 378.662 | 1762.101 | 364.5171 | 1389.75 | 535973.0448 | 131226.1407 | 59525.6355 | 0 | 222446.5343
6803 | 364.7608 | 2720.4395 | 378.9144 | 2648.2406 | 364.7608 | 368.9 | 142403.8276 | 131313.8959 | 59565.4422 | 0 | 594961.3766
6804 | 378.6719 | 1985.9454 | 393.3663 | 1933.2395 | 378.6719 | 909.8 | 363343.9087 | 136321.884 | 61837.1213 | 0 | 412828.1054
6805 | 728.4592 | 1164.3723 | 756.7277 | 1133.4705 | 728.4592 | 891.95 | 682944.0576 | 262245.3051 | 118957.3842 | 0 | 807169.1953
6806 | 1278.5809 | 1495.5682 | 1328.196 | 1455.8767 | 1278.5809 | 1088.25 | 1467024.8375 | 460289.1395 | 208792.268 | 0 | 1165746.1748
6807 | 1456.5445 | 225.6367 | 225.6367 | 219.6484 | 219.6484 | 1548.15 | 360113.2233 | 79073.4336 | 35868.5881 | 2267230.429 | 97148.6537
6808 | 1463.702 | 221.4264 | 221.4264 | 215.5499 | 215.5499 | 1693.65 | 386504.9652 | 77597.9602 | 35199.297 | 2287862.8241 | 64636.7865
6809 | 1357.0867 | 29.1447 | 29.1447 | 28.3712 | 28.3712 | 1863.95 | 55858.562 | 10213.6397 | 4633.0205 | 2435535.4008 | 3778.2445
6810 | 968.9779 | 0 | 0 | 0 | 0 | 1908.65 | 0 | 0 | 0 | 1776136.4463 | 0
6811 | 859.4179 | 0 | 0 | 0 | 0 | 1910.95 | 0 | 0 | 0 | 2920302.154 | 0
6812 | 666.613 | 0 | 0 | 0 | 0 | 1818.3 | 0 | 0 | 0 | 2265150.8354 | 0
6813 | 1020.8968 | 0 | 0 | 0 | 0 | 1797.45 | 0 | 0 | 0 | 3469007.2245 | 0
6814 | 1041.8741 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1789.7 | 582852.0706 | 111351.8261 | 50510.4255 | 2489250.6815 | 64325.3022
6815 | 1133.5528 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1725.1 | 1090366.5498 | 215514.4963 | 97759.7701 | 1817595.0507 | 162740.8
6816 | 1121.8987 | 0 | 0 | 0 | 0 | 1696.7 | 0 | 0 | 0 | 2056440.3776 | 0
6817 | 916.0101 | 0 | 0 | 0 | 0 | 1587.1 | 0 | 0 | 0 | 1679046.5413 | 0
6818 | 1391.4963 | 0 | 0 | 0 | 0 | 1478.6 | 0 | 0 | 0 | 2550612.6849 | 0
6819 | 1013.9043 | 0 | 0 | 0 | 0 | 1427.3 | 0 | 0 | 0 | 1858486.6296 | 0
6820 | 1124.2295 | 0 | 0 | 0 | 0 | 1414.65 | 0 | 0 | 0 | 2060712.7615 | 0
6821 | 933.1028 | 0 | 0 | 0 | 0 | 1429.7 | 0 | 0 | 0 | 1710377.3505 | 0
6822 | 828.2161 | 0 | 0 | 0 | 0 | 1444.05 | 0 | 0 | 0 | 1518120.1128 | 0
6823 | 1121.5161 | 103.0515 | 103.0515 | 100.3166 | 100.3166 | 1445.35 | 153309.2177 | 36113.968 | 16381.6972 | 1871858.7077 | 54463.3021
6824 | 241.5452 | 250.9181 | 250.9181 | 244.2589 | 241.5452 | 1458.4 | 372336.2643 | 86956.2809 | 39444.3352 | 0 | 130820.772
6825 | 286.4047 | 457.7504 | 297.5189 | 445.6019 | 286.4047 | 1538.4 | 467345.5969 | 103105.679 | 46769.8816 | 0 | 132204.3929
6826 | 227.0213 | 1929.1373 | 235.8305 | 1877.939 | 227.0213 | 1518.75 | 366618.6424 | 81727.6811 | 37072.5843 | 0 | 109254.0182
6827 | 226.7086 | 2750.4537 | 235.5064 | 2677.4582 | 226.7086 | 1382.9 | 334216.9634 | 81615.1028 | 37021.5175 | 0 | 139901.8887
6828 | 265.6099 | 2789.8462 | 275.9159 | 2715.8052 | 265.6099 | 1269.8 | 358151.9125 | 95619.5689 | 43374.0989 | 0 | 193948.3589
6829 | 180.5099 | 2701.1188 | 187.5146 | 2629.4326 | 180.5099 | 1251.95 | 239055.9344 | 64983.5756 | 29477.2719 | 0 | 135030.4549
6830 | 244.417 | 1704.0065 | 253.9015 | 1658.7831 | 244.417 | 1490.6 | 384987.2939 | 87990.1136 | 39913.2932 | 0 | 124506.0108
6831 | 281.7887 | 164.5363 | 164.5363 | 160.1696 | 160.1696 | 1569.8 | 266379.7574 | 57661.0491 | 26155.6925 | 222927.8088 | 65695.842
6832 | 244.5879 | 254.0792 | 254.0792 | 247.3361 | 244.5879 | 1808.65 | 467995.3299 | 88051.6471 | 39941.2055 | 0 | 46652.2781
6833 | 259.577 | 269.6498 | 269.6498 | 262.4935 | 259.577 | 1898.95 | 520783.6595 | 93447.7159 | 42388.9222 | 0 | 26230.2547
6834 | 261.3999 | 1.9935 | 1.9935 | 1.9406 | 1.9406 | 1908.65 | 3914.1069 | 698.6019 | 316.8936 | 475588.9317 | 173.4736
6835 | 181.0159 | 0 | 0 | 0 | 0 | 1910.95 | 0 | 0 | 0 | 331802.1689 | 0
6836 | 341.8528 | 0 | 0 | 0 | 0 | 1862.8 | 0 | 0 | 0 | 626616.1817 | 0
6837 | 203.5578 | 120.786 | 120.786 | 117.5804 | 117.5804 | 1845.45 | 228650.6793 | 42328.9401 | 19200.8775 | 157596.6003 | 17970.1467
6838 | 261.8282 | 271.9882 | 271.9882 | 264.7698 | 261.8282 | 1837.7 | 507321.1278 | 94258.1401 | 42756.5397 | 0 | 42494.6844
6839 | 280.4747 | 291.3588 | 291.3588 | 283.6263 | 280.4747 | 1739.2 | 516470.2663 | 100970.886 | 45801.5158 | 0 | 73147.7974
6840 | 239.297 | 248.5829 | 248.5829 | 241.9856 | 239.297 | 1702.6 | 431296.0996 | 86146.9055 | 39077.1935 | 0 | 71166.9158
6841 | 247.8433 | 0 | 0 | 0 | 0 | 1626.85 | 0 | 0 | 0 | 294933.5028 | 0
6842 | 213.658 | 0 | 0 | 0 | 0 | 1690.85 | 0 | 0 | 0 | 254253.0196 | 0
6843 | 278.9208 | 0 | 0 | 0 | 0 | 1581.15 | 0 | 0 | 0 | 331915.7602 | 0
6844 | 284.3594 | 0 | 0 | 0 | 0 | 1674.95 | 0 | 0 | 0 | 338387.6553 | 0
6845 | 227.6429 | 0 | 0 | 0 | 0 | 1675.35 | 0 | 0 | 0 | 270895.0355 | 0
6846 | 224.5351 | 0 | 0 | 0 | 0 | 1678.15 | 0 | 0 | 0 | 267196.8098 | 0
6847 | 211.1465 | 219.3405 | 219.3405 | 213.5193 | 211.1465 | 1703 | 379636.3272 | 76012.757 | 34480.2311 | 0 | 62710.362
6848 | 228.4266 | 1183.0075 | 237.29 | 1151.6111 | 228.4266 | 1541.8 | 371989.9979 | 82233.5844 | 37302.0676 | 0 | 104665.0788
6849 | 798.5303 | 886.2833 | 829.5168 | 862.7618 | 798.5303 | 1534.9 | 1296963.6237 | 287470.8951 | 130399.9921 | 0 | 371396.4258
6850 | 1189.1388 | 2143.9725 | 1235.2832 | 2087.0726 | 1189.1388 | 1493.05 | 1883395.4353 | 428089.9853 | 194186.3739 | 0 | 602833.939
6851 | 1149.785 | 1542.3654 | 1194.4021 | 1501.4318 | 1149.785 | 1500.8 | 1834690.086 | 413922.5953 | 187759.8884 | 0 | 573972.6655
6852 | 1049.2511 | 2156.9835 | 1089.9669 | 2099.7384 | 1049.2511 | 1431.2 | 1592334.902 | 377730.4064 | 171342.7094 | 0 | 596814.0422
6853 | 1004.3509 | 2755.5397 | 1043.3246 | 2682.4092 | 1004.3509 | 1243.65 | 1316490.604 | 361566.324 | 164010.502 | 0 | 759640.8032
6854 | 1250.2042 | 2904.2114 | 1298.7179 | 2827.1352 | 1250.2042 | 1496.7 | 1977422.3598 | 450073.5289 | 204158.3535 | 0 | 629227.7975
6855 | 903.8122 | 1957.6992 | 938.8842 | 1905.743 | 903.8122 | 1668.65 | 1598857.2625 | 325372.3869 | 147592.5299 | 0 | 299478.1678
6856 | 1265.9984 | 923.9327 | 923.9327 | 899.412 | 899.412 | 1827.1 | 1741639.8773 | 323788.3239 | 146873.9814 | 671952.9046 | 152218.7394
6857 | 1338.141 | 16.3051 | 16.3051 | 15.8724 | 15.8724 | 1880.5 | 31599.4864 | 5714.0465 | 2591.955 | 2423718.4769 | 1856.552
6858 | 1446.2015 | 0 | 0 | 0 | 0 | 1880.8 | 0 | 0 | 0 | 2650887.2945 | 0
6859 | 1536.9168 | 0 | 0 | 0 | 0 | 1882.05 | 0 | 0 | 0 | 5222443.1913 | 0
6860 | 1201.1464 | 0 | 0 | 0 | 0 | 1841.9 | 0 | 0 | 0 | 4081495.5623 | 0
6861 | 1445.882 | 0 | 0 | 0 | 0 | 1824.45 | 0 | 0 | 0 | 4913106.8831 | 0
6862 | 1395.381 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1815.2 | 591072.0003 | 111351.8261 | 50510.4255 | 3690467.0325 | 56525.5152
6863 | 1485.5058 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1808.85 | 1141681.807 | 215514.4963 | 97759.7701 | 3013531.3311 | 113160.8
6864 | 1257.086 | 0 | 0 | 0 | 0 | 1713.2 | 0 | 0 | 0 | 2304238.5958 | 0
6865 | 1266.4092 | 0 | 0 | 0 | 0 | 1463 | 0 | 0 | 0 | 1507026.9896 | 0
6866 | 1198.8156 | 0 | 0 | 0 | 0 | 1477.9 | 0 | 0 | 0 | 1426590.5795 | 0
6867 | 1652.5475 | 0 | 0 | 0 | 0 | 1470.7 | 0 | 0 | 0 | 1966531.5381 | 0
6868 | 1262.5245 | 0 | 0 | 0 | 0 | 1468.85 | 0 | 0 | 0 | 1502404.2074 | 0
6869 | 1325.4565 | 0 | 0 | 0 | 0 | 1467.85 | 0 | 0 | 0 | 1577293.279 | 0
6870 | 1463.7515 | 0 | 0 | 0 | 0 | 1474.45 | 0 | 0 | 0 | 1741864.3243 | 0
6871 | 1647.1089 | 518.1963 | 518.1963 | 504.4437 | 504.4437 | 1468.5 | 779803.8044 | 181599.7226 | 82375.652 | 2094505.44 | 262440.3495
6872 | 1347.642 | 1301.5704 | 1301.5704 | 1267.0274 | 1267.0274 | 1287.95 | 1716232.0982 | 456129.8785 | 206905.581 | 147766.4989 | 883102.9233
6873 | 1537.3752 | 1467.8197 | 1467.8197 | 1428.8645 | 1428.8645 | 619.7 | 931949.2412 | 514391.2374 | 233333.5807 | 198899.9622 | 1930541.4117
6874 | 2055.2559 | 2135.0097 | 2135.0097 | 2078.3477 | 2055.2559 | 284.7 | 618896.3318 | 739892.137 | 335623.2943 | 0 | 3525380.507
6875 | 1950.1673 | 2025.8427 | 2025.8427 | 1972.078 | 1950.1673 | 300.8 | 622546.4631 | 702060.2197 | 318462.3163 | 0 | 3313723.7664
6876 | 1632.9415 | 2589.3424 | 1696.3079 | 2520.6226 | 1632.9415 | 295.55 | 512489.6154 | 587858.9314 | 266659.343 | 0 | 2783267.0988
6877 | 1578.9248 | 2594.4959 | 1640.1948 | 2525.6394 | 1578.9248 | 283.35 | 474571.7624 | 568412.9456 | 257838.4278 | 0 | 2710461.342
6878 | 1500.0918 | 2548.1475 | 1558.3027 | 2480.5211 | 1500.0918 | 285 | 451624.2144 | 540033.0642 | 244964.9983 | 0 | 2572657.5142
6879 | 1560.4337 | 2073.9041 | 1620.9862 | 2018.8638 | 1560.4337 | 1088.6 | 1795958.589 | 561756.1392 | 254818.8265 | 0 | 1422179.2924
6880 | 1354.9627 | 1056.3647 | 1056.3647 | 1028.3294 | 1028.3294 | 1204.8 | 1303927.0965 | 370198.5698 | 167926.1846 | 598718.9224 | 800430.0304
6881 | 1401.9869 | 577.7323 | 577.7323 | 562.3996 | 562.3996 | 1584.75 | 938235.4202 | 202463.8558 | 91839.8546 | 1538963.5038 | 228596.3707
6882 | 1511.5332 | 0 | 0 | 0 | 0 | 1797.65 | 0 | 0 | 0 | 2770640.4124 | 0
6883 | 1511.2516 | 0 | 0 | 0 | 0 | 1851.05 | 0 | 0 | 0 | 5135232.9062 | 0
6884 | 1042.651 | 0 | 0 | 0 | 0 | 1816.4 | 0 | 0 | 0 | 3542928.2305 | 0
6885 | 1417.1352 | 0 | 0 | 0 | 0 | 1724.2 | 0 | 0 | 0 | 4815425.5523 | 0
6886 | 1734.126 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1716.35 | 557766.2769 | 111351.8261 | 50510.4255 | 4841522.7022 | 86761.1601
6887 | 1786.9578 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1679.75 | 1056566.0831 | 215514.4963 | 97759.7701 | 4037865.2747 | 189588
6888 | 1498.7138 | 0 | 0 | 0 | 0 | 1493.6 | 0 | 0 | 0 | 2747142.3056 | 0
6889 | 1306.0331 | 0 | 0 | 0 | 0 | 1584.95 | 0 | 0 | 0 | 1554179.3676 | 0
6890 | 1539.8915 | 0 | 0 | 0 | 0 | 1419.8 | 0 | 0 | 0 | 1832470.8553 | 0
6891 | 1354.9802 | 0 | 0 | 0 | 0 | 1416.15 | 0 | 0 | 0 | 1612426.4225 | 0
6892 | 1587.2847 | 0 | 0 | 0 | 0 | 1401.8 | 0 | 0 | 0 | 1888868.7978 | 0
6893 | 1386.8347 | 0 | 0 | 0 | 0 | 1415.4 | 0 | 0 | 0 | 1650333.2371 | 0
6894 | 1682.8481 | 0 | 0 | 0 | 0 | 1432.4 | 0 | 0 | 0 | 2002589.239 | 0
6895 | 1314.5969 | 330.7284 | 330.7284 | 321.9511 | 321.9511 | 1457.5 | 495071.4886 | 115902.3855 | 52574.6099 | 1819519.7736 | 170963.9925
6896 | 1491.5815 | 1073.1601 | 1073.1601 | 1044.679 | 1044.679 | 1481.7 | 1631163.0597 | 376084.4454 | 170596.0831 | 819172.1781 | 530003.7323
6897 | 1238.8415 | 1286.9139 | 1286.9139 | 1252.7599 | 1238.8415 | 1749.4 | 2289842.0803 | 445982.9494 | 202302.8212 | 0 | 310453.5546
6898 | 1931.0148 | 2005.9476 | 2005.9476 | 1952.7108 | 1931.0148 | 1640.9 | 3351483.8892 | 695165.3208 | 315334.7136 | 0 | 693427.4075
6899 | 1849.8422 | 2017.3567 | 1921.6247 | 1963.8172 | 1849.8422 | 1513.6 | 2958172.7672 | 665943.1996 | 302079.2347 | 0 | 899763.2563
6900 | 1624.0727 | 3654.6564 | 1687.0937 | 3557.6638 | 1624.0727 | 1457.65 | 2495005.8004 | 584666.1814 | 265211.0762 | 0 | 880815.8429
6901 | 1805.6859 | 2968.5383 | 1875.7552 | 2889.7549 | 1805.6859 | 788.15 | 1498913.0854 | 650046.928 | 294868.5093 | 0 | 2188220.4712
6902 | 1579.4376 | 2874.6241 | 1640.7277 | 2798.3332 | 1579.4376 | 1456.1 | 2426435.7983 | 568597.5461 | 257922.1647 | 0 | 859056.1259
6903 | 1451.8731 | 2234.5397 | 1508.2126 | 2175.2362 | 1451.8731 | 1785.8 | 2734229.5326 | 522674.3228 | 237090.8803 | 0 | 310991.2221
6904 | 1128.7455 | 657.152 | 657.152 | 639.7116 | 639.7116 | 1891.75 | 1274719.022 | 230296.1696 | 104464.9014 | 896399.1733 | 67783.8768
6905 | 1228.0848 | 103.1751 | 103.1751 | 100.4369 | 100.4369 | 1899.95 | 200566.1645 | 36157.2893 | 16401.3482 | 2066978.6047 | 9836.2156
6906 | 1434.2978 | 0 | 0 | 0 | 0 | 1908.65 | 0 | 0 | 0 | 2629067.8784 | 0
6907 | 1492.2516 | 0 | 0 | 0 | 0 | 1910.95 | 0 | 0 | 0 | 5070670.8281 | 0
6908 | 1240.7703 | 0 | 0 | 0 | 0 | 1863.8 | 0 | 0 | 0 | 4216137.3944 | 0
6909 | 1418.6891 | 0 | 0 | 0 | 0 | 1847.45 | 0 | 0 | 0 | 4820705.623 | 0
6910 | 1613.7006 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1839.7 | 599374.9705 | 111351.8261 | 50510.4255 | 4432317.1319 | 49031.6022
6911 | 1366.6343 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1821.7 | 1149165.4463 | 215514.4963 | 97759.7701 | 2609605.8314 | 105553.6
6912 | 1386.8347 | 0 | 0 | 0 | 0 | 1805.7 | 0 | 0 | 0 | 2542067.9189 | 0
6913 | 1509.5909 | 0 | 0 | 0 | 0 | 1719.6 | 0 | 0 | 0 | 1796413.1531 | 0
6914 | 1275.7325 | 0 | 0 | 0 | 0 | 1690 | 0 | 0 | 0 | 1518121.6667 | 0
6915 | 1501.8215 | 0 | 0 | 0 | 0 | 1682.25 | 0 | 0 | 0 | 1787167.5898 | 0
6916 | 1306.0331 | 0 | 0 | 0 | 0 | 1668.95 | 0 | 0 | 0 | 1554179.3676 | 0
6917 | 1323.1257 | 0 | 0 | 0 | 0 | 1669.7 | 0 | 0 | 0 | 1574519.6092 | 0
6918 | 1096.2598 | 0 | 0 | 0 | 0 | 1675.55 | 0 | 0 | 0 | 1304549.1299 | 0
6919 | 1443.5696 | 206.5466 | 206.5466 | 201.065 | 201.065 | 1688.5 | 358052.188 | 72383.3831 | 32833.9068 | 2277511.0031 | 61306.938
6920 | 1285.1606 | 814.772 | 814.772 | 793.1484 | 793.1484 | 1507.2 | 1261026.3846 | 285533.4087 | 129521.1268 | 901858.5103 | 382595.136
6921 | 1191.5872 | 1237.8262 | 1237.8262 | 1204.975 | 1191.5872 | 1759.4 | 2213970.3949 | 428971.383 | 194586.1857 | 0 | 286695.8322
6922 | 1744.2447 | 1811.9289 | 1811.9289 | 1763.8413 | 1744.2447 | 1839.4 | 3386014.1281 | 627928.0805 | 284835.1543 | 0 | 280125.6937
6923 | 1620.4415 | 1683.3218 | 1683.3218 | 1638.6474 | 1620.4415 | 1787.9 | 3056925.7573 | 583358.9443 | 264618.0989 | 0 | 343695.5361
6924 | 1876.2766 | 2562.2576 | 1949.0844 | 2494.2567 | 1876.2766 | 1705.45 | 3377890.0395 | 675459.5659 | 306395.9642 | 0 | 552657.2643
6925 | 1620.8484 | 3409.1899 | 1683.7446 | 3318.7119 | 1620.8484 | 1498.8 | 2561251.7391 | 583505.4359 | 264684.5491 | 0 | 812369.2346
6926 | 1712.8476 | 2473.6424 | 1779.3136 | 2407.9933 | 1712.8476 | 1673.25 | 3030608.0573 | 616625.145 | 279708.0172 | 0 | 559672.9615
6927 | 1534.4519 | 2169.8761 | 1593.996 | 2112.2888 | 1534.4519 | 1879.8 | 3045168.9717 | 552402.697 | 250576.0011 | 0 | 184441.1227
6928 | 1664.7066 | 300.7506 | 300.7506 | 292.7688 | 292.7688 | 1892.75 | 584327.3919 | 105396.7819 | 47809.1514 | 2514761.9037 | 30735.276
6929 | 1575.5306 | 68.2058 | 68.2058 | 66.3957 | 66.3957 | 1899.95 | 133029.6762 | 23902.4507 | 10842.4172 | 2766244.2785 | 6502.4496
6930 | 1789.0993 | 0 | 0 | 0 | 0 | 1908.65 | 0 | 0 | 0 | 3279418.9289 | 0
6931 | 1655.2046 | 0 | 0 | 0 | 0 | 1910.95 | 0 | 0 | 0 | 5624385.3633 | 0
6932 | 1494.8291 | 0 | 0 | 0 | 0 | 1863.8 | 0 | 0 | 0 | 5079429.1459 | 0
6933 | 1709.264 | 0 | 0 | 0 | 0 | 1847.45 | 0 | 0 | 0 | 5808079.0652 | 0
6934 | 1697.6099 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1839.7 | 599423.3117 | 111351.8261 | 50510.4255 | 4717441.0114 | 49031.6022
6935 | 1894.9522 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1821.7 | 1148646.8665 | 215514.4963 | 97759.7701 | 4404830.2697 | 105553.6
6936 | 1490.1674 | 0 | 0 | 0 | 0 | 1775.7 | 0 | 0 | 0 | 2731476.901 | 0
6937 | 1436.5587 | 0 | 0 | 0 | 0 | 1597.1 | 0 | 0 | 0 | 1709504.8482 | 0
6938 | 1714.7026 | 0 | 0 | 0 | 0 | 1674.1 | 0 | 0 | 0 | 2040496.0524 | 0
6939 | 1420.243 | 0 | 0 | 0 | 0 | 1580.45 | 0 | 0 | 0 | 1690089.1641 | 0
6940 | 1859.99 | 0 | 0 | 0 | 0 | 1501.3 | 0 | 0 | 0 | 2213388.106 | 0
6941 | 1577.9614 | 0 | 0 | 0 | 0 | 1524.4 | 0 | 0 | 0 | 1877774.1195 | 0
6942 | 1522.7988 | 0 | 0 | 0 | 0 | 1675.55 | 0 | 0 | 0 | 1812130.6136 | 0
6943 | 1380.6823 | 380.4768 | 380.4768 | 370.3791 | 370.3791 | 1788.5 | 698798.8775 | 133336.4889 | 60482.9129 | 1851885.652 | 76678.2675
6944 | 1445.3682 | 1244.2824 | 1244.2824 | 1211.2598 | 1211.2598 | 1816.7 | 2317682.6736 | 436053.5382 | 197798.73 | 429120.6524 | 217327.2621
6945 | 1443.6317 | 1610.3478 | 1499.6518 | 1567.6101 | 1443.6317 | 1769.4 | 2697520.6369 | 519707.4289 | 235745.0643 | 0 | 332901.4809
6946 | 1751.3527 | 2696.4307 | 1819.3138 | 2624.8689 | 1751.3527 | 1524.75 | 2825522.2896 | 630486.9655 | 285995.893 | 0 | 832330.3621
6947 | 1975.004 | 2802.2132 | 2051.6435 | 2727.844 | 1975.004 | 1477.9 | 3090227.2964 | 711001.4576 | 322518.1612 | 0 | 1031149.614
6948 | 1647.8616 | 3562.4521 | 1711.8069 | 3467.9065 | 1647.8616 | 1492.65 | 2601632.2802 | 593230.1767 | 269095.7996 | 0 | 836042.5838
6949 | 1546.6392 | 3251.2033 | 1606.6559 | 3164.9182 | 1546.6392 | 1464.8 | 2396418.451 | 556790.1059 | 252566.1786 | 0 | 827761.2907
6950 | 1415.4066 | 2960.2996 | 1470.3305 | 2881.7348 | 1415.4066 | 1531.1 | 2294686.7557 | 509546.3598 | 231135.8904 | 0 | 663684.1336
6951 | 1594.654 | 2409.009 | 1656.5341 | 2345.0752 | 1594.654 | 1858.8 | 3137632.1969 | 574075.4263 | 260406.992 | 0 | 225165.1394
6952 | 1899.5274 | 817.4157 | 817.4157 | 795.722 | 795.722 | 1892.25 | 1590932.8301 | 286459.9026 | 129941.3947 | 2023275.4199 | 83925.2897
6953 | 1653.7527 | 226.8615 | 226.8615 | 220.8407 | 220.8407 | 1899.95 | 442899.6039 | 79502.6424 | 36063.2819 | 2626527.8109 | 21627.7084
6954 | 1424.522 | 0 | 0 | 0 | 0 | 1908.65 | 0 | 0 | 0 | 2611148.793 | 0
6955 | 1615.5546 | 0 | 0 | 0 | 0 | 1910.95 | 0 | 0 | 0 | 5489654.4289 | 0
6956 | 1257.086 | 0 | 0 | 0 | 0 | 1863.8 | 0 | 0 | 0 | 4271578.1498 | 0
6957 | 1328.5643 | 0 | 0 | 0 | 0 | 1847.45 | 0 | 0 | 0 | 4514461.454 | 0
6958 | 1113.3524 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1839.7 | 597789.4143 | 111351.8261 | 50510.4255 | 2732133.9856 | 49031.6022
6959 | 1417.1352 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1776.7 | 1119522.4889 | 215514.4963 | 97759.7701 | 2781208.1683 | 132193.6
6960 | 1232.224 | 0 | 0 | 0 | 0 | 1624.05 | 0 | 0 | 0 | 2258666.5095 | 0
6961 | 896.5867 | 0 | 0 | 0 | 0 | 1581.6 | 0 | 0 | 0 | 1066938.1264 | 0
6962 | 1312.2486 | 0 | 0 | 0 | 0 | 1479.1 | 0 | 0 | 0 | 1561575.8197 | 0
6963 | 996.8117 | 0 | 0 | 0 | 0 | 1439.8 | 0 | 0 | 0 | 1186205.9065 | 0
6964 | 1216.6852 | 0 | 0 | 0 | 0 | 1414.65 | 0 | 0 | 0 | 1447855.3773 | 0
6965 | 1229.1162 | 0 | 0 | 0 | 0 | 1445.2 | 0 | 0 | 0 | 1462648.2804 | 0
6966 | 891.925 | 0 | 0 | 0 | 0 | 1472.05 | 0 | 0 | 0 | 1061390.7877 | 0
6967 | 1020.5365 | 225.7021 | 225.7021 | 219.7121 | 219.7121 | 1503.5 | 348473.0952 | 79096.3684 | 35878.9916 | 1467910.9977 | 106779.276
6968 | 782.7914 | 813.167 | 813.167 | 791.586 | 782.7914 | 1511.7 | 1247849.8238 | 281804.918 | 127829.842 | 0 | 382236.8453
6969 | 1064.2324 | 976.3726 | 976.3726 | 950.4602 | 950.4602 | 1558.9 | 1564026.4408 | 342165.6673 | 155210.1485 | 208544.5381 | 407228.3721
6970 | 1233.7118 | 1362.3498 | 1281.5859 | 1326.1938 | 1233.7118 | 1537.4 | 2004332.128 | 444136.2451 | 201465.1356 | 0 | 570715.075
6971 | 1280.4233 | 1868.8316 | 1330.1105 | 1819.2338 | 1280.4233 | 1519.75 | 2057348.0427 | 460952.3725 | 209093.1179 | 0 | 614923.2692
6972 | 1104.2739 | 2264.1217 | 1147.1251 | 2204.0331 | 1104.2739 | 1505.5 | 1758413.2553 | 397538.6008 | 180327.9264 | 0 | 546063.4391
6973 | 1300.3109 | 2903.1829 | 1350.7692 | 2826.1341 | 1300.3109 | 1487.65 | 2043596.5557 | 468111.9355 | 212340.7752 | 0 | 666214.306
6974 | 1092.2168 | 1599.1755 | 1134.6002 | 1556.7343 | 1092.2168 | 1654.75 | 1911992.9986 | 393198.0412 | 178359.0003 | 0 | 377087.8436
6975 | 1134.3734 | 1835.0901 | 1178.3921 | 1786.3878 | 1134.3734 | 1810.8 | 2171051.413 | 408374.4409 | 185243.1839 | 0 | 214623.4562
6976 | 1436.7588 | 933.8855 | 933.8855 | 909.1007 | 909.1007 | 1832.75 | 1757657.2387 | 327276.2367 | 148456.1374 | 967197.2982 | 148830.7575
6977 | 1263.9143 | 445.4717 | 445.4717 | 433.6491 | 433.6491 | 1898.3 | 867838.5195 | 156113.6773 | 70814.8986 | 1521876.0905 | 43169.2092
6978 | 1435.7711 | 0 | 0 | 0 | 0 | 1907.5 | 0 | 0 | 0 | 2631768.3805 | 0
6979 | 1114.3042 | 0 | 0 | 0 | 0 | 1910.95 | 0 | 0 | 0 | 3786405.5425 | 0
6980 | 986.7115 | 0 | 0 | 0 | 0 | 1817.8 | 0 | 0 | 0 | 3352845.642 | 0
6981 | 1394.604 | 0 | 0 | 0 | 0 | 1787.45 | 0 | 0 | 0 | 4738864.5109 | 0
6982 | 1505.7062 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1789.7 | 583010.08 | 111351.8261 | 50510.4255 | 4065352.1369 | 64325.3022
6983 | 1400.0426 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1717.6 | 1084087.572 | 215514.4963 | 97759.7701 | 2723127.3775 | 167180.8
6984 | 1386.8347 | 0 | 0 | 0 | 0 | 1624.05 | 0 | 0 | 0 | 2542067.9189 | 0
6985 | 1262.5245 | 0 | 0 | 0 | 0 | 1587.1 | 0 | 0 | 0 | 2314207.4892 | 0
6986 | 1246.9858 | 0 | 0 | 0 | 0 | 1479.1 | 0 | 0 | 0 | 2285724.9347 | 0
6987 | 1582.6231 | 0 | 0 | 0 | 0 | 1465.45 | 0 | 0 | 0 | 2900948.0946 | 0
6988 | 1398.4887 | 0 | 0 | 0 | 0 | 1463.95 | 0 | 0 | 0 | 2563429.8348 | 0
6989 | 1537.5607 | 0 | 0 | 0 | 0 | 1467.2 | 0 | 0 | 0 | 2818348.6898 | 0
6990 | 1553.8764 | 0 | 0 | 0 | 0 | 1480.55 | 0 | 0 | 0 | 2848255.3715 | 0
6991 | 1107.5098 | 422.2419 | 422.2419 | 411.0359 | 411.0359 | 1584.65 | 685607.5128 | 147972.9084 | 67122.1554 | 1276636.8077 | 167112.3343
6992 | 198.9214 | 614.6192 | 206.6401 | 598.3076 | 198.9214 | 1507.7 | 315612.343 | 71611.7129 | 32483.8687 | 0 | 97929.0174
6993 | 298.2132 | 2044.4592 | 309.7851 | 1990.2003 | 298.2132 | 1544.4 | 485402.9492 | 107356.7351 | 48698.2079 | 0 | 135865.9126
6994 | 304.1927 | 2145.6107 | 315.9961 | 2088.6674 | 304.1927 | 1507.6 | 484344.2961 | 109509.3589 | 49674.662 | 0 | 149784.4676
6995 | 345.2975 | 2187.8308 | 358.6962 | 2129.767 | 345.2975 | 1513.6 | 552570.5349 | 124307.1177 | 56387.0898 | 0 | 167952.728
6996 | 302.5368 | 3148.5247 | 314.2769 | 3064.9646 | 302.5368 | 1505.5 | 482350.302 | 108913.2531 | 49404.2617 | 0 | 149604.4546
6997 | 291.076 | 1390.624 | 302.3711 | 1353.7176 | 291.076 | 1328.65 | 409396.3918 | 104787.3617 | 47532.7116 | 0 | 195413.8758
6998 | 306.2603 | 2361.9272 | 318.1443 | 2299.243 | 306.2603 | 1417.8 | 458633.0857 | 110253.7045 | 50012.3054 | 0 | 178304.7411
6999 | 275.21 | 2489.8706 | 285.8895 | 2423.7908 | 275.21 | 1673.3 | 486250.1248 | 99075.5842 | 44941.7858 | 0 | 89911.0926
7000 | 224.034 | 1771.3023 | 232.7276 | 1724.2929 | 224.034 | 1782.75 | 421135.7783 | 80652.2433 | 36584.7537 | 0 | 48671.3885
7001 | 243.4565 | 266.6799 | 252.9032 | 259.6023 | 243.4565 | 1812.45 | 465025.1763 | 87644.3373 | 39756.4452 | 0 | 45660.2652
7002 | 289.9125 | 0 | 0 | 0 | 0 | 1907.15 | 0 | 0 | 0 | 531409.6856 | 0
7003 | 248.7805 | 0 | 0 | 0 | 0 | 1910.95 | 0 | 0 | 0 | 456014.5857 | 0
7004 | 309.2214 | 0 | 0 | 0 | 0 | 1862.3 | 0 | 0 | 0 | 566802.8189 | 0
7005 | 289.7979 | 215.2154 | 215.2154 | 209.5037 | 209.5037 | 1841.45 | 406330.1593 | 75421.3366 | 34211.9563 | 147179.3212 | 32847.7548
7006 | 230.7506 | 239.7052 | 239.7052 | 233.3436 | 230.7506 | 1837.7 | 446562.2906 | 83070.2303 | 37681.5795 | 0 | 37450.8288
7007 | 296.7904 | 308.3069 | 308.3069 | 300.1246 | 296.7904 | 1730.1 | 541146.4309 | 106844.5386 | 48465.8699 | 0 | 80103.621
7008 | 163.157 | 169.4883 | 169.4883 | 164.9901 | 163.157 | 1696.7 | 292333.3883 | 58736.5265 | 26643.541 | 0 | 49485.5181
7009 | 222.2043 | 0 | 0 | 0 | 0 | 1681.2 | 0 | 0 | 0 | 264423.1404 | 0
7010 | 219.8735 | 0 | 0 | 0 | 0 | 1580.85 | 0 | 0 | 0 | 261649.4712 | 0
7011 | 215.2119 | 0 | 0 | 0 | 0 | 1446 | 0 | 0 | 0 | 256102.1326 | 0
7012 | 131.3026 | 0 | 0 | 0 | 0 | 1444.8 | 0 | 0 | 0 | 156250.0376 | 0
7013 | 144.5105 | 0 | 0 | 0 | 0 | 1451.35 | 0 | 0 | 0 | 171967.4969 | 0
7014 | 197.3423 | 0 | 0 | 0 | 0 | 1450.5 | 0 | 0 | 0 | 234837.3345 | 0
7015 | 135.9137 | 141.1881 | 141.1881 | 137.4411 | 135.9137 | 1494.1 | 214176.8608 | 48928.9251 | 22194.7041 | 0 | 68758.7311
7016 | 163.4921 | 445.6327 | 169.8363 | 433.8058 | 163.4921 | 1352.15 | 232459.5241 | 58857.1461 | 26698.2555 | 0 | 105918.3392
7017 | 970.3841 | 1492.591 | 1008.0395 | 1452.9785 | 970.3841 | 1515.75 | 1551476.874 | 349338.2882 | 158463.7291 | 0 | 469908.5168
7018 | 1153.9649 | 2171.1185 | 1198.7443 | 2113.4982 | 1153.9649 | 1557.35 | 1897077.8254 | 415427.369 | 188442.4705 | 0 | 510802.5692
7019 | 1330.2706 | 3321.2312 | 1381.8908 | 3233.0876 | 1330.2706 | 1483.95 | 2083468.234 | 478897.4304 | 217233.1955 | 0 | 686486.1638
7020 | 1342.4171 | 3598.805 | 1394.5092 | 3503.2947 | 1342.4171 | 1494.55 | 2118185.3981 | 483270.1549 | 219216.7119 | 0 | 678524.7217
7021 | 1361.5307 | 2721.6051 | 1414.3649 | 2649.3752 | 1361.5307 | 1468.65 | 2109554.919 | 490151.0693 | 222337.9711 | 0 | 723449.3629
7022 | 1355.7183 | 1170.6291 | 1170.6291 | 1139.5612 | 1139.5612 | 1496.7 | 1802168.1276 | 410242.0369 | 186090.3462 | 396215.901 | 561409.0048
7023 | 1394.876 | 873.2432 | 873.2432 | 850.0678 | 850.0678 | 1536.5 | 1378656.3074 | 306024.3959 | 138816.0663 | 998633.4243 | 385671.861
7024 | 1538.6163 | 473.0436 | 473.0436 | 460.4893 | 460.4893 | 1639.95 | 796360.1305 | 165776.1532 | 75197.9051 | 1976206.8103 | 162291.8174
7025 | 1416.4175 | 147.797 | 147.797 | 143.8745 | 143.8745 | 1845.5 | 279931.5086 | 51794.8319 | 23494.7112 | 2332571.341 | 21758.3895
7026 | 1352.2386 | 0 | 0 | 0 | 0 | 1849.8 | 0 | 0 | 0 | 2478653.2933 | 0
7027 | 1554.2017 | 0 | 0 | 0 | 0 | 1881.55 | 0 | 0 | 0 | 5281177.3936 | 0
7028 | 1215.1313 | 0 | 0 | 0 | 0 | 1810.9 | 0 | 0 | 0 | 4129016.2084 | 0
7029 | 895.0328 | 0 | 0 | 0 | 0 | 1782.95 | 0 | 0 | 0 | 3041321.4014 | 0
7030 | 1180.946 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1823.2 | 594829.5685 | 111351.8261 | 50510.4255 | 2961817.1132 | 54078.5232
7031 | 1267.9631 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1738.35 | 1099190.0663 | 215514.4963 | 97759.7701 | 2274321.2671 | 154896.8
7032 | 849.9704 | 0 | 0 | 0 | 0 | 1712.3 | 0 | 0 | 0 | 1557995.688 | 0
7033 | 1104.8061 | 0 | 0 | 0 | 0 | 1573.7 | 0 | 0 | 0 | 1314719.2507 | 0
7034 | 738.0913 | 0 | 0 | 0 | 0 | 1670.3 | 0 | 0 | 0 | 878328.6136 | 0
7035 | 1162.2995 | 0 | 0 | 0 | 0 | 1660.7 | 0 | 0 | 0 | 1383136.4276 | 0
7036 | 1122.6757 | 0 | 0 | 0 | 0 | 1658.85 | 0 | 0 | 0 | 1335984.0485 | 0
7037 | 1184.8307 | 0 | 0 | 0 | 0 | 1583.75 | 0 | 0 | 0 | 1409948.5639 | 0
7038 | 1024.0045 | 0 | 0 | 0 | 0 | 1657.45 | 0 | 0 | 0 | 1218565.3812 | 0
7039 | 1256.0216 | 213.5253 | 213.5253 | 207.8584 | 207.8584 | 1496.5 | 328202.963 | 74829.0358 | 33943.2821 | 1921283.0324 | 102442.6135
7040 | 1353.606 | 1183.6224 | 1183.6224 | 1152.2097 | 1152.2097 | 1492.45 | 1810087.6582 | 414795.5087 | 188155.8516 | 369159.2926 | 572433.1618
7041 | 1534.3568 | 939.6934 | 939.6934 | 914.7545 | 914.7545 | 1490.6 | 1440952.5981 | 329311.6109 | 149379.4057 | 1135730.9905 | 456118.7976
7042 | 1602.1427 | 1664.3127 | 1664.3127 | 1620.1428 | 1602.1427 | 1462.7 | 2480780.8268 | 576771.363 | 261629.8988 | 0 | 860831.2593
7043 | 1628.6013 | 2826.6449 | 1691.7995 | 2751.6272 | 1628.6013 | 1445.5 | 2497080.9304 | 586296.4698 | 265950.5931 | 0 | 903059.4236
7044 | 1636.1784 | 3701.1522 | 1699.6695 | 3602.9257 | 1636.1784 | 1433.9 | 2485602.044 | 589024.2218 | 267187.9317 | 0 | 926240.5888
7045 | 1876.1804 | 3776.7752 | 1948.9857 | 3676.5416 | 1876.1804 | 1421.7 | 2830856.6233 | 675424.9534 | 306380.2636 | 0 | 1084995.1404
7046 | 1679.1101 | 3363.469 | 1744.2674 | 3274.2044 | 1679.1101 | 1423.35 | 2530335.7466 | 604479.6202 | 274198.6721 | 0 | 968258.8138
7047 | 1605.5447 | 2243.3518 | 1667.8478 | 2183.8145 | 1605.5447 | 1341.7 | 2277020.8717 | 577996.0895 | 262185.4484 | 0 | 1056930.0714
7048 | 1427.7269 | 1146.8664 | 1146.8664 | 1116.4292 | 1116.4292 | 1324 | 1560456.3657 | 401914.513 | 182312.8888 | 570608.5908 | 738741.588
7049 | 1587.1934 | 706.1847 | 706.1847 | 687.4429 | 687.4429 | 1370.3 | 995846.6391 | 247479.4462 | 112259.4265 | 1649242.6794 | 423725.7597
7050 | 1493.7656 | 0 | 0 | 0 | 0 | 1733.65 | 0 | 0 | 0 | 2738072.3925 | 0
7051 | 1428.0124 | 0 | 0 | 0 | 0 | 1752.85 | 0 | 0 | 0 | 4852386.0536 | 0
7052 | 1214.3544 | 0 | 0 | 0 | 0 | 1707.4 | 0 | 0 | 0 | 4126376.173 | 0
7053 | 1286.6096 | 0 | 0 | 0 | 0 | 1477.05 | 0 | 0 | 0 | 4371899.5159 | 0
7054 | 1485.5058 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1486.35 | 486219.1331 | 111351.8261 | 50510.4255 | 3996711.2015 | 157112.1801
7055 | 1588.0616 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1446.7 | 915999.4094 | 215514.4963 | 97759.7701 | 3362016.0755 | 327553.6
7056 | 1464.5285 | 0 | 0 | 0 | 0 | 1494.25 | 0 | 0 | 0 | 2684480.6873 | 0
7057 | 943.9799 | 0 | 0 | 0 | 0 | 1582.1 | 0 | 0 | 0 | 1123336.0689 | 0
7058 | 1055.082 | 0 | 0 | 0 | 0 | 1584.1 | 0 | 0 | 0 | 1255547.6395 | 0
7059 | 1517.3603 | 0 | 0 | 0 | 0 | 1480.45 | 0 | 0 | 0 | 1805658.7177 | 0
7060 | 1184.8307 | 0 | 0 | 0 | 0 | 1473.45 | 0 | 0 | 0 | 1409948.5639 | 0
7061 | 1555.4302 | 0 | 0 | 0 | 0 | 1479.7 | 0 | 0 | 0 | 1850961.9832 | 0
7062 | 1419.4661 | 0 | 0 | 0 | 0 | 1580.55 | 0 | 0 | 0 | 1689164.6066 | 0
7063 | 1509.6793 | 480.8793 | 480.8793 | 468.1171 | 468.1171 | 1688.5 | 837764.3894 | 168522.1428 | 76443.5164 | 1909183.5101 | 142733.9725
7064 | 1222.5996 | 1270.0427 | 1270.0427 | 1236.3364 | 1222.5996 | 1610.2 | 2083243.4075 | 440135.8679 | 199650.5201 | 0 | 476569.3369
7065 | 1098.0623 | 1461.055 | 1140.6731 | 1422.2794 | 1098.0623 | 1654.4 | 1924406.2063 | 395302.4172 | 179313.5687 | 0 | 379490.3205
7066 | 1450.0124 | 2446.7841 | 1506.2804 | 2381.8478 | 1450.0124 | 1671.9 | 2566052.1965 | 522004.4467 | 236787.0171 | 0 | 475749.0527
7067 | 1367.1296 | 2755.8119 | 1420.1811 | 2682.6741 | 1367.1296 | 1562.9 | 2268246.819 | 492166.6409 | 223252.2568 | 0 | 597572.3298
7068 | 1547.1005 | 3124.9335 | 1607.1348 | 3041.9995 | 1547.1005 | 1554.8 | 2557916.7219 | 556956.1764 | 252641.51 | 0 | 688769.1381
7069 | 1876.2222 | 3325.6139 | 1949.0283 | 3237.354 | 1876.2222 | 1531.45 | 3052566.0852 | 675439.987 | 306387.083 | 0 | 879103.9053
7070 | 1289.5668 | 2817.8732 | 1339.6083 | 2743.0884 | 1289.5668 | 1510.1 | 2059092.4219 | 464244.0656 | 210586.2664 | 0 | 631758.7993
7071 | 1309.7799 | 395.0668 | 395.0668 | 384.5819 | 384.5819 | 1422.5 | 577007.8211 | 138449.4976 | 62802.2304 | 1695887.8026 | 217398.1425
7072 | 1430.0072 | 164.0252 | 164.0252 | 159.6721 | 159.6721 | 1569.45 | 264642.5558 | 57481.9391 | 26074.4463 | 2328524.2603 | 67292.3817
7073 | 1378.6088 | 42.108 | 42.108 | 40.9904 | 40.9904 | 1868.95 | 80872.0123 | 14756.5542 | 6693.737 | 2451854.5118 | 5258.1191
7074 | 911.5146 | 0 | 0 | 0 | 0 | 1907.15 | 0 | 0 | 0 | 1670806.1824 | 0
7075 | 1308.9971 | 0 | 0 | 0 | 0 | 1910.95 | 0 | 0 | 0 | 4447972.1492 | 0
7076 | 978.1652 | 0 | 0 | 0 | 0 | 1862.15 | 0 | 0 | 0 | 3323805.2466 | 0
7077 | 1111.0216 | 0 | 0 | 0 | 0 | 1845.45 | 0 | 0 | 0 | 3775251.3934 | 0
7078 | 1313.0255 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1811.2 | 591700.1563 | 111351.8261 | 50510.4255 | 3410623.2236 | 57749.0112
7079 | 1476.9595 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1734.2 | 1097471.101 | 215514.4963 | 97759.7701 | 2984490.9358 | 157353.6
7080 | 1488.6136 | 0 | 0 | 0 | 0 | 1702.6 | 0 | 0 | 0 | 2728628.6463 | 0
7081 | 1055.859 | 0 | 0 | 0 | 0 | 1682.1 | 0 | 0 | 0 | 1256472.1957 | 0
7082 | 1290.4943 | 0 | 0 | 0 | 0 | 1660.25 | 0 | 0 | 0 | 1535688.2384 | 0
7083 | 1036.4355 | 0 | 0 | 0 | 0 | 1670.45 | 0 | 0 | 0 | 1233358.2843 | 0
7084 | 1038.7663 | 0 | 0 | 0 | 0 | 1668.95 | 0 | 0 | 0 | 1236131.9541 | 0
7085 | 936.9874 | 0 | 0 | 0 | 0 | 1669.7 | 0 | 0 | 0 | 1115015.061 | 0
7086 | 1198.0387 | 0 | 0 | 0 | 0 | 1675.55 | 0 | 0 | 0 | 1425666.0233 | 0
7087 | 1205.407 | 496.4032 | 496.4032 | 483.229 | 483.229 | 1708.5 | 873776.4542 | 173962.4277 | 78911.2901 | 1323752.2671 | 137881.5405
7088 | 1106.8931 | 1149.8457 | 1149.8457 | 1119.3294 | 1106.8931 | 1738.7 | 2029867.3977 | 398481.5315 | 180755.6503 | 0 | 289231.1409
7089 | 1442.5236 | 1905.492 | 1498.5008 | 1854.9213 | 1442.5236 | 1858.4 | 2830303.3805 | 519308.51 | 235564.1102 | 0 | 204261.3473
7090 | 1737.0055 | 2793.7532 | 1804.4101 | 2719.6085 | 1737.0055 | 1871.9 | 3431852.0942 | 625321.9969 | 283653.0058 | 0 | 222510.4106
7091 | 1443.4841 | 2886.0084 | 1499.498 | 2809.4153 | 1443.4841 | 1872.4 | 2849112.1786 | 519654.2864 | 235720.9583 | 0 | 184188.5749
7092 | 1588.2695 | 2062.472 | 1649.9014 | 2007.7352 | 1588.2695 | 1769.8 | 2965443.5363 | 571777.0103 | 259364.4049 | 0 | 365619.6327
7093 | 1786.2343 | 3414.3829 | 1855.5484 | 3323.7671 | 1786.2343 | 1539.95 | 2903314.5343 | 643044.3451 | 291692.0599 | 0 | 821757.086
7094 | 1390.1667 | 3387.1901 | 1444.1121 | 3297.2959 | 1390.1667 | 1567.25 | 2301524.5581 | 500460.0289 | 227014.2298 | 0 | 601594.6598
7095 | 1677.3843 | 2465.8243 | 1742.4745 | 2400.3827 | 1677.3843 | 1801.8 | 3183386.7891 | 603858.3415 | 273916.8533 | 0 | 332457.5647
7096 | 1676.6695 | 1630.4487 | 1630.4487 | 1587.1775 | 1587.1775 | 1838.75 | 3073169.7645 | 571383.9003 | 259186.0859 | 164038.8325 | 250518.4837
7097 | 1553.3917 | 508.1542 | 508.1542 | 494.6681 | 494.6681 | 1871.95 | 975617.4144 | 178080.502 | 80779.2944 | 1940640.5164 | 62002.3222
7098 | 1585.9659 | 0 | 0 | 0 | 0 | 1908.15 | 0 | 0 | 0 | 2907075.4049 | 0
7099 | 1572.7909 | 0 | 0 | 0 | 0 | 1910.95 | 0 | 0 | 0 | 5344343.553 | 0
7100 | 1489.3905 | 0 | 0 | 0 | 0 | 1862.8 | 0 | 0 | 0 | 5060948.8952 | 0
7101 | 1698.3869 | 0 | 0 | 0 | 0 | 1845.45 | 0 | 0 | 0 | 5771118.5605 | 0
7102 | 1112.5755 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1838.05 | 598926.7204 | 111351.8261 | 50510.4255 | 2729493.9503 | 49536.2943
7103 | 1168.515 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1762.7 | 1111157.526 | 215514.4963 | 97759.7701 | 1936396.6675 | 140481.6
7104 | 371.3765 | 0 | 0 | 0 | 0 | 1706.7 | 0 | 0 | 0 | 680733.0338 | 0
7105 | 116.5407 | 0 | 0 | 0 | 0 | 1561.1 | 0 | 0 | 0 | 138683.4652 | 0
7106 | 122.7562 | 0 | 0 | 0 | 0 | 1426.1 | 0 | 0 | 0 | 146079.9168 | 0
7107 | 114.9869 | 0 | 0 | 0 | 0 | 1243.85 | 0 | 0 | 0 | 136834.3525 | 0
7108 | 121.2024 | 0 | 0 | 0 | 0 | 1242.35 | 0 | 0 | 0 | 144230.8039 | 0
7109 | 123.5332 | 0 | 0 | 0 | 0 | 1447.55 | 0 | 0 | 0 | 147004.4733 | 0
7110 | 101.7789 | 0 | 0 | 0 | 0 | 1615.3 | 0 | 0 | 0 | 121116.893 | 0
7111 | 87.8474 | 91.2559 | 91.2559 | 88.834 | 87.8474 | 1714.5 | 159393.2876 | 31625.0744 | 14345.4851 | 0 | 25080.441
7112 | 176.3999 | 454.61 | 183.2452 | 442.5449 | 176.3999 | 1712.7 | 318389.5382 | 63503.9745 | 28806.1085 | 0 | 50679.6997
7113 | 1266.3005 | 677.0825 | 677.0825 | 659.1131 | 659.1131 | 1829.4 | 1270542.7641 | 237280.7323 | 107633.1766 | 1112974.3553 | 110066.002
7114 | 1548.0484 | 327.1809 | 327.1809 | 318.4977 | 318.4977 | 1824.4 | 612515.5056 | 114659.1727 | 52010.6747 | 2253766.3453 | 54497.2844
7115 | 1673.0266 | 1241.0642 | 1241.0642 | 1208.127 | 1208.127 | 1777.9 | 2261590.7064 | 434925.7276 | 197287.1425 | 852160.9832 | 263984.2843
7116 | 1771.9988 | 1840.761 | 1840.761 | 1791.9082 | 1771.9988 | 1669.8 | 3121772.9872 | 637919.5835 | 289367.4111 | 0 | 585114.018
7117 | 1494.0026 | 2746.0804 | 1551.9764 | 2673.2009 | 1494.0026 | 1315.35 | 2073232.3027 | 537840.9331 | 243970.6233 | 0 | 1022868.8746
7118 | 1420.6499 | 2356.4984 | 1475.778 | 2293.9583 | 1420.6499 | 1331.65 | 1997064.4191 | 511433.9698 | 231992.1313 | 0 | 949491.3714
7119 | 1712.2377 | 2403.9583 | 1778.681 | 2340.1586 | 1712.2377 | 1562.5 | 2827465.6681 | 616405.5824 | 279608.4211 | 0 | 749104.0064
7120 | 1677.291 | 1114.0028 | 1114.0028 | 1084.4378 | 1084.4378 | 1834.75 | 2100145.9877 | 390397.5931 | 177088.686 | 1086700.0812 | 175412.5445
7121 | 1676.9667 | 12.3784 | 12.3784 | 12.0499 | 12.0499 | 1871.95 | 23784.9184 | 4337.9573 | 1967.7456 | 3051792.4881 | 1510.3498
7122 | 1398.5489 | 0 | 0 | 0 | 0 | 1908.15 | 0 | 0 | 0 | 2563540.2034 | 0
7123 | 1443.0422 | 0 | 0 | 0 | 0 | 1910.95 | 0 | 0 | 0 | 4903457.5519 | 0
7124 | 1379.0653 | 0 | 0 | 0 | 0 | 1862.3 | 0 | 0 | 0 | 4686063.7909 | 0
7125 | 1510.3678 | 0 | 0 | 0 | 0 | 1793.45 | 0 | 0 | 0 | 5132229.866 | 0
7126 | 1776.0807 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1754.7 | 573077.8536 | 111351.8261 | 50510.4255 | 4984084.6437 | 75030.8922
7127 | 1299.0406 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1734.2 | 1097472.5252 | 215514.4963 | 97759.7701 | 2379922.7039 | 157353.6
7128 | 1407.035 | 0 | 0 | 0 | 0 | 1602.1 | 0 | 0 | 0 | 2579095.2393 | 0
7129 | 1057.4129 | 0 | 0 | 0 | 0 | 1717.1 | 0 | 0 | 0 | 1258321.3082 | 0
7130 | 1358.0879 | 0 | 0 | 0 | 0 | 1722.6 | 0 | 0 | 0 | 1616124.6486 | 0
7131 | 1203.4772 | 0 | 0 | 0 | 0 | 1686.35 | 0 | 0 | 0 | 1432137.918 | 0
7132 | 1147.5377 | 0 | 0 | 0 | 0 | 1674.85 | 0 | 0 | 0 | 1365569.8547 | 0
7133 | 1421.0199 | 0 | 0 | 0 | 0 | 1685.6 | 0 | 0 | 0 | 1691013.7203 | 0
7134 | 1152.9763 | 0 | 0 | 0 | 0 | 1675.55 | 0 | 0 | 0 | 1372041.7494 | 0
7135 | 1150.6454 | 112.0174 | 112.0174 | 109.0446 | 109.0446 | 1708.5 | 196419.169 | 39256.0383 | 17806.9752 | 1909254.4408 | 31114.127
7136 | 1557.2327 | 390.6436 | 390.6436 | 380.2761 | 380.2761 | 1722.7 | 688781.8331 | 136899.395 | 62099.0867 | 2157361.5171 | 103219.9336
7137 | 1562.9559 | 123.248 | 123.248 | 119.977 | 119.977 | 1604.1 | 202685.9179 | 43191.7262 | 19592.2469 | 2644980.2116 | 46494.1001
7138 | 1484.153 | 850.3271 | 850.3271 | 827.7599 | 827.7599 | 1421.45 | 1241124.6612 | 297993.5686 | 135173.1937 | 1203168.452 | 468770.1375
7139 | 1538.7348 | 2339.1888 | 1598.4452 | 2277.108 | 1538.7348 | 766.8 | 1248785.3625 | 553944.5309 | 251275.3941 | 0 | 1897567.7652
7140 | 1370.921 | 2444.3585 | 1424.1192 | 2379.4865 | 1370.921 | 360.8 | 523364.8914 | 493531.5661 | 223871.4021 | 0 | 2247213.7311
7141 | 1755.5239 | 711.9033 | 711.9033 | 693.0098 | 693.0098 | 342.95 | 251070.4825 | 249483.5125 | 113168.4933 | 1947588.3653 | 1124061.5245
7142 | 1535.2541 | 1144.3941 | 1144.3941 | 1114.0225 | 1114.0225 | 757.15 | 889508.9376 | 401048.0865 | 181919.8681 | 772117.6372 | 1355275.7253
7143 | 1077.4462 | 223.2298 | 223.2298 | 217.3054 | 217.3054 | 1576 | 361239.0853 | 78229.9419 | 35485.9709 | 1576638.1245 | 90188.616
7144 | 1517.8449 | 317.9844 | 317.9844 | 309.5452 | 309.5452 | 1710.1 | 558749.189 | 111436.2844 | 50548.7368 | 2214813.2538 | 87838.8303
7145 | 1251.0074 | 417.7003 | 417.7003 | 406.6147 | 406.6147 | 1857.95 | 795968.2532 | 146381.3047 | 66400.1863 | 1547771.7671 | 56537.7466
7146 | 1642.0142 | 0 | 0 | 0 | 0 | 1907.65 | 0 | 0 | 0 | 3009811.9754 | 0
7147 | 1603.6198 | 0 | 0 | 0 | 0 | 1910.95 | 0 | 0 | 0 | 5449100.1789 | 0
7148 | 1352.6494 | 0 | 0 | 0 | 0 | 1862.8 | 0 | 0 | 0 | 4596302.5695 | 0
7149 | 1404.7042 | 0 | 0 | 0 | 0 | 1791.45 | 0 | 0 | 0 | 4773184.9769 | 0
7150 | 1233.7778 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1783.7 | 579797.8611 | 111351.8261 | 50510.4255 | 3141339.556 | 66160.5462
7151 | 1466.0823 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1760.2 | 1107032.3894 | 215514.4963 | 97759.7701 | 2947530.431 | 141961.6
7152 | 1573.2998 | 0 | 0 | 0 | 0 | 1721.7 | 0 | 0 | 0 | 2883858.5627 | 0
7153 | 1475.4056 | 0 | 0 | 0 | 0 | 1722.6 | 0 | 0 | 0 | 2704418.4758 | 0
7154 | 1317.6872 | 0 | 0 | 0 | 0 | 1719.1 | 0 | 0 | 0 | 2415320.5551 | 0
7155 | 1793.9503 | 0 | 0 | 0 | 0 | 1692.95 | 0 | 0 | 0 | 3288310.8266 | 0
7156 | 1639.3396 | 0 | 0 | 0 | 0 | 1684.85 | 0 | 0 | 0 | 3004909.4171 | 0
7157 | 1427.2354 | 0 | 0 | 0 | 0 | 1685.6 | 0 | 0 | 0 | 2616122.5579 | 0
7158 | 1366.6343 | 0 | 0 | 0 | 0 | 1695.55 | 0 | 0 | 0 | 2505040.5986 | 0
7159 | 1260.9775 | 295.9721 | 295.9721 | 288.1172 | 288.1172 | 1737 | 524491.2868 | 103722.176 | 47049.5315 | 1783252.9489 | 74171.786
7160 | 331.6128 | 984.0608 | 344.4812 | 957.9443 | 331.6128 | 1747.7 | 606634.5975 | 119380.5916 | 54152.3628 | 0 | 83665.8979
7161 | 268.4554 | 1330.8232 | 278.8734 | 1295.5038 | 268.4554 | 1761.9 | 496658.3871 | 96643.9619 | 43838.7749 | 0 | 63919.2425
7162 | 276.049 | 2123.8592 | 286.761 | 2067.4931 | 276.049 | 1562.1 | 453138.585 | 99377.6577 | 45078.8097 | 0 | 120881.8786
7163 | 261.2493 | 2978.0953 | 271.3867 | 2899.0583 | 261.2493 | 1341.3 | 368807.6823 | 94049.7653 | 42662.0185 | 0 | 172084.9455
7164 | 324.2289 | 3601.5257 | 336.8106 | 3505.9431 | 324.2289 | 847 | 288608.5431 | 116722.4141 | 52946.584 | 0 | 373835.9541
7165 | 205.8624 | 3876.5326 | 213.8515 | 3773.6515 | 205.8624 | 342.95 | 74244.6561 | 74110.4627 | 33617.3293 | 0 | 341124.2838
7166 | 205.1622 | 2608.6184 | 213.1243 | 2539.3871 | 205.1622 | 1225.65 | 264415.4096 | 73858.3851 | 33502.9841 | 0 | 158867.3346
7167 | 333.7513 | 2578.8764 | 346.7021 | 2510.4344 | 333.7513 | 1500.65 | 527663.2692 | 120150.4596 | 54501.5835 | 0 | 166658.7
7168 | 381.8331 | 1322.9085 | 396.6499 | 1287.7992 | 381.8331 | 1720.1 | 691130.4572 | 137459.9042 | 62353.3399 | 0 | 106875.0755
7169 | 308.0162 | 687.8394 | 319.9685 | 669.5845 | 308.0162 | 1898.35 | 613581.5753 | 110885.8214 | 50299.0407 | 0 | 31309.8437
7170 | 338.7742 | 0 | 0 | 0 | 0 | 1908.65 | 0 | 0 | 0 | 620973.0758 | 0
7171 | 273.5706 | 0 | 0 | 0 | 0 | 1910.95 | 0 | 0 | 0 | 501454.9399 | 0
7172 | 258.7204 | 0 | 0 | 0 | 0 | 1863.3 | 0 | 0 | 0 | 474234.5192 | 0
7173 | 300.6751 | 252.3413 | 252.3413 | 245.6443 | 245.6443 | 1845.45 | 475235.1625 | 88431.9322 | 40113.707 | 100871.4929 | 37542.5133
7174 | 283.5824 | 294.5863 | 294.5863 | 286.7682 | 283.5824 | 1838.05 | 546101.4547 | 102089.677 | 46309.0118 | 0 | 45926.1049
7175 | 236.1892 | 245.3543 | 245.3543 | 238.8427 | 236.1892 | 1789.7 | 443529.621 | 85028.1145 | 38569.6975 | 0 | 49670.5467
7176 | 135.1872 | 140.4329 | 140.4329 | 136.7059 | 135.1872 | 1734.2 | 246047.1512 | 48667.4077 | 22076.0769 | 0 | 35932.7046
7177 | 138.295 | 0 | 0 | 0 | 0 | 1759.2 | 0 | 0 | 0 | 164571.0455 | 0
7178 | 120.4254 | 0 | 0 | 0 | 0 | 1760.85 | 0 | 0 | 0 | 143306.2474 | 0
7179 | 114.9869 | 0 | 0 | 0 | 0 | 1736.15 | 0 | 0 | 0 | 136834.3525 | 0
7180 | 111.8791 | 0 | 0 | 0 | 0 | 1730.95 | 0 | 0 | 0 | 133136.1266 | 0
7181 | 98.6711 | 0 | 0 | 0 | 0 | 1731.35 | 0 | 0 | 0 | 117418.6673 | 0
7182 | 96.3403 | 0 | 0 | 0 | 0 | 1736.15 | 0 | 0 | 0 | 114644.998 | 0
7183 | 79.4371 | 82.5195 | 82.5195 | 80.3295 | 79.4371 | 1787.1 | 149305.4902 | 28597.3463 | 12972.074 | 0 | 16912.1529
7184 | 86.9093 | 1099.7556 | 90.2815 | 1070.5687 | 86.9093 | 1769.45 | 161249.5098 | 31287.3394 | 14192.2848 | 0 | 20036.9336
7185 | 86.5519 | 2910.2323 | 89.9106 | 2832.9963 | 86.5519 | 1844.9 | 167609.2261 | 31158.6784 | 14133.9227 | 0 | 13424.1973
7186 | 85.5428 | 3643.1776 | 88.8625 | 3546.4896 | 85.5428 | 1827.35 | 164084.1551 | 30795.421 | 13969.1451 | 0 | 14768.9706
7187 | 82.0117 | 2326.7741 | 85.1934 | 2265.0228 | 82.0117 | 1777.6 | 153056.8875 | 29524.1947 | 13392.5028 | 0 | 18239.3914
7188 | 89.4741 | 2441.8259 | 92.946 | 2377.0211 | 89.4741 | 1603.55 | 150813.6484 | 32210.6916 | 14611.1276 | 0 | 35472.0241
7189 | 85.7196 | 2838.9391 | 89.0463 | 2763.5952 | 85.7196 | 1482.15 | 133871.8961 | 30859.0522 | 13998.009 | 0 | 44389.8894
7190 | 90.0355 | 3244.4386 | 93.5298 | 3158.333 | 90.0355 | 1523.85 | 144491.8325 | 32412.7732 | 14702.7941 | 0 | 42870.3943
7191 | 84.2988 | 490.1403 | 87.5702 | 477.1322 | 84.2988 | 1618.35 | 143687.383 | 30347.555 | 13765.9881 | 0 | 32172.6232
7192 | 95.4148 | 1054.1998 | 99.1176 | 1026.2219 | 95.4148 | 1797.1 | 180282.8357 | 34349.3305 | 15581.238 | 0 | 19359.6643
7193 | 85.638 | 107.4103 | 88.9612 | 104.5597 | 85.638 | 1880 | 169202.82 | 30829.684 | 13984.6872 | 0 | 10276.5613
7194 | 92.1604 | 95.7362 | 95.7362 | 93.1955 | 92.1604 | 1880.8 | 182108.6569 | 33177.7465 | 15049.7945 | 0 | 10985.472
7195 | 99.1266 | 102.9736 | 102.9736 | 100.2407 | 99.1266 | 1882.05 | 196148.1948 | 35685.5864 | 16187.3785 | 0 | 11691.9859
7196 | 101.7789 | 105.7285 | 105.7285 | 102.9225 | 101.7789 | 1841.9 | 197102.6921 | 36640.4046 | 16620.4946 | 0 | 16091.2444
7197 | 100.225 | 104.1142 | 104.1142 | 101.3511 | 100.225 | 1829.45 | 192875.1109 | 36081.0091 | 16366.7466 | 0 | 17093.3737
7198 | 107.9944 | 112.1847 | 112.1847 | 109.2074 | 107.9944 | 1824.2 | 207598.407 | 38877.9866 | 17635.4867 | 0 | 18985.3452
7199 | 98.6711 | 102.4999 | 102.4999 | 99.7796 | 98.6711 | 1804.85 | 188174.916 | 35521.6136 | 16112.9986 | 0 | 19255.6456
7200 | 104.1097 | 108.15 | 108.15 | 105.2797 | 104.1097 | 1747.3 | 192394.3328 | 37479.4978 | 17001.1167 | 0 | 26308.5253
7201 | 94.0095 | 0 | 0 | 0 | 0 | 1499.5 | 0 | 0 | 0 | 111871.3287 | 0
7202 | 100.225 | 0 | 0 | 0 | 0 | 1724.4 | 0 | 0 | 0 | 119267.7801 | 0
7203 | 97.1173 | 0 | 0 | 0 | 0 | 1711.2 | 0 | 0 | 0 | 115569.5544 | 0
7204 | 98.6711 | 1.9779 | 1.9779 | 1.9254 | 1.9254 | 1645 | 3349.8249 | 693.1412 | 314.4166 | 115127.4505 | 675.92
7205 | 93.2326 | 96.8509 | 96.8509 | 94.2805 | 93.2326 | 1495.2 | 147606.3575 | 33563.7294 | 15224.8806 | 0 | 47063.8072
7206 | 98.6711 | 102.4999 | 102.4999 | 99.7796 | 98.6711 | 1494.8 | 156359.456 | 35521.6136 | 16112.9986 | 0 | 49848.5892
7207 | 88.0252 | 91.4408 | 91.4408 | 89.014 | 88.0252 | 1231.9 | 114777.3587 | 31689.0553 | 14374.5076 | 0 | 67612.0025
7208 | 138.2668 | 934.7435 | 143.6314 | 909.9359 | 138.2668 | 1239.35 | 180258.6724 | 49776.0596 | 22578.9737 | 0 | 105172.6659
7209 | 851.5291 | 2392.5637 | 884.5713 | 2329.0663 | 851.5291 | 1183.15 | 1055665.937 | 306550.4768 | 139054.7024 | 0 | 695571.5471
7210 | 1151.9371 | 3501.9157 | 1196.6376 | 3408.9768 | 1151.9371 | 1270.4 | 1528725.956 | 414697.3582 | 188111.3294 | 0 | 840453.3125
7211 | 1368.5727 | 3948.4522 | 1421.6791 | 3843.6624 | 1368.5727 | 1372.15 | 1964839.8938 | 492686.1796 | 223487.9253 | 0 | 859258.3829
7212 | 1597.6423 | 3344.8993 | 1659.6381 | 3256.1275 | 1597.6423 | 1440.25 | 2405876.3546 | 575151.214 | 260894.9812 | 0 | 894280.2556
7213 | 1506.7813 | 2946.3307 | 1565.2513 | 2868.1367 | 1506.7813 | 1341.9 | 2109319.9293 | 542441.2619 | 246057.3835 | 0 | 991612.7623
7214 | 1412.897 | 2631.014 | 1467.7241 | 2561.1883 | 1412.897 | 1129.2 | 1665418.3961 | 508642.9358 | 230726.0873 | 0 | 1230350.7459
7215 | 1414.7093 | 1765.323 | 1469.6064 | 1718.4723 | 1414.7093 | 1261.9 | 1867635.3807 | 509295.3307 | 231022.0209 | 0 | 1044196.8989
7216 | 1584.3586 | 1004.5346 | 1004.5346 | 977.8748 | 977.8748 | 1226.25 | 1256954.5482 | 352034.9206 | 159686.9515 | 1111684.7695 | 740624.9888
7217 | 1584.5198 | 351.9419 | 351.9419 | 342.6015 | 342.6015 | 1371.45 | 493029.35 | 123336.5435 | 55946.8265 | 2276436.1802 | 210787.3852
7218 | 1715.024 | 0 | 0 | 0 | 0 | 1759.65 | 0 | 0 | 0 | 3143639.0342 | 0
7219 | 1680.964 | 0 | 0 | 0 | 0 | 1799.05 | 0 | 0 | 0 | 5711915.757 | 0
7220 | 1793.1733 | 0 | 0 | 0 | 0 | 1729.9 | 0 | 0 | 0 | 6093202.9482 | 0
7221 | 1675.8557 | 0 | 0 | 0 | 0 | 1548.9 | 0 | 0 | 0 | 5694557.5191 | 0
7222 | 1509.5909 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1438.2 | 469575.9426 | 111351.8261 | 50510.4255 | 4078552.3135 | 171840.0132
7223 | 1940.7916 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1446.2 | 914216.164 | 215514.4963 | 97759.7701 | 4560592.3912 | 327849.6
7224 | 1651.7706 | 0 | 0 | 0 | 0 | 1307.45 | 0 | 0 | 0 | 3027695.4603 | 0
7225 | 1884.852 | 0 | 0 | 0 | 0 | 1368.8 | 0 | 0 | 0 | 2242973.9121 | 0
7226 | 1574.8537 | 0 | 0 | 0 | 0 | 1312.8 | 0 | 0 | 0 | 1874075.8947 | 0
7227 | 1236.1086 | 0 | 0 | 0 | 0 | 1243.85 | 0 | 0 | 0 | 1470969.2887 | 0
7228 | 1240.7703 | 0 | 0 | 0 | 0 | 1154.05 | 0 | 0 | 0 | 1476516.6272 | 0
7229 | 1692.1714 | 0 | 0 | 0 | 0 | 1066.5 | 0 | 0 | 0 | 2013683.916 | 0
7230 | 1647.1089 | 0 | 0 | 0 | 0 | 1248.95 | 0 | 0 | 0 | 1960059.6434 | 0
7231 | 1061.519 | 530.0896 | 530.0896 | 516.0213 | 516.0213 | 1261.9 | 685175.2774 | 185767.6711 | 84266.2797 | 999897.2356 | 372818.7386
7232 | 1120.1186 | 1163.5839 | 1163.5839 | 1132.703 | 1120.1186 | 1426.75 | 1677813.8332 | 403242.6866 | 182915.3631 | 0 | 642107.6435
7233 | 1674.4572 | 2111.3416 | 1739.4328 | 2055.3077 | 1674.4572 | 1809.3 | 3185880.1801 | 602804.5801 | 273438.8554 | 0 | 319318.9817
7234 | 2076.6159 | 3442.9417 | 2157.1986 | 3351.5679 | 2076.6159 | 1869.9 | 4079555.3432 | 747581.7272 | 339111.3779 | 0 | 270167.7298
7235 | 1845.2748 | 3862.8588 | 1916.8794 | 3760.3407 | 1845.2748 | 1876.9 | 3638357.3501 | 664298.9266 | 301333.3742 | 0 | 227153.3274
7236 | 2071.6969 | 3111.7459 | 2152.0887 | 3029.1618 | 2071.6969 | 1864.3 | 4060094.8382 | 745810.8908 | 338308.1069 | 0 | 281129.2719
7237 | 1651.0189 | 3254.675 | 1715.0864 | 3168.2977 | 1651.0189 | 1641.45 | 2845528.1217 | 594366.7986 | 269611.3839 | 0 | 591972.8212
7238 | 1496.2674 | 3023.7279 | 1554.3303 | 2943.4798 | 1496.2674 | 1531.1 | 2402484.8836 | 538656.2521 | 244340.461 | 0 | 701599.7684
7239 | 1315.4865 | 231.8643 | 231.8643 | 225.7108 | 225.7108 | 1827.8 | 432702.1658 | 81255.8819 | 36858.5709 | 1997558.8468 | 38045.1792
7240 | 1605.1611 | 1127.4158 | 1127.4158 | 1097.4948 | 1097.4948 | 1862.75 | 2143391.845 | 395098.139 | 179220.9058 | 930552.2352 | 147444.7927
7241 | 1758.8346 | 547.9851 | 547.9851 | 533.4419 | 533.4419 | 1899.95 | 1062548.0837 | 192039.0701 | 87111.056 | 2246144.8826 | 52241.9079
7242 | 1473.3059 | 0 | 0 | 0 | 0 | 1908.65 | 0 | 0 | 0 | 2700569.7697 | 0
7243 | 1812.4967 | 0 | 0 | 0 | 0 | 1910.95 | 0 | 0 | 0 | 6158863.9395 | 0
7244 | 1695.2791 | 0 | 0 | 0 | 0 | 1863.8 | 0 | 0 | 0 | 5760558.4192 | 0
7245 | 1998.285 | 0 | 0 | 0 | 0 | 1846.95 | 0 | 0 | 0 | 6790172.4334 | 0
7246 | 1626.9086 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1838.7 | 598050.6979 | 111351.8261 | 50510.4255 | 4477197.7426 | 49337.4762
7247 | 1615.2545 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1810.7 | 1140820.6679 | 215514.4963 | 97759.7701 | 3454417.3322 | 112065.6
7248 | 1388.3885 | 0 | 0 | 0 | 0 | 1534.85 | 0 | 0 | 0 | 2544916.1737 | 0
7249 | 1436.5587 | 0 | 0 | 0 | 0 | 1255.5 | 0 | 0 | 0 | 1709504.8482 | 0
7250 | 1567.0843 | 0 | 0 | 0 | 0 | 1247.5 | 0 | 0 | 0 | 1864830.3301 | 0
7251 | 991.3731 | 0 | 0 | 0 | 0 | 1309.15 | 0 | 0 | 0 | 1179734.0114 | 0
7252 | 1218.2391 | 0 | 0 | 0 | 0 | 1242.35 | 0 | 0 | 0 | 1449704.4909 | 0
7253 | 1230.6701 | 0 | 0 | 0 | 0 | 1469.9 | 0 | 0 | 0 | 1464497.394 | 0
7254 | 1351.8724 | 0 | 0 | 0 | 0 | 1728.95 | 0 | 0 | 0 | 1608728.1976 | 0
7255 | 1256.2333 | 171.595 | 171.595 | 167.0409 | 167.0409 | 1786 | 313623.5684 | 60134.7332 | 27277.7832 | 1996489.5985 | 34990.498
7256 | 631.5235 | 550.2507 | 550.2507 | 535.6474 | 535.6474 | 1816.7 | 1023102.6262 | 192833.0517 | 87471.2148 | 175740.9858 | 96107.1228
7257 | 1426.3624 | 912.1402 | 912.1402 | 887.9325 | 887.9325 | 1846.9 | 1726209.4514 | 319655.6878 | 144999.3717 | 986941.9845 | 133066.7119
7258 | 1434.29 | 2106.4903 | 1489.9473 | 2050.5852 | 1434.29 | 1562.1 | 2360241.9829 | 516344.4133 | 234219.563 | 0 | 628075.6072
7259 | 1329.046 | 2193.8767 | 1380.6193 | 2135.6524 | 1329.046 | 1519.75 | 2123421.1869 | 478456.5568 | 217033.2103 | 0 | 638274.3372
7260 | 1071.6104 | 2553.9254 | 1113.1936 | 2486.1456 | 1071.6104 | 1432.15 | 1610644.8074 | 385779.7577 | 174993.9845 | 0 | 608513.9872
7261 | 1688.5431 | 2146.4272 | 1754.0665 | 2089.4622 | 1688.5431 | 1328.15 | 2355174.2022 | 607875.5005 | 275739.0812 | 0 | 1134447.6528
7262 | 1314.6289 | 855.892 | 855.892 | 833.1771 | 833.1771 | 1558.45 | 1365053.7403 | 299943.7563 | 136057.8206 | 882501.2063 | 360106.9856
7263 | 1623.5803 | 833.0165 | 833.0165 | 810.9087 | 810.9087 | 1848.3 | 1572113.1184 | 291927.1267 | 132421.3883 | 1489627.1466 | 120412.6335
7264 | 1596.3166 | 340.8827 | 340.8827 | 331.8359 | 331.8359 | 1884.25 | 656098.6385 | 119460.923 | 54188.802 | 2317793.1464 | 37597.5677
7265 | 1509.3432 | 257.8324 | 257.8324 | 250.9896 | 250.9896 | 1898.45 | 500299.2504 | 90356.2728 | 40986.6093 | 2306562.1294 | 24948.9055
7266 | 1577.5497 | 0 | 0 | 0 | 0 | 1908.65 | 0 | 0 | 0 | 2891648.5414 | 0
7267 | 1551.363 | 0 | 0 | 0 | 0 | 1910.95 | 0 | 0 | 0 | 5271531.3619 | 0
7268 | 1267.9631 | 0 | 0 | 0 | 0 | 1863.8 | 0 | 0 | 0 | 4308538.6512 | 0
7269 | 1587.2847 | 0 | 0 | 0 | 0 | 1846.95 | 0 | 0 | 0 | 5393593.4242 | 0
7270 | 1797.835 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1838.2 | 598203.8664 | 111351.8261 | 50510.4255 | 5058005.6498 | 49490.4132
7271 | 1567.0843 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1790.7 | 1129971.2429 | 215514.4963 | 97759.7701 | 3290735.1047 | 123905.6
7272 | 1323.9027 | 0 | 0 | 0 | 0 | 1410.75 | 0 | 0 | 0 | 2426713.5758 | 0
7273 | 1209.6927 | 0 | 0 | 0 | 0 | 1634.6 | 0 | 0 | 0 | 1439534.3701 | 0
7274 | 1199.5926 | 0 | 0 | 0 | 0 | 1428.1 | 0 | 0 | 0 | 1427515.1357 | 0
7275 | 1285.8327 | 0 | 0 | 0 | 0 | 1330.45 | 0 | 0 | 0 | 1530140.8999 | 0
7276 | 1353.4263 | 0 | 0 | 0 | 0 | 1507.1 | 0 | 0 | 0 | 1610577.3101 | 0
7277 | 1157.6379 | 0 | 0 | 0 | 0 | 1681.5 | 0 | 0 | 0 | 1377589.0891 | 0
7278 | 1076.0594 | 0 | 0 | 0 | 0 | 1706.45 | 0 | 0 | 0 | 1280510.6634 | 0
7279 | 1040.5708 | 477.9458 | 477.9458 | 465.2613 | 465.2613 | 1786 | 874760.1226 | 167494.0804 | 75977.1759 | 1054542.2264 | 97459.88
7280 | 680.187 | 971.9722 | 706.5815 | 946.1766 | 680.187 | 1765.7 | 1263152.2782 | 244867.3345 | 111074.5437 | 0 | 159367.8236
7281 | 1145.7167 | 2123.0447 | 1190.1763 | 2066.7003 | 1145.7167 | 1803.4 | 2175894.1294 | 412458.0278 | 187095.5443 | 0 | 225247.9119
7282 | 1580.9303 | 3093.6551 | 1642.2786 | 3011.5512 | 1580.9303 | 1753.95 | 2917487.6106 | 569134.9152 | 258165.9213 | 0 | 388987.9052
7283 | 1460.9439 | 2752.2041 | 1517.6356 | 2679.1621 | 1460.9439 | 1622.6 | 2492305.7573 | 525939.7939 | 238572.1343 | 0 | 551360.2173
7284 | 1561.3107 | 2541.8783 | 1621.8962 | 2474.4183 | 1561.3107 | 1587.15 | 2611765.3644 | 562071.848 | 254962.0355 | 0 | 644587.118
7285 | 1658.8698 | 2800.4742 | 1723.242 | 2726.1512 | 1658.8698 | 1380.65 | 2409070.4396 | 597193.1442 | 270893.4457 | 0 | 1027421.0385
7286 | 1697.236 | 1763.0968 | 1763.0968 | 1716.3052 | 1697.236 | 1331.65 | 2370470.3026 | 611004.9686 | 277158.6427 | 0 | 1134347.6806
7287 | 1609.0448 | 2011.8511 | 1671.4836 | 1958.4576 | 1609.0448 | 1435.35 | 2425044.145 | 579256.128 | 262757.0158 | 0 | 908547.1463
7288 | 1884.7238 | 207.8711 | 207.8711 | 202.3543 | 202.3543 | 1737.75 | 369686.2405 | 72847.5402 | 33044.4536 | 3083783.392 | 51944.9065
7289 | 1429.3409 | 398.4502 | 398.4502 | 387.8755 | 387.8755 | 1894.45 | 773307.3858 | 139635.1913 | 63340.0743 | 1909006.0956 | 40074.1685
7290 | 1778.5902 | 0 | 0 | 0 | 0 | 1908.65 | 0 | 0 | 0 | 3260155.8219 | 0
7291 | 1691.5158 | 0 | 0 | 0 | 0 | 1910.95 | 0 | 0 | 0 | 5747770.7428 | 0
7292 | 1294.379 | 0 | 0 | 0 | 0 | 1863.8 | 0 | 0 | 0 | 4398299.8726 | 0
7293 | 1858.4361 | 0 | 0 | 0 | 0 | 1847.45 | 0 | 0 | 0 | 6314965.9663 | 0
7294 | 1860.7669 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1839.7 | 597937.6451 | 111351.8261 | 50510.4255 | 5271848.5586 | 49031.6022
7295 | 1745.7801 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1821.2 | 1144743.0585 | 215514.4963 | 97759.7701 | 3897943.3686 | 105849.6
7296 | 1270.2939 | 0 | 0 | 0 | 0 | 1798.2 | 0 | 0 | 0 | 2328448.7664 | 0
7297 | 979.2 | 0 | 0 | 0 | 0 | 1761.45 | 0 | 0 | 0 | 1165248 | 0
7298 | 1126.4 | 0 | 0 | 0 | 0 | 1685.9 | 0 | 0 | 0 | 1340416 | 0
7299 | 942.4 | 0 | 0 | 0 | 0 | 1682.25 | 0 | 0 | 0 | 1121456 | 0
7300 | 1153.6 | 0 | 0 | 0 | 0 | 1697.35 | 0 | 0 | 0 | 1372784 | 0
7301 | 813.6 | 0 | 0 | 0 | 0 | 1717.2 | 0 | 0 | 0 | 968184 | 0
7302 | 752.8 | 0 | 0 | 0 | 0 | 1726.55 | 0 | 0 | 0 | 895832 | 0
7303 | 972.165 | 335.0166 | 335.0166 | 326.1255 | 326.1255 | 1764 | 603931.1705 | 117405.1623 | 53256.2861 | 1184190.4937 | 75337.336
7304 | 714.13 | 518.6337 | 518.6337 | 504.8694 | 504.8694 | 1768.7 | 936856.1411 | 181752.9855 | 82445.1737 | 383574.6723 | 114306.147
7305 | 999.303 | 1038.0807 | 1038.0807 | 1010.5306 | 999.303 | 1801.4 | 1890845.9316 | 359749.08 | 163186.1799 | 0 | 198461.5758
7306 | 1215.461 | 2497.6128 | 1262.6277 | 2431.3275 | 1215.461 | 1711.75 | 2187437.4127 | 437565.96 | 198484.7813 | 0 | 350356.6333
7307 | 1450.762 | 3909.4378 | 1507.0585 | 3805.6834 | 1450.762 | 1701.15 | 2593928.431 | 522274.32 | 236909.4346 | 0 | 433560.2237
7308 | 1203.09 | 3474.6461 | 1249.7756 | 3382.4309 | 1203.09 | 1685.7 | 2131833.3621 | 433112.4 | 196464.597 | 0 | 378131.187
7309 | 1458.605 | 2788.0076 | 1515.2058 | 2714.0154 | 1458.605 | 1596.65 | 2450418.8795 | 525097.8 | 238190.1965 | 0 | 588328.3268
7310 | 1394.271 | 2526.0231 | 1448.3753 | 2458.9838 | 1394.271 | 1558.45 | 2278678.0969 | 501937.56 | 227684.4543 | 0 | 615640.36
7311 | 1158.39 | 2080.3675 | 1203.341 | 2025.1557 | 1158.39 | 1806.7 | 2196023.9572 | 417020.4 | 189165.087 | 0 | 223916.787
7312 | 1214.189 | 1620.2227 | 1261.3053 | 1577.2229 | 1214.189 | 1860.75 | 2369596.618 | 437108.04 | 198277.0637 | 0 | 169075.8183
7313 | 1159.956 | 638.6052 | 638.6052 | 621.657 | 621.657 | 1899.45 | 1238129.9961 | 223796.5145 | 101516.5856 | 986702.0951 | 61185.3788
7314 | 1375.523 | 0 | 0 | 0 | 0 | 1908.65 | 0 | 0 | 0 | 2521333.659 | 0
7315 | 1310.4 | 0 | 0 | 0 | 0 | 1910.95 | 0 | 0 | 0 | 4452739.2 | 0
7316 | 1376 | 0 | 0 | 0 | 0 | 1863.8 | 0 | 0 | 0 | 4675648 | 0
7317 | 1444 | 0 | 0 | 0 | 0 | 1847.45 | 0 | 0 | 0 | 4906712 | 0
7318 | 890.4 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1839.7 | 596619.8645 | 111351.8261 | 50510.4255 | 1974541.6863 | 49031.6022
7319 | 1152 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1821.7 | 1145274.8719 | 215514.4963 | 97759.7701 | 1880278.6159 | 105553.6
7320 | 1338.4 | 0 | 0 | 0 | 0 | 1806.65 | 0 | 0 | 0 | 2453287.2 | 0
7321 | 1149.6 | 0 | 0 | 0 | 0 | 1788.85 | 0 | 0 | 0 | 2107216.8 | 0
7322 | 1115.2 | 0 | 0 | 0 | 0 | 1631.35 | 0 | 0 | 0 | 2044161.6 | 0
7323 | 995.2 | 0 | 0 | 0 | 0 | 1563.95 | 0 | 0 | 0 | 1824201.6 | 0
7324 | 1403.2 | 0 | 0 | 0 | 0 | 1563.1 | 0 | 0 | 0 | 2572065.6 | 0
7325 | 927.2 | 0 | 0 | 0 | 0 | 1564.5 | 0 | 0 | 0 | 1699557.6 | 0
7326 | 899.2 | 0 | 0 | 0 | 0 | 1738.2 | 0 | 0 | 0 | 1648233.6 | 0
7327 | 729.6 | 323.4661 | 323.4661 | 314.8815 | 314.8815 | 1775.2 | 586476.0247 | 113357.3486 | 51420.1529 | 760178.9666 | 69288.0808
7328 | 1140.583 | 1184.843 | 1184.843 | 1153.3979 | 1140.583 | 1696.35 | 2030373.9964 | 410609.88 | 186257.2039 | 0 | 346338.028
7329 | 1125.237 | 1418.9408 | 1168.9015 | 1381.2829 | 1125.237 | 1704.8 | 2013070.71 | 405085.32 | 183751.2021 | 0 | 332169.9624
7330 | 1053.168 | 2488.5679 | 1094.0349 | 2422.5227 | 1053.168 | 1650.75 | 1823330.4643 | 379140.48 | 171982.3344 | 0 | 367818.924
7331 | 1214.887 | 3117.3222 | 1262.0304 | 3034.5901 | 1214.887 | 1545.7 | 1969530.3044 | 437359.32 | 198391.0471 | 0 | 551923.1641
7332 | 1367.312 | 3449.5953 | 1420.3702 | 3358.0449 | 1367.312 | 1487 | 2131363.9458 | 492232.32 | 223282.0496 | 0 | 701431.056
7333 | 1412.702 | 2686.2275 | 1467.5215 | 2614.9365 | 1412.702 | 1448.5 | 2145503.8053 | 508572.72 | 230694.2366 | 0 | 779105.153
7334 | 992.147 | 1985.6493 | 1030.647 | 1932.9513 | 992.147 | 1600.55 | 1669000.9954 | 357172.92 | 162017.6051 | 0 | 396313.1191
7335 | 979.152 | 1372.3494 | 1017.1477 | 1335.928 | 979.152 | 1622.6 | 1671574.5747 | 352494.72 | 159895.5216 | 0 | 369531.9648
7336 | 1263.475 | 1235.1098 | 1235.1098 | 1202.3306 | 1202.3306 | 1884.75 | 2378399.2567 | 432839.023 | 196340.5902 | 112077.6494 | 135637.3793
7337 | 1350.183 | 709.3842 | 709.3842 | 690.5575 | 690.5575 | 1900.75 | 1376956.9234 | 248600.704 | 112768.0416 | 1209093.5211 | 67088.0375
7338 | 1374.738 | 0 | 0 | 0 | 0 | 1913.4 | 0 | 0 | 0 | 2519894.754 | 0
7339 | 1219.2 | 0 | 0 | 0 | 0 | 1913.15 | 0 | 0 | 0 | 2234793.6 | 0
7340 | 1216 | 0 | 0 | 0 | 0 | 1864.5 | 0 | 0 | 0 | 2228928 | 0
7341 | 1084.8 | 0 | 0 | 0 | 0 | 1845 | 0 | 0 | 0 | 1988438.4 | 0
7342 | 1232 | 0 | 0 | 0 | 0 | 1837.85 | 0 | 0 | 0 | 2258256 | 0
7343 | 838.4 | 0 | 0 | 0 | 0 | 1821.1 | 0 | 0 | 0 | 1536787.2 | 0
7344 | 932 | 361.8479 | 361.8479 | 352.2447 | 352.2447 | 1807.2 | 670436.1391 | 126808.0743 | 57521.5515 | 1062691.555 | 66464.3296
7345 | 870.547 | 0 | 0 | 0 | 0 | 1439.25 | 0 | 0 | 0 | 1035950.93 | 0
7346 | 870.2682 | 0 | 0 | 0 | 0 | 1791.1 | 0 | 0 | 0 | 1035619.158 | 0
7347 | 862.4134 | 0 | 0 | 0 | 0 | 1694.7 | 0 | 0 | 0 | 1026271.946 | 0
7348 | 826.5843 | 0 | 0 | 0 | 0 | 1528.75 | 0 | 0 | 0 | 983635.317 | 0
7349 | 819.3456 | 0 | 0 | 0 | 0 | 1365.05 | 0 | 0 | 0 | 975021.264 | 0
7350 | 813.6014 | 0 | 0 | 0 | 0 | 1296.25 | 0 | 0 | 0 | 968185.666 | 0
7351 | 903.9083 | 938.9839 | 938.9839 | 914.0638 | 903.9083 | 1032.25 | 982972.2573 | 325406.988 | 147608.2254 | 0 | 874756.967
7352 | 791.2837 | 822.3604 | 821.9896 | 800.5354 | 791.2837 | 717.85 | 598698.7209 | 284862.132 | 129216.6282 | 0 | 1014544.396
7353 | 1005.2559 | 1884.155 | 1044.2647 | 1834.1505 | 1005.2559 | 1517.55 | 1606522.1814 | 361892.124 | 164158.2885 | 0 | 484985.709
7354 | 1195.4363 | 2748.5548 | 1241.8246 | 2675.6096 | 1195.4363 | 359.6 | 452073.1225 | 430357.068 | 195214.7478 | 0 | 1960993.7065
7355 | 1226.7781 | 3841.6755 | 1274.3828 | 3739.7195 | 1226.7781 | 364.85 | 471198.4527 | 441640.116 | 200332.8637 | 0 | 2005966.2102
7356 | 1217.1598 | 3623.2242 | 1264.3916 | 3527.0658 | 1217.1598 | 356.05 | 456514.7414 | 438177.528 | 198762.1953 | 0 | 2000949.8532
7357 | 1234.1608 | 3187.8175 | 1282.0523 | 3103.2146 | 1234.1608 | 341 | 441807.6521 | 444297.888 | 201538.4586 | 0 | 2047472.7672
7358 | 1231.0896 | 2871.2054 | 1278.8611 | 2795.0052 | 1231.0896 | 1030.55 | 1337632.6015 | 443192.256 | 201036.9317 | 0 | 1193479.8127
7359 | 1249.2235 | 2081.2256 | 1297.6998 | 2025.991 | 1249.2235 | 768.3 | 1012967.6454 | 449720.46 | 203998.1976 | 0 | 1538668.585
7360 | 1250.9173 | 1571.616 | 1299.4585 | 1529.9062 | 1250.9173 | 1536.45 | 2027182.2631 | 450330.228 | 204274.7951 | 0 | 579862.7144
7361 | 1257.5245 | 600.3066 | 600.3066 | 584.3748 | 584.3748 | 1884.2 | 1161667.1964 | 210374.9124 | 95428.3977 | 1233883.4797 | 66239.1054
7362 | 1230.4932 | 0 | 0 | 0 | 0 | 1860.9 | 0 | 0 | 0 | 2255494.0356 | 0
7363 | 1196.9072 | 0 | 0 | 0 | 0 | 1860.75 | 0 | 0 | 0 | 4067090.6656 | 0
7364 | 1113.5542 | 0 | 0 | 0 | 0 | 736.85 | 0 | 0 | 0 | 3783857.1716 | 0
7365 | 1185.424 | 0 | 0 | 0 | 0 | 949.5 | 0 | 0 | 0 | 4028070.752 | 0
7366 | 1185.7689 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1644.2 | 535741.3971 | 111351.8261 | 50510.4255 | 2978205.2085 | 108829.9692
7367 | 1162.3773 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1503.7 | 951218.2718 | 215514.4963 | 97759.7701 | 1915540.6813 | 293809.6
7368 | 889.2698 | 0 | 0 | 0 | 0 | 1303.85 | 0 | 0 | 0 | 1630031.5434 | 0
7369 | 85.6 | 0 | 0 | 0 | 0 | 835.85 | 0 | 0 | 0 | 101864 | 0
7370 | 91.2 | 0 | 0 | 0 | 0 | 828.85 | 0 | 0 | 0 | 108528 | 0
7371 | 84 | 0 | 0 | 0 | 0 | 551.3 | 0 | 0 | 0 | 99960 | 0
7372 | 87.2 | 0 | 0 | 0 | 0 | 550.65 | 0 | 0 | 0 | 103768 | 0
7373 | 81.6 | 0 | 0 | 0 | 0 | 550.3 | 0 | 0 | 0 | 97104 | 0
7374 | 85.6 | 0 | 0 | 0 | 0 | 275.1 | 0 | 0 | 0 | 101864 | 0
7375 | 65.492 | 58.9335 | 58.9335 | 57.3694 | 57.3694 | 274.35 | 16523.3445 | 20652.9872 | 9368.4245 | 14888.7097 | 96903.8758
7376 | 93.277 | 96.8966 | 96.8966 | 94.325 | 93.277 | 280.75 | 27465.7956 | 33579.72 | 15232.1341 | 0 | 160366.4823
7377 | 618.406 | 948.0922 | 642.4031 | 922.9303 | 618.406 | 291.5 | 189656.1114 | 222626.16 | 100985.6998 | 0 | 1056546.651
7378 | 770.837 | 1974.8852 | 800.7491 | 1922.4728 | 770.837 | 303.85 | 246685.551 | 277501.32 | 125877.6821 | 0 | 1307455.1775
7379 | 1352.587 | 2909.1498 | 1405.0738 | 2831.9426 | 1352.587 | 314.3 | 447958.1573 | 486931.32 | 220877.4571 | 0 | 2280055.9059
7380 | 1093.259 | 3321.3559 | 1135.6826 | 3233.2089 | 1093.259 | 309.1 | 355935.0699 | 393573.24 | 178529.1947 | 0 | 1848591.6431
7381 | 1179.255 | 3265.249 | 1225.0157 | 3178.5911 | 1179.255 | 297.25 | 368421.6163 | 424531.8 | 192572.3415 | 0 | 2007976.4512
7382 | 1555.276 | 2773.0332 | 1615.6281 | 2699.4384 | 1555.276 | 299.95 | 490876.8178 | 559899.36 | 253976.5708 | 0 | 2644046.9638
7383 | 1278.067 | 2464.7783 | 1327.6621 | 2399.3644 | 1278.067 | 307.7 | 413483.2285 | 460104.12 | 208708.3411 | 0 | 2162872.7841
7384 | 1480.787 | 1335.0791 | 1335.0791 | 1299.6469 | 1299.6469 | 312.95 | 427000.2974 | 467872.8702 | 212232.3325 | 332029.8733 | 2146189.0927
7385 | 1756.931 | 633.5431 | 633.5431 | 616.7292 | 616.7292 | 321.8 | 208627.5942 | 222022.5244 | 100711.884 | 2089989.8364 | 1013100.8106
7386 | 1617.657 | 0 | 0 | 0 | 0 | 1432.05 | 0 | 0 | 0 | 2965165.281 | 0
7387 | 1474.4 | 0 | 0 | 0 | 0 | 1855.8 | 0 | 0 | 0 | 5010011.2 | 0
7388 | 1431.2 | 0 | 0 | 0 | 0 | 1355.9 | 0 | 0 | 0 | 4863217.6 | 0
7389 | 1365.6 | 0 | 0 | 0 | 0 | 605.4 | 0 | 0 | 0 | 4640308.8 | 0
7390 | 1100.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 301.15 | 98048.3128 | 111351.8261 | 50510.4255 | 2689480.8863 | 519634.0449
7391 | 1292.8 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 288.95 | 182043.2875 | 215514.4963 | 97759.7701 | 2358717.0159 | 1012941.6
7392 | 1215.2 | 0 | 0 | 0 | 0 | 276.85 | 0 | 0 | 0 | 2227461.6 | 0
7393 | 949.6 | 0 | 0 | 0 | 0 | 1535.75 | 0 | 0 | 0 | 1130024 | 0
7394 | 1412.8 | 0 | 0 | 0 | 0 | 1272.85 | 0 | 0 | 0 | 1681232 | 0
7395 | 1319.2 | 0 | 0 | 0 | 0 | 1264.3 | 0 | 0 | 0 | 1569848 | 0
7396 | 1212.8 | 0 | 0 | 0 | 0 | 1274.45 | 0 | 0 | 0 | 1443232 | 0
7397 | 1012 | 0 | 0 | 0 | 0 | 1320.35 | 0 | 0 | 0 | 1204280 | 0
7398 | 1101.6 | 0 | 0 | 0 | 0 | 1399.2 | 0 | 0 | 0 | 1310904 | 0
7399 | 1240.205 | 495.4694 | 495.4694 | 482.3199 | 482.3199 | 1445.4 | 732035.1964 | 173635.1514 | 78762.834 | 1389203.4523 | 261836.0882
7400 | 972.841 | 1010.5919 | 1010.5919 | 983.7713 | 972.841 | 1470.9 | 1496594.1533 | 350222.76 | 158864.9353 | 0 | 514730.1731
7401 | 1091.276 | 2214.4627 | 1133.6227 | 2155.692 | 1091.276 | 1577.4 | 1805793.612 | 392859.36 | 178205.3708 | 0 | 461173.2376
7402 | 1317.246 | 2886.4935 | 1368.3614 | 2809.8875 | 1317.246 | 1511.65 | 2097619.3551 | 474208.56 | 215106.2718 | 0 | 643277.0841
7403 | 1461.008 | 3375.9118 | 1517.702 | 3286.317 | 1461.008 | 1482.75 | 2280262.3874 | 525962.88 | 238582.6064 | 0 | 755706.388
7404 | 1485.364 | 3329.4222 | 1543.0032 | 3241.0611 | 1485.364 | 1459.95 | 2294722.3777 | 534731.04 | 242559.9412 | 0 | 802170.8282
7405 | 1859.342 | 3092.9684 | 1931.4933 | 3010.8827 | 1859.342 | 1485.7 | 2936432.3285 | 669363.12 | 303630.5486 | 0 | 956259.5906
7406 | 1111.595 | 3296.7591 | 1154.7302 | 3209.2649 | 1111.595 | 1506.35 | 1769167.4544 | 400174.2 | 181523.4635 | 0 | 548738.8718
7407 | 1623.432 | 2616.9808 | 1686.4289 | 2547.5276 | 1623.432 | 1547.15 | 2653057.1336 | 584435.52 | 265106.4456 | 0 | 735171.1812
7408 | 1529.712 | 1052.5855 | 1052.5855 | 1024.6505 | 1024.6505 | 1794.4 | 1938499.7502 | 368874.1749 | 167325.4244 | 925777.7553 | 206211.8656
7409 | 1351.591 | 476.2722 | 476.2722 | 463.6322 | 463.6322 | 1900.25 | 926001.5043 | 166907.6043 | 75711.1438 | 1627628.4177 | 45269.0438
7410 | 1119.86 | 0 | 0 | 0 | 0 | 1913.4 | 0 | 0 | 0 | 2052703.38 | 0
7411 | 915.2 | 0 | 0 | 0 | 0 | 1913.15 | 0 | 0 | 0 | 3109849.6 | 0
7412 | 1072.8 | 0 | 0 | 0 | 0 | 1860.9 | 0 | 0 | 0 | 3645374.4 | 0
7413 | 1204 | 0 | 0 | 0 | 0 | 1757.25 | 0 | 0 | 0 | 4091192 | 0
7414 | 921.6 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1837.85 | 596193.4021 | 111351.8261 | 50510.4255 | 2080559.2863 | 49597.4691
7415 | 1499.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1821.1 | 1144211.1117 | 215514.4963 | 97759.7701 | 3060064.2159 | 105908.8
7416 | 1340 | 0 | 0 | 0 | 0 | 1806.25 | 0 | 0 | 0 | 2456220 | 0
7417 | 1268 | 0 | 0 | 0 | 0 | 1632.35 | 0 | 0 | 0 | 1508920 | 0
7418 | 1223.2 | 0 | 0 | 0 | 0 | 1740.85 | 0 | 0 | 0 | 1455608 | 0
7419 | 1244.8 | 0 | 0 | 0 | 0 | 1574.8 | 0 | 0 | 0 | 1481312 | 0
7420 | 1196 | 0 | 0 | 0 | 0 | 1573.45 | 0 | 0 | 0 | 1423240 | 0
7421 | 920 | 0 | 0 | 0 | 0 | 1522.95 | 0 | 0 | 0 | 1094800 | 0
7422 | 1409.6 | 0 | 0 | 0 | 0 | 1585.85 | 0 | 0 | 0 | 1677424 | 0
7423 | 1301.174 | 188.4911 | 188.4911 | 183.4887 | 183.4887 | 1712.85 | 329836.3012 | 66055.9212 | 29963.6998 | 2048717.2099 | 51574.15
7424 | 900.704 | 644.1296 | 644.1296 | 627.0347 | 627.0347 | 1565.85 | 1031444.4102 | 225732.5045 | 102394.7722 | 501635.7633 | 266468.2455
7425 | 1025.232 | 299.6443 | 299.6443 | 291.6919 | 291.6919 | 1576.3 | 483988.4383 | 105009.0743 | 47633.2828 | 1344579.0529 | 120975.6714
7426 | 1161.734 | 1206.8148 | 1206.8148 | 1174.7866 | 1161.734 | 1571.6 | 1920405.496 | 418224.24 | 189711.1622 | 0 | 497686.8456
7427 | 1161.093 | 1603.5759 | 1206.1489 | 1561.0179 | 1161.093 | 1515.3 | 1855759.5694 | 417993.48 | 189606.4869 | 0 | 562781.7771
7428 | 1382.406 | 1906.2275 | 1436.0499 | 1855.6373 | 1382.406 | 1505.5 | 2191325.8694 | 497666.16 | 225746.8998 | 0 | 683599.767
7429 | 1308.312 | 2019.424 | 1359.0807 | 1965.8296 | 1308.312 | 1522.7 | 2097834.1259 | 470992.32 | 213647.3496 | 0 | 624457.3176
7430 | 1078.045 | 1898.4531 | 1119.8783 | 1848.0692 | 1078.045 | 1603.45 | 1817374.9034 | 388096.2 | 176044.7485 | 0 | 427498.7447
7431 | 1313.362 | 1523.7656 | 1364.3267 | 1483.3256 | 1313.362 | 1589.2 | 2191816.7995 | 472810.32 | 214472.0146 | 0 | 539529.1096
7432 | 1419.024 | 609.4086 | 609.4086 | 593.2352 | 593.2352 | 1860.75 | 1159111.5978 | 213564.6725 | 96875.3084 | 1513670.8677 | 80860.5255
7433 | 1209.14 | 329.6231 | 329.6231 | 320.8751 | 320.8751 | 1899.25 | 640366.8627 | 115515.0419 | 52398.9065 | 1628189.5317 | 31644.2653
7434 | 1214.131 | 0 | 0 | 0 | 0 | 1911.9 | 0 | 0 | 0 | 2225502.123 | 0
7435 | 1495.2 | 0 | 0 | 0 | 0 | 1911.65 | 0 | 0 | 0 | 5080689.6 | 0
7436 | 1044.8 | 0 | 0 | 0 | 0 | 1726.55 | 0 | 0 | 0 | 3550230.4 | 0
7437 | 1540.8 | 0 | 0 | 0 | 0 | 1696.2 | 0 | 0 | 0 | 5235638.4 | 0
7438 | 1288 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1829.65 | 594217.2716 | 111351.8261 | 50510.4255 | 3325586.4863 | 52105.6359
7439 | 1128.8 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1812.9 | 1139160.4921 | 215514.4963 | 97759.7701 | 1801445.0159 | 110763.2
7440 | 1216 | 0 | 0 | 0 | 0 | 1680.25 | 0 | 0 | 0 | 2228928 | 0
7441 | 784.8 | 0 | 0 | 0 | 0 | 1484.85 | 0 | 0 | 0 | 933912 | 0
7442 | 1167.2 | 0 | 0 | 0 | 0 | 1478.35 | 0 | 0 | 0 | 1388968 | 0
7443 | 1024 | 0 | 0 | 0 | 0 | 1369.8 | 0 | 0 | 0 | 1218560 | 0
7444 | 1230.4 | 0 | 0 | 0 | 0 | 1333.95 | 0 | 0 | 0 | 1464176 | 0
7445 | 1207.2 | 0 | 0 | 0 | 0 | 1070.85 | 0 | 0 | 0 | 1436568 | 0
7446 | 961.6 | 0 | 0 | 0 | 0 | 1426.7 | 0 | 0 | 0 | 1144304 | 0
7447 | 1106.751 | 415.7837 | 415.7837 | 404.749 | 404.749 | 1543.4 | 655777.437 | 145709.6422 | 66095.5127 | 1286769.655 | 180898.9842
7448 | 981.304 | 1019.3833 | 1019.3833 | 992.3294 | 981.304 | 1530.85 | 1575650.8417 | 353269.44 | 160246.9432 | 0 | 460378.7716
7449 | 1087.115 | 2219.8239 | 1129.3013 | 2160.911 | 1087.115 | 1551.8 | 1772790.9358 | 391361.4 | 177525.8795 | 0 | 487244.943
7450 | 1162.094 | 3451.7124 | 1207.1888 | 3360.1058 | 1162.094 | 1584.2 | 1935627.9612 | 418353.84 | 189769.9502 | 0 | 483198.6852
7451 | 1710.031 | 3226.1224 | 1776.3883 | 3140.5029 | 1710.031 | 1462.25 | 2635520.6266 | 615611.16 | 279248.0623 | 0 | 919569.1702
7452 | 1447.547 | 3342.214 | 1503.7187 | 3253.5135 | 1447.547 | 1419.4 | 2170122.5015 | 521116.92 | 236384.4251 | 0 | 840445.7882
7453 | 1355.19 | 2468.279 | 1407.7778 | 2402.7723 | 1355.19 | 1396.6 | 1994182.4294 | 487868.4 | 221302.527 | 0 | 817721.646
7454 | 1224.544 | 2701.9052 | 1272.0621 | 2630.1981 | 1224.544 | 1556.35 | 2003696.8892 | 440835.84 | 199968.0352 | 0 | 543268.9456
7455 | 1435.996 | 1612.4992 | 1491.7195 | 1569.7044 | 1435.996 | 1472.6 | 2222980.3154 | 516958.56 | 234498.1468 | 0 | 757344.2904
7456 | 1576.816 | 1540.4664 | 1540.4664 | 1499.5833 | 1499.5833 | 1734.45 | 2728015.7238 | 539849.9794 | 244881.949 | 141567.5828 | 389790.7541
7457 | 1545.343 | 674.178 | 674.178 | 656.2857 | 656.2857 | 1899.25 | 1307681.3469 | 236262.8631 | 107171.4599 | 1629641.9742 | 64722.1023
7458 | 1644.762 | 0 | 0 | 0 | 0 | 1911.4 | 0 | 0 | 0 | 3014848.746 | 0
7459 | 1521.6 | 0 | 0 | 0 | 0 | 1911.65 | 0 | 0 | 0 | 5170396.8 | 0
7460 | 1470.4 | 0 | 0 | 0 | 0 | 1715 | 0 | 0 | 0 | 4996419.2 | 0
7461 | 1567.2 | 0 | 0 | 0 | 0 | 1712.6 | 0 | 0 | 0 | 5325345.6 | 0
7462 | 1155.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1835.85 | 595512.2439 | 111351.8261 | 50510.4255 | 2874332.0863 | 50209.2171
7463 | 1411.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1712 | 1073717.5825 | 215514.4963 | 97759.7701 | 2761040.2159 | 170496
7464 | 1588.8 | 0 | 0 | 0 | 0 | 1527.25 | 0 | 0 | 0 | 2912270.4 | 0
7465 | 1478.4 | 0 | 0 | 0 | 0 | 1484.85 | 0 | 0 | 0 | 1759296 | 0
7466 | 1609.6 | 0 | 0 | 0 | 0 | 1251.3 | 0 | 0 | 0 | 1915424 | 0
7467 | 1016 | 0 | 0 | 0 | 0 | 1202.2 | 0 | 0 | 0 | 1209040 | 0
7468 | 1200 | 0 | 0 | 0 | 0 | 1201.35 | 0 | 0 | 0 | 1428000 | 0
7469 | 1240 | 0 | 0 | 0 | 0 | 1186.35 | 0 | 0 | 0 | 1475600 | 0
7470 | 1102.4 | 0 | 0 | 0 | 0 | 1482.2 | 0 | 0 | 0 | 1311856 | 0
7471 | 1127.493 | 217.5174 | 217.5174 | 211.7446 | 211.7446 | 1655.8 | 367651.6673 | 76228.0598 | 34577.8949 | 1678566.7979 | 71340.613
7472 | 1108.431 | 389.5019 | 389.5019 | 379.1647 | 379.1647 | 1803.35 | 717333.8037 | 136499.3098 | 61917.6036 | 1336745.0373 | 72985.4676
7473 | 1506.879 | 1003.9965 | 1003.9965 | 977.351 | 977.351 | 1747.95 | 1794423.3748 | 351846.3455 | 159601.4117 | 970624.898 | 241130.1858
7474 | 1545.101 | 1381.3859 | 1381.3859 | 1344.7247 | 1344.7247 | 1606.3 | 2269050.6085 | 484100.8934 | 219593.5441 | 367289.7509 | 518219.0423
7475 | 1717.536 | 2549.8159 | 1784.1846 | 2482.1451 | 1717.536 | 1329.2 | 2402297.4639 | 618312.96 | 280473.6288 | 0 | 1152123.1488
7476 | 1743.337 | 3249.0821 | 1810.9868 | 3162.8532 | 1743.337 | 1157.7 | 2126201.0803 | 627601.32 | 284686.9321 | 0 | 1468412.7551
7477 | 1659.288 | 3651.4631 | 1723.6763 | 3554.5553 | 1659.288 | 1133.65 | 1984942.761 | 597343.68 | 270961.7304 | 0 | 1437524.1588
7478 | 1711.846 | 3486.4209 | 1778.2738 | 3393.8932 | 1711.846 | 1517.1 | 2737189.4475 | 616264.56 | 279544.4518 | 0 | 826650.4334
7479 | 1778.711 | 1321.2765 | 1321.2765 | 1286.2106 | 1286.2106 | 1567.1 | 2122281.4814 | 463035.8076 | 210038.1871 | 902753.2762 | 545022.3987
7480 | 1671.964 | 1399.2586 | 1399.2586 | 1362.123 | 1362.123 | 1612.35 | 2305223.1912 | 490364.2834 | 222434.6875 | 567938.5355 | 516857.2339
7481 | 1740.399 | 7.7765 | 7.7765 | 7.5701 | 7.5701 | 1874.15 | 14884.7945 | 2725.2391 | 1236.1987 | 3176275.3582 | 932.5485
7482 | 1561.823 | 0 | 0 | 0 | 0 | 1905.2 | 0 | 0 | 0 | 2862821.559 | 0
7483 | 1636 | 0 | 0 | 0 | 0 | 1911.15 | 0 | 0 | 0 | 5559128 | 0
7484 | 1423.2 | 0 | 0 | 0 | 0 | 1706.25 | 0 | 0 | 0 | 4836033.6 | 0
7485 | 1198.4 | 0 | 0 | 0 | 0 | 1672.1 | 0 | 0 | 0 | 4072163.2 | 0
7486 | 1556.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1829.65 | 595592.9796 | 111351.8261 | 50510.4255 | 4238968.8863 | 52105.6359
7487 | 1191.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1778.1 | 1118956.2802 | 215514.4963 | 97759.7701 | 2013480.2159 | 131364.8
7488 | 1529.6 | 0 | 0 | 0 | 0 | 1652.35 | 0 | 0 | 0 | 2803756.8 | 0
7489 | 1598.4 | 0 | 0 | 0 | 0 | 1458.95 | 0 | 0 | 0 | 2929867.2 | 0
7490 | 1415.2 | 0 | 0 | 0 | 0 | 1286.3 | 0 | 0 | 0 | 2594061.6 | 0
7491 | 1582.4 | 0 | 0 | 0 | 0 | 1329.3 | 0 | 0 | 0 | 2900539.2 | 0
7492 | 1364.8 | 0 | 0 | 0 | 0 | 1268.95 | 0 | 0 | 0 | 2501678.4 | 0
7493 | 1329.6 | 0 | 0 | 0 | 0 | 1335.35 | 0 | 0 | 0 | 2437156.8 | 0
7494 | 1695.2 | 0 | 0 | 0 | 0 | 1476.7 | 0 | 0 | 0 | 3107301.6 | 0
7495 | 1435.98 | 208.699 | 208.699 | 203.1602 | 203.1602 | 1534.65 | 325838.292 | 73137.6839 | 33176.066 | 2259758.6331 | 92540.897
7496 | 1870.081 | 1293.0844 | 1293.0844 | 1258.7667 | 1258.7667 | 1521.35 | 2005917.7745 | 453155.9969 | 205556.5953 | 1120539.1888 | 589763.3324
7497 | 1222.75 | 1549.5217 | 1270.1985 | 1508.3982 | 1222.75 | 1551.8 | 1989987.8027 | 440190 | 199675.075 | 0 | 548036.55
7498 | 1723.893 | 2562.5911 | 1790.7882 | 2494.5813 | 1723.893 | 1408.6 | 2549849.1095 | 620601.48 | 281511.7269 | 0 | 1019510.3202
7499 | 1512.119 | 2708.1858 | 1570.7964 | 2636.312 | 1512.119 | 1165.75 | 1848182.5993 | 544362.84 | 246929.0327 | 0 | 1261485.2758
7500 | 1701.586 | 3329.9073 | 1767.6156 | 3241.5334 | 1701.586 | 1150.95 | 2061154.3361 | 612570.96 | 277868.9938 | 0 | 1444731.5933
7501 | 1506.384 | 2694.7613 | 1564.8389 | 2623.2438 | 1506.384 | 1023.15 | 1620732.803 | 542298.24 | 245992.5072 | 0 | 1471511.2104
7502 | 1400.986 | 1852.2824 | 1455.3509 | 1803.1238 | 1400.986 | 1415.85 | 2075016.6843 | 504354.96 | 228781.0138 | 0 | 818385.9719
7503 | 1718.665 | 1996.3303 | 1785.3574 | 1943.3488 | 1718.665 | 1644.7 | 2966298.1587 | 618719.4 | 280657.9945 | 0 | 610641.6745
7504 | 1537.608 | 176.8991 | 176.8991 | 172.2043 | 172.2043 | 1865.25 | 337435.8667 | 61993.5457 | 28120.9612 | 2502784.9936 | 22713.7295
7505 | 1343.34 | 146.5369 | 146.5369 | 142.6479 | 142.6479 | 1899.25 | 284410.5219 | 51353.2456 | 23294.4028 | 2200868.6112 | 14067.8233
7506 | 1522.828 | 0 | 0 | 0 | 0 | 1911.9 | 0 | 0 | 0 | 2791343.724 | 0
7507 | 1356.8 | 0 | 0 | 0 | 0 | 1911.65 | 0 | 0 | 0 | 2487014.4 | 0
7508 | 1599.2 | 0 | 0 | 0 | 0 | 1722.65 | 0 | 0 | 0 | 2931333.6 | 0
7509 | 1412.8 | 0 | 0 | 0 | 0 | 1355.85 | 0 | 0 | 0 | 2589662.4 | 0
7510 | 1264.8 | 0 | 0 | 0 | 0 | 1801.9 | 0 | 0 | 0 | 2318378.4 | 0
7511 | 1524 | 0 | 0 | 0 | 0 | 1693.6 | 0 | 0 | 0 | 2793492 | 0
7512 | 828.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1587.75 | 515118.2047 | 111351.8261 | 50510.4255 | 952224.019 | 126096.5565
7513 | 1140 | 0 | 0 | 0 | 0 | 1739.8 | 0 | 0 | 0 | 1356600 | 0
7514 | 1248.8 | 0 | 0 | 0 | 0 | 1499.35 | 0 | 0 | 0 | 1486072 | 0
7515 | 1267.2 | 0 | 0 | 0 | 0 | 1546.4 | 0 | 0 | 0 | 1507968 | 0
7516 | 1367.2 | 0 | 0 | 0 | 0 | 1633.25 | 0 | 0 | 0 | 1626968 | 0
7517 | 1266.4 | 0 | 0 | 0 | 0 | 1779.9 | 0 | 0 | 0 | 1507016 | 0
7518 | 1180 | 0 | 0 | 0 | 0 | 1785.6 | 0 | 0 | 0 | 1404200 | 0
7519 | 1235.738 | 990.5585 | 990.5585 | 964.2696 | 964.2696 | 1779.2 | 1806478.3103 | 347137.0625 | 157465.2286 | 497601.5442 | 209734.3872
7520 | 932.415 | 968.5971 | 968.5971 | 942.8911 | 932.415 | 1589.05 | 1557398.3662 | 335669.4 | 152263.3695 | 0 | 383175.9443
7521 | 1225.774 | 1568.056 | 1273.3399 | 1526.4407 | 1225.774 | 1546.45 | 1993082.3726 | 441278.64 | 200168.8942 | 0 | 555949.7977
7522 | 1183.594 | 2724.816 | 1229.5231 | 2652.5009 | 1183.594 | 1362.55 | 1699094.1355 | 426093.84 | 193280.9002 | 0 | 754481.9953
7523 | 1167.775 | 3340.6112 | 1213.0902 | 3251.9532 | 1167.775 | 1109.35 | 1362848.7281 | 420399 | 190697.6575 | 0 | 1040078.8037
7524 | 1149.101 | 2735.952 | 1193.6916 | 2663.3413 | 1149.101 | 1045.35 | 1264738.594 | 413676.36 | 187648.1933 | 0 | 1096989.2696
7525 | 1061.564 | 2592.6447 | 1102.7577 | 2523.8374 | 1061.564 | 1035.05 | 1157169.9098 | 382163.04 | 173353.4012 | 0 | 1024356.1818
7526 | 1207.035 | 2080.2907 | 1253.8737 | 2025.0809 | 1207.035 | 1304.55 | 1659076.1689 | 434532.6 | 197108.8155 | 0 | 839432.4907
7527 | 1229.373 | 1159.3684 | 1159.3684 | 1128.5994 | 1128.5994 | 1608.65 | 1915800.2685 | 406295.7917 | 184300.2855 | 184717.9696 | 432334.5201
7528 | 1219.569 | 714.0744 | 714.0744 | 695.1232 | 695.1232 | 1773.7 | 1300435.1734 | 250244.3661 | 113513.6249 | 961309.0797 | 153978.8197
7529 | 850.341 | 246.0347 | 246.0347 | 239.505 | 239.505 | 1883.7 | 475524.1563 | 86221.8165 | 39111.174 | 1119662.3041 | 27265.1394
7530 | 1029.964 | 0 | 0 | 0 | 0 | 1860.3 | 0 | 0 | 0 | 1887924.012 | 0
7531 | 1183.2 | 0 | 0 | 0 | 0 | 1880.55 | 0 | 0 | 0 | 4020513.6 | 0
7532 | 1294.4 | 0 | 0 | 0 | 0 | 1819.35 | 0 | 0 | 0 | 4398371.2 | 0
7533 | 1021.6 | 0 | 0 | 0 | 0 | 1738.5 | 0 | 0 | 0 | 3471396.8 | 0
7534 | 1191.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1824.9 | 594951.363 | 111351.8261 | 50510.4255 | 2996660.0863 | 53558.5374
7535 | 1176 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1812.7 | 1144107.1937 | 215514.4963 | 97759.7701 | 1961830.6159 | 110881.6
7536 | 173.6 | 0 | 0 | 0 | 0 | 1796.3 | 0 | 0 | 0 | 318208.8 | 0
7537 | 89.6 | 0 | 0 | 0 | 0 | 1648.85 | 0 | 0 | 0 | 106624 | 0
7538 | 171.2 | 0 | 0 | 0 | 0 | 1777.85 | 0 | 0 | 0 | 203728 | 0
7539 | 109.6 | 0 | 0 | 0 | 0 | 1740.75 | 0 | 0 | 0 | 130424 | 0
7540 | 114.4 | 0 | 0 | 0 | 0 | 1752.6 | 0 | 0 | 0 | 136136 | 0
7541 | 85.6 | 0 | 0 | 0 | 0 | 1775.15 | 0 | 0 | 0 | 101864 | 0
7542 | 88.8 | 0 | 0 | 0 | 0 | 1775.85 | 0 | 0 | 0 | 105672 | 0
7543 | 85.749 | 89.0765 | 89.0765 | 86.7124 | 85.749 | 1678.55 | 151196.1845 | 30869.64 | 14002.8117 | 0 | 27564.0161
7544 | 209.928 | 168.33 | 168.33 | 163.8626 | 163.8626 | 1518.05 | 261278.0541 | 58990.5405 | 26758.7646 | 84437.8551 | 77303.3342
7545 | 856.951 | 566.614 | 566.614 | 551.5763 | 551.5763 | 1496.45 | 862816.0568 | 198567.4847 | 90072.4174 | 559751.74 | 271871.1769
7546 | 1343.987 | 693.4167 | 693.4167 | 675.0138 | 675.0138 | 1256.85 | 887277.9941 | 243004.972 | 110229.7554 | 1226227.855 | 491025.2153
7547 | 1233.607 | 1223.1188 | 1223.1188 | 1190.6579 | 1190.6579 | 1188.25 | 1485255.7985 | 428636.8544 | 194434.4398 | 78725.6473 | 945436.2957
7548 | 1009.939 | 1254.6621 | 1049.1294 | 1221.3641 | 1009.939 | 1183.05 | 1257434.4839 | 363578.04 | 164923.0387 | 0 | 825069.6661
7549 | 1251.764 | 1300.3384 | 1300.3384 | 1265.8281 | 1251.764 | 1016.65 | 1339086.4757 | 450635.04 | 204413.0612 | 0 | 1230922.1294
7550 | 1114.082 | 2188.6328 | 1157.3137 | 2130.5477 | 1114.082 | 1019.35 | 1193600.9148 | 401069.52 | 181929.5906 | 0 | 1092524.5133
7551 | 1131.027 | 2803.922 | 1174.9162 | 2729.5075 | 1131.027 | 1027.1 | 1219353.1333 | 407169.72 | 184696.7091 | 0 | 1100376.1683
7552 | 1306.039 | 1967.0495 | 1356.7195 | 1914.8451 | 1306.039 | 1355.45 | 1853644.0457 | 470174.04 | 213276.1687 | 0 | 841807.4374
7553 | 1317.887 | 784.7287 | 784.7287 | 763.9024 | 763.9024 | 1542.9 | 1234494.6446 | 275004.8702 | 124745.2648 | 1015453.74 | 341793.3253
7554 | 1482.151 | 0 | 0 | 0 | 0 | 1846.5 | 0 | 0 | 0 | 2716782.783 | 0
7555 | 1344.8 | 0 | 0 | 0 | 0 | 1859.4 | 0 | 0 | 0 | 4569630.4 | 0
7556 | 1447.2 | 0 | 0 | 0 | 0 | 1826.35 | 0 | 0 | 0 | 4917585.6 | 0
7557 | 1483.2 | 0 | 0 | 0 | 0 | 1815.35 | 0 | 0 | 0 | 5039913.6 | 0
7558 | 1075.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1808.05 | 589214.5126 | 111351.8261 | 50510.4255 | 2602492.0863 | 58712.5143
7559 | 1232.8 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1795.95 | 1132336.27 | 215514.4963 | 97759.7701 | 2154837.0159 | 120797.6
7560 | 1115.2 | 0 | 0 | 0 | 0 | 1759.25 | 0 | 0 | 0 | 2044161.6 | 0
7561 | 1131.2 | 0 | 0 | 0 | 0 | 1661.95 | 0 | 0 | 0 | 1346128 | 0
7562 | 1402.4 | 0 | 0 | 0 | 0 | 1454.1 | 0 | 0 | 0 | 1668856 | 0
7563 | 878.4 | 0 | 0 | 0 | 0 | 1394.3 | 0 | 0 | 0 | 1045296 | 0
7564 | 985.6 | 0 | 0 | 0 | 0 | 1490.7 | 0 | 0 | 0 | 1172864 | 0
7565 | 1147.2 | 0 | 0 | 0 | 0 | 1508.35 | 0 | 0 | 0 | 1365168 | 0
7566 | 1303.2 | 0 | 0 | 0 | 0 | 1538.45 | 0 | 0 | 0 | 1550808 | 0
7567 | 1182.365 | 501.7084 | 501.7084 | 488.3933 | 488.3933 | 1779.7 | 911147.4956 | 175821.6042 | 79754.6333 | 1272050.0434 | 105317.0586
7568 | 1335.808 | 1387.6437 | 1387.6437 | 1350.8164 | 1335.808 | 1804.75 | 2530484.6138 | 480890.88 | 218137.4464 | 0 | 260816.512
7569 | 1230.58 | 2210.831 | 1278.3323 | 2152.1568 | 1230.58 | 1734.3 | 2243044.1097 | 443008.8 | 200953.714 | 0 | 326965.106
7570 | 1363.817 | 3516.2575 | 1416.7385 | 3422.9379 | 1363.817 | 1600.45 | 2298557.2597 | 490974.12 | 222711.3161 | 0 | 544913.0823
7571 | 1384.068 | 4000.7799 | 1437.7764 | 3894.6014 | 1384.068 | 1284.75 | 1876433.2373 | 498264.48 | 226018.3044 | 0 | 989954.637
7572 | 1456.248 | 4160.3507 | 1512.7573 | 4049.9372 | 1456.248 | 1153 | 1771721.166 | 524249.28 | 237805.2984 | 0 | 1233442.056
7573 | 1474.147 | 3851.1255 | 1531.3509 | 3748.9188 | 1474.147 | 1148.15 | 1782696.2763 | 530692.92 | 240728.2051 | 0 | 1255752.122
7574 | 1408.803 | 1455.4766 | 1455.4766 | 1416.849 | 1408.803 | 1578.45 | 2340729.7334 | 507169.08 | 230057.5299 | 0 | 584638.4209
7575 | 1416.215 | 323.3062 | 323.3062 | 314.7258 | 314.7258 | 1672.6 | 553132.1934 | 113301.2857 | 51394.7221 | 2019029.7151 | 100861.7906
7576 | 1598.239 | 759.5533 | 759.5533 | 739.3951 | 739.3951 | 1885.25 | 1464821.7198 | 266182.2456 | 120743.2242 | 1574260.82 | 83050.7715
7577 | 1617.779 | 555.8987 | 555.8987 | 541.1455 | 541.1455 | 1900.75 | 1080082.3484 | 194812.363 | 88369.0525 | 1973469.2918 | 52572.5265
7578 | 1347.526 | 0 | 0 | 0 | 0 | 1913.4 | 0 | 0 | 0 | 2470015.158 | 0
7579 | 1315.2 | 0 | 0 | 0 | 0 | 1913.15 | 0 | 0 | 0 | 4469049.6 | 0
7580 | 1236.8 | 0 | 0 | 0 | 0 | 1865.5 | 0 | 0 | 0 | 4202646.4 | 0
7581 | 1147.2 | 0 | 0 | 0 | 0 | 1849.6 | 0 | 0 | 0 | 3898185.6 | 0
7582 | 1199.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1837.85 | 597332.6506 | 111351.8261 | 50510.4255 | 3023844.0863 | 49597.4691
7583 | 1183.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1821.1 | 1145673.2824 | 215514.4963 | 97759.7701 | 1986296.2159 | 105908.8
7584 | 1420 | 0 | 0 | 0 | 0 | 1807.75 | 0 | 0 | 0 | 2602860 | 0
7585 | 1430.4 | 0 | 0 | 0 | 0 | 1794.85 | 0 | 0 | 0 | 1702176 | 0
7586 | 1165.6 | 0 | 0 | 0 | 0 | 1788.35 | 0 | 0 | 0 | 1387064 | 0
7587 | 1365.6 | 0 | 0 | 0 | 0 | 1785.3 | 0 | 0 | 0 | 1625064 | 0
7588 | 876.8 | 0 | 0 | 0 | 0 | 1783.55 | 0 | 0 | 0 | 1043392 | 0
7589 | 816 | 0 | 0 | 0 | 0 | 1784.95 | 0 | 0 | 0 | 971040 | 0
7590 | 768 | 0 | 0 | 0 | 0 | 1792.2 | 0 | 0 | 0 | 913920 | 0
7591 | 1244.499 | 421.0359 | 421.0359 | 409.8618 | 409.8618 | 1806.3 | 776757.6819 | 147550.2524 | 66930.434 | 1529889.965 | 77710.6967
7592 | 1277.595 | 1327.1718 | 1327.1718 | 1291.9493 | 1277.595 | 1829.9 | 2453115.4489 | 459934.2 | 208631.2635 | 0 | 217318.9095
7593 | 1546.546 | 1761.684 | 1606.5604 | 1714.9299 | 1546.546 | 1856.7 | 3021096.0102 | 556756.56 | 252550.9618 | 0 | 221620.0418
7594 | 1572.208 | 3419.5697 | 1633.2171 | 3328.8162 | 1572.208 | 1870.1 | 3094751.6941 | 565994.88 | 256741.5664 | 0 | 204229.8192
7595 | 1429.627 | 3766.5138 | 1485.1033 | 3666.5526 | 1429.627 | 1849.15 | 2783831.0709 | 514665.72 | 233458.0891 | 0 | 215659.233
7596 | 1773.524 | 1846.1555 | 1842.3452 | 1797.1595 | 1773.524 | 1689.95 | 3158692.9607 | 638468.64 | 289616.4692 | 0 | 545422.5972
7597 | 1456.594 | 1513.1168 | 1513.1168 | 1472.9595 | 1456.594 | 1573.15 | 2415077.4107 | 524373.84 | 237861.8002 | 0 | 614084.7645
7598 | 1568.38 | 1629.2406 | 1629.2406 | 1586.0014 | 1568.38 | 1839.75 | 3040519.1196 | 564616.8 | 256116.454 | 0 | 251332.895
7599 | 1614.354 | 1829.5969 | 1676.9986 | 1781.0404 | 1614.354 | 1882.15 | 3196285.1754 | 581167.44 | 263624.0082 | 0 | 190251.6189
7600 | 1835.767 | 1701.3222 | 1701.3222 | 1656.17 | 1656.17 | 1889.85 | 3287752.8422 | 596221.2179 | 270452.5691 | 329201.2097 | 178568.1304
7601 | 1488.288 | 294.5759 | 294.5759 | 286.7581 | 286.7581 | 1900.75 | 573058.4266 | 103232.8999 | 46827.5904 | 2202404.3888 | 27858.7803
7602 | 1561.284 | 0 | 0 | 0 | 0 | 1913.4 | 0 | 0 | 0 | 2861833.572 | 0
7603 | 1532 | 0 | 0 | 0 | 0 | 1913.15 | 0 | 0 | 0 | 5205736 | 0
7604 | 1440.8 | 0 | 0 | 0 | 0 | 1865.5 | 0 | 0 | 0 | 4895838.4 | 0
7605 | 1496.8 | 0 | 0 | 0 | 0 | 1849.6 | 0 | 0 | 0 | 5086126.4 | 0
7606 | 967.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1837.85 | 597510.3581 | 111351.8261 | 50510.4255 | 2235508.0863 | 49597.4691
7607 | 1389.6 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1821.1 | 1149725.3141 | 215514.4963 | 97759.7701 | 2687643.4159 | 105908.8
7608 | 994.4 | 0 | 0 | 0 | 0 | 1807.75 | 0 | 0 | 0 | 1822735.2 | 0
7609 | 1131.2 | 0 | 0 | 0 | 0 | 1794.85 | 0 | 0 | 0 | 1346128 | 0
7610 | 1332.8 | 0 | 0 | 0 | 0 | 1788.35 | 0 | 0 | 0 | 1586032 | 0
7611 | 1132.8 | 0 | 0 | 0 | 0 | 1785.3 | 0 | 0 | 0 | 1348032 | 0
7612 | 1163.2 | 0 | 0 | 0 | 0 | 1784.45 | 0 | 0 | 0 | 1384208 | 0
7613 | 1312.8 | 0 | 0 | 0 | 0 | 1785.85 | 0 | 0 | 0 | 1562232 | 0
7614 | 1239.2 | 0 | 0 | 0 | 0 | 1792.2 | 0 | 0 | 0 | 1474648 | 0
7615 | 1053.267 | 380.7843 | 380.7843 | 370.6785 | 370.6785 | 1806.3 | 703892.4386 | 133444.2462 | 60531.7928 | 1251184.7908 | 70281.7206
7616 | 1323.515 | 1350.7817 | 1350.7817 | 1314.9327 | 1314.9327 | 1826.75 | 2521014.944 | 473375.7708 | 214728.5094 | 15731.362 | 222993.0203
7617 | 1381.943 | 1797.8926 | 1435.569 | 1750.1775 | 1381.943 | 1860.8 | 2701078.9499 | 497499.48 | 225671.2919 | 0 | 192366.4656
7618 | 1401.676 | 3042.0452 | 1456.0677 | 2961.311 | 1401.676 | 1871.1 | 2756757.3181 | 504603.36 | 228893.6908 | 0 | 180676.0364
7619 | 1376.532 | 3872.0554 | 1429.948 | 3769.2931 | 1376.532 | 1858.2 | 2694313.3297 | 495551.52 | 224787.6756 | 0 | 195192.2376
7620 | 1661.105 | 4023.4778 | 1725.5638 | 3916.6969 | 1661.105 | 1830 | 3200201.7161 | 597997.8 | 271258.4465 | 0 | 282387.85
7621 | 1751.024 | 3929.8887 | 1818.972 | 3825.5916 | 1751.024 | 1840.45 | 3396407.3791 | 630368.64 | 285942.2192 | 0 | 279375.8792
7622 | 1832.523 | 3567.0529 | 1903.6336 | 3472.3853 | 1832.523 | 1857.65 | 3584365.4009 | 659708.28 | 299251.0059 | 0 | 260859.6491
7623 | 1589.617 | 2331.7427 | 1651.3017 | 2269.8595 | 1589.617 | 1873.9 | 3130241.4745 | 572262.12 | 259584.4561 | 0 | 200450.7037
7624 | 1620.881 | 1553.1232 | 1553.1232 | 1511.9042 | 1511.9042 | 1889.85 | 2999192.3808 | 544285.5007 | 246893.9507 | 199754.5318 | 163013.4083
7625 | 1347.911 | 550.8418 | 550.8418 | 536.2228 | 536.2228 | 1900.75 | 1069198.9445 | 193040.1932 | 87565.1765 | 1487824.5461 | 52094.34
7626 | 1547.415 | 0 | 0 | 0 | 0 | 1913.4 | 0 | 0 | 0 | 2836411.695 | 0
7627 | 1665.6 | 0 | 0 | 0 | 0 | 1913.15 | 0 | 0 | 0 | 5659708.8 | 0
7628 | 1189.6 | 0 | 0 | 0 | 0 | 1865.5 | 0 | 0 | 0 | 4042260.8 | 0
7629 | 890.4 | 0 | 0 | 0 | 0 | 1849.6 | 0 | 0 | 0 | 3025579.2 | 0
7630 | 993.6 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1837.85 | 597409.0097 | 111351.8261 | 50510.4255 | 2325215.2863 | 49597.4691
7631 | 1250.4 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1821.1 | 1146409.9861 | 215514.4963 | 97759.7701 | 2214641.8159 | 105908.8
7632 | 1127.2 | 0 | 0 | 0 | 0 | 1807.75 | 0 | 0 | 0 | 2066157.6 | 0
7633 | 1052 | 0 | 0 | 0 | 0 | 1794.85 | 0 | 0 | 0 | 1251880 | 0
7634 | 1386.4 | 0 | 0 | 0 | 0 | 1788.35 | 0 | 0 | 0 | 1649816 | 0
7635 | 1046.4 | 0 | 0 | 0 | 0 | 1785.3 | 0 | 0 | 0 | 1245216 | 0
7636 | 1260 | 0 | 0 | 0 | 0 | 1784.45 | 0 | 0 | 0 | 1499400 | 0
7637 | 1321.6 | 0 | 0 | 0 | 0 | 1785.85 | 0 | 0 | 0 | 1572704 | 0
7638 | 721.6 | 0 | 0 | 0 | 0 | 1792.2 | 0 | 0 | 0 | 858704 | 0
7639 | 904.057 | 244.8993 | 244.8993 | 238.3998 | 238.3998 | 1806.3 | 453389.797 | 85823.9156 | 38930.6817 | 1220149.711 | 45201.0572
7640 | 979.12 | 1056.3772 | 1017.1145 | 1028.3415 | 979.12 | 1826.25 | 1880675.904 | 352483.2 | 159890.296 | 0 | 170122.1
7641 | 1105.275 | 1816.6815 | 1148.1649 | 1768.4677 | 1105.275 | 1853.6 | 2153721.5769 | 397899 | 180491.4075 | 0 | 161812.26
7642 | 1633.544 | 2030.962 | 1696.9333 | 1977.0613 | 1633.544 | 1826 | 3139102.8807 | 588075.84 | 266757.7352 | 0 | 284236.656
7643 | 1559.029 | 3641.9238 | 1619.5267 | 3545.2691 | 1559.029 | 1625.25 | 2670995.1835 | 561250.44 | 254589.4357 | 0 | 584246.1178
7644 | 1491.985 | 2604.4134 | 1549.8811 | 2535.2936 | 1491.985 | 1359.95 | 2139321.8139 | 537114.6 | 243641.1505 | 0 | 954944.9993
7645 | 1664.025 | 2453.7482 | 1728.5971 | 2388.6271 | 1664.025 | 1414.4 | 2479466.2149 | 599049 | 271735.2825 | 0 | 974453.04
7646 | 1509.416 | 2322.2916 | 1567.9885 | 2260.6593 | 1509.416 | 1530.45 | 2431914.511 | 543389.76 | 246487.6328 | 0 | 708746.2828
7647 | 1181.19 | 2465.789 | 1227.0258 | 2400.3483 | 1181.19 | 1644.7 | 2046548.2903 | 425228.4 | 192888.327 | 0 | 419676.807
7648 | 1646.173 | 1964.921 | 1710.0523 | 1912.7731 | 1646.173 | 1863.25 | 3223536.9232 | 592622.28 | 268820.0509 | 0 | 225114.1577
7649 | 1321.611 | 757.1754 | 757.1754 | 737.0804 | 737.0804 | 1900.75 | 1470809.1936 | 265348.9471 | 120365.2307 | 1071444.574 | 71607.7832
7650 | 1456.398 | 0 | 0 | 0 | 0 | 1913.4 | 0 | 0 | 0 | 2669577.534 | 0
7651 | 1341.6 | 0 | 0 | 0 | 0 | 1913.15 | 0 | 0 | 0 | 4558756.8 | 0
7652 | 1266.4 | 0 | 0 | 0 | 0 | 1865.5 | 0 | 0 | 0 | 4303227.2 | 0
7653 | 1124.8 | 0 | 0 | 0 | 0 | 1849.6 | 0 | 0 | 0 | 3822070.4 | 0
7654 | 1446.4 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1837.85 | 595795.2401 | 111351.8261 | 50510.4255 | 3863829.6863 | 49597.4691
7655 | 1150.4 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1821.1 | 1143894.8732 | 215514.4963 | 97759.7701 | 1874841.8159 | 105908.8
7656 | 1467.2 | 0 | 0 | 0 | 0 | 1807.75 | 0 | 0 | 0 | 2689377.6 | 0
7657 | 1057.6 | 0 | 0 | 0 | 0 | 1794.85 | 0 | 0 | 0 | 1938580.8 | 0
7658 | 1108 | 0 | 0 | 0 | 0 | 1788.35 | 0 | 0 | 0 | 2030964 | 0
7659 | 1446.4 | 0 | 0 | 0 | 0 | 1785.3 | 0 | 0 | 0 | 2651251.2 | 0
7660 | 1334.4 | 0 | 0 | 0 | 0 | 1784.45 | 0 | 0 | 0 | 2445955.2 | 0
7661 | 826.4 | 0 | 0 | 0 | 0 | 1785.85 | 0 | 0 | 0 | 1514791.2 | 0
7662 | 1045.6 | 0 | 0 | 0 | 0 | 1792.2 | 0 | 0 | 0 | 1916584.8 | 0
7663 | 960.752 | 498.7987 | 498.7987 | 485.5609 | 485.5609 | 1806.3 | 922876.9717 | 174801.9149 | 79292.0908 | 871025.3328 | 92063.4793
7664 | 891.267 | 1147.8138 | 925.8524 | 1117.3514 | 891.267 | 1829.85 | 1713587.6417 | 320856.12 | 145543.9011 | 0 | 151649.08
7665 | 1021.024 | 2393.4446 | 1060.6446 | 2329.9239 | 1021.024 | 1859.8 | 1996210.9744 | 367568.64 | 166733.2192 | 0 | 143147.5648
7666 | 1278.022 | 3553.5391 | 1327.6153 | 3459.2301 | 1278.022 | 1863.9 | 2509692.124 | 460087.92 | 208700.9926 | 0 | 173938.7942
7667 | 1410.682 | 4038.3981 | 1465.4232 | 3931.2212 | 1410.682 | 1665.75 | 2478964.939 | 507845.52 | 230364.3706 | 0 | 471520.4585
7668 | 1375.315 | 3674.6939 | 1428.6838 | 3577.1695 | 1375.315 | 1738.45 | 2515071.2316 | 495113.4 | 224588.9395 | 0 | 359713.6382
7669 | 1500.064 | 3701.1938 | 1558.2736 | 3602.9661 | 1500.064 | 1582.85 | 2506374.2344 | 540023.04 | 244960.4512 | 0 | 625751.6976
7670 | 1347.201 | 2327.2301 | 1399.4788 | 2265.4667 | 1347.201 | 1740.85 | 2475521.3076 | 484992.36 | 219997.9233 | 0 | 349127.1392
7671 | 1165.374 | 2898.1853 | 1210.596 | 2821.269 | 1165.374 | 1877.5 | 2305090.9058 | 419534.64 | 190305.5742 | 0 | 142758.315
7672 | 1265.572 | 1709.3823 | 1314.6822 | 1664.0162 | 1265.572 | 1889.85 | 2518233.3185 | 455605.92 | 206667.9076 | 0 | 139402.7558
7673 | 1012.197 | 234.4956 | 234.4956 | 228.2722 | 228.2722 | 1900.75 | 456384.8886 | 82178.0073 | 37276.8572 | 1436934.0805 | 22176.817
7674 | 1011.616 | 0 | 0 | 0 | 0 | 1913.4 | 0 | 0 | 0 | 1854292.128 | 0
7675 | 971.2 | 0 | 0 | 0 | 0 | 1913.15 | 0 | 0 | 0 | 1780209.6 | 0
7676 | 1312 | 0 | 0 | 0 | 0 | 1865.5 | 0 | 0 | 0 | 2404896 | 0
7677 | 1095.2 | 0 | 0 | 0 | 0 | 1849.6 | 0 | 0 | 0 | 2007501.6 | 0
7678 | 1071.2 | 0 | 0 | 0 | 0 | 1837.85 | 0 | 0 | 0 | 1963509.6 | 0
7679 | 1172 | 0 | 0 | 0 | 0 | 1821.1 | 0 | 0 | 0 | 2148276 | 0
7680 | 1040 | 521.3179 | 521.3179 | 507.4824 | 507.4824 | 1807.75 | 965274.5445 | 182693.6771 | 82871.8819 | 976104.694 | 95522.4885
7681 | 1044 | 0 | 0 | 0 | 0 | 1794.4 | 0 | 0 | 0 | 1242360 | 0
7682 | 1136.8 | 0 | 0 | 0 | 0 | 1793.1 | 0 | 0 | 0 | 1352792 | 0
7683 | 1080.8 | 0 | 0 | 0 | 0 | 1790.15 | 0 | 0 | 0 | 1286152 | 0
7684 | 1034.4 | 0 | 0 | 0 | 0 | 1788.75 | 0 | 0 | 0 | 1230936 | 0
7685 | 1055.2 | 0 | 0 | 0 | 0 | 1789.5 | 0 | 0 | 0 | 1255688 | 0
7686 | 1076 | 0 | 0 | 0 | 0 | 1793.8 | 0 | 0 | 0 | 1280440 | 0
7687 | 886.193 | 920.5815 | 920.5815 | 896.1498 | 886.193 | 1803.8 | 1681477.5122 | 319029.48 | 144715.3169 | 0 | 173871.0666
7688 | 293.458 | 1163.3855 | 304.8456 | 1132.5099 | 293.458 | 1826.45 | 563144.5662 | 105644.88 | 47921.6914 | 0 | 50929.6359
7689 | 141.382 | 2362.3957 | 146.8683 | 2299.699 | 141.382 | 1855.45 | 275276.1689 | 50897.52 | 23087.6806 | 0 | 20436.7681
7690 | 225.957 | 3463.2202 | 234.7252 | 3371.3083 | 225.957 | 1845.05 | 437546.6164 | 81344.52 | 36898.7781 | 0 | 35012.0372
7691 | 173.99 | 3875.687 | 180.7416 | 3772.8284 | 173.99 | 1596.35 | 291472.1676 | 62636.4 | 28412.567 | 0 | 70231.0635
7692 | 186.914 | 2674.5005 | 194.1672 | 2603.5207 | 186.914 | 1274.4 | 251024.4008 | 67289.04 | 30523.0562 | 0 | 135624.7984
7693 | 144.11 | 3432.616 | 149.7022 | 3341.5163 | 144.11 | 1305.95 | 198078.3597 | 51879.6 | 23533.163 | 0 | 100019.5455
7694 | 135.505 | 3256.2602 | 140.7632 | 3169.8408 | 135.505 | 1718.2 | 244827.5782 | 48781.8 | 22127.9665 | 0 | 38185.309
7695 | 194.577 | 2943.0492 | 202.1275 | 2864.9422 | 194.577 | 1869.2 | 383098.4999 | 70047.72 | 31774.4241 | 0 | 25450.6716
7696 | 215.288 | 1322.0868 | 223.6422 | 1286.9993 | 215.288 | 1881.3 | 426683.6189 | 77503.68 | 35156.5304 | 0 | 25554.6856
7697 | 184.122 | 784.871 | 191.2668 | 764.041 | 184.122 | 1885.7 | 365673.3811 | 66283.92 | 30067.1226 | 0 | 21045.1446
7698 | 203.03 | 53.4714 | 53.4714 | 52.0523 | 52.0523 | 1886.9 | 103377.85 | 18738.8398 | 8500.146 | 276742.0639 | 5821.7094
7699 | 140 | 145.4327 | 145.4327 | 141.573 | 140 | 1888.75 | 278186.8267 | 50400 | 22862 | 0 | 15575
7700 | 197.6 | 205.2678 | 205.2678 | 199.8201 | 197.6 | 1844.45 | 383215.864 | 71136 | 32268.08 | 0 | 30736.68
7701 | 199.2 | 206.9299 | 206.9299 | 201.4381 | 199.2 | 1829.35 | 382794.7771 | 71712 | 32529.36 | 0 | 33993.48
7702 | 108.8 | 113.022 | 113.022 | 110.0224 | 108.8 | 1826.9 | 208914.3422 | 39168 | 17767.04 | 0 | 18833.28
7703 | 98.4 | 102.2184 | 102.2184 | 99.5056 | 98.4 | 1813.7 | 187693.5136 | 35424 | 16068.72 | 0 | 18331.92
7704 | 102.4 | 106.3736 | 106.3736 | 103.5505 | 102.4 | 1801.4 | 194018.0753 | 36864 | 16721.92 | 0 | 20336.64
7705 | 92.8 | 0 | 0 | 0 | 0 | 1781.75 | 0 | 0 | 0 | 110432 | 0
7706 | 99.2 | 0 | 0 | 0 | 0 | 1787.85 | 0 | 0 | 0 | 118048 | 0
7707 | 94.4 | 0 | 0 | 0 | 0 | 1784.25 | 0 | 0 | 0 | 112336 | 0
7708 | 98.4 | 0 | 0 | 0 | 0 | 1783.1 | 0 | 0 | 0 | 117096 | 0
7709 | 92.8 | 0 | 0 | 0 | 0 | 1783.25 | 0 | 0 | 0 | 110432 | 0
7710 | 93.6 | 0 | 0 | 0 | 0 | 1782.55 | 0 | 0 | 0 | 111384 | 0
7711 | 80.485 | 83.6082 | 83.6082 | 81.3893 | 80.485 | 1778.25 | 150510.781 | 28974.6 | 13143.2005 | 0 | 17847.5487
7712 | 100.984 | 1092.1983 | 104.9027 | 1063.2119 | 100.984 | 1439.75 | 153148.0581 | 36354.24 | 16490.6872 | 0 | 56576.286
7713 | 679.251 | 2691.2242 | 705.6092 | 2619.8006 | 679.251 | 1066.15 | 764717.0912 | 244530.36 | 110921.6883 | 0 | 634318.5463
7714 | 1271.683 | 3422.7806 | 1321.0303 | 3331.9419 | 1271.683 | 1043.05 | 1407882.8012 | 457805.88 | 207665.8339 | 0 | 1216937.0469
7715 | 1286.429 | 3713.1286 | 1336.3486 | 3614.5842 | 1286.429 | 1160.35 | 1586622.4742 | 463114.44 | 210073.8557 | 0 | 1080150.1098
7716 | 1324.926 | 2658.8395 | 1376.3394 | 2588.2753 | 1324.926 | 1171.3 | 1650617.5708 | 476973.36 | 216360.4158 | 0 | 1097966.1762
7717 | 1133.191 | 1681.0718 | 1177.1642 | 1636.457 | 1133.191 | 1176.35 | 1414104.4178 | 407948.76 | 185050.0903 | 0 | 933352.7671
7718 | 1217.422 | 1819.4187 | 1264.6638 | 1771.1324 | 1217.422 | 1146 | 1480524.8218 | 438271.92 | 198805.0126 | 0 | 1039678.388
7719 | 1214.924 | 531.8576 | 531.8576 | 517.7424 | 517.7424 | 1098.5 | 603157.8708 | 186387.2752 | 84547.339 | 1277933.8156 | 456872.0865
7720 | 1286.664 | 219.9773 | 219.9773 | 214.1392 | 214.1392 | 1349.5 | 305257.7145 | 77090.1178 | 34968.934 | 1965937.929 | 136350.6545
7721 | 1421.989 | 7.6227 | 7.6227 | 7.4204 | 7.4204 | 1735.35 | 13552.6603 | 2671.3604 | 1211.7588 | 2592904.1602 | 1922.4176
7722 | 1335.966 | 0 | 0 | 0 | 0 | 1846.5 | 0 | 0 | 0 | 2448825.678 | 0
7723 | 1252.8 | 0 | 0 | 0 | 0 | 1859.9 | 0 | 0 | 0 | 4257014.4 | 0
7724 | 1186.4 | 0 | 0 | 0 | 0 | 1826.35 | 0 | 0 | 0 | 4031387.2 | 0
7725 | 1470.4 | 0 | 0 | 0 | 0 | 1815.85 | 0 | 0 | 0 | 4996419.2 | 0
7726 | 1188.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1809.05 | 588685.754 | 111351.8261 | 50510.4255 | 2988504.8863 | 58406.6403
7727 | 779.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1796.95 | 1133396.8108 | 215514.4963 | 97759.7701 | 613504.2159 | 120205.6
7728 | 1133.6 | 0 | 0 | 0 | 0 | 1777.65 | 0 | 0 | 0 | 2077888.8 | 0
7729 | 877.6 | 0 | 0 | 0 | 0 | 1660.75 | 0 | 0 | 0 | 1044344 | 0
7730 | 888 | 0 | 0 | 0 | 0 | 1347.35 | 0 | 0 | 0 | 1056720 | 0
7731 | 992 | 0 | 0 | 0 | 0 | 1022.8 | 0 | 0 | 0 | 1180480 | 0
7732 | 1028 | 0 | 0 | 0 | 0 | 1166.45 | 0 | 0 | 0 | 1223320 | 0
7733 | 1020 | 0 | 0 | 0 | 0 | 1120.4 | 0 | 0 | 0 | 1213800 | 0
7734 | 988.8 | 0 | 0 | 0 | 0 | 1520.55 | 0 | 0 | 0 | 1176672 | 0
7735 | 1027.129 | 435.4597 | 435.4597 | 423.9028 | 423.9028 | 1697.2 | 757081.6535 | 152605.0139 | 69223.3299 | 1105713.5946 | 125642.6208
7736 | 958.726 | 1021.278 | 995.9291 | 994.1739 | 958.726 | 1587.6 | 1600319.901 | 345141.36 | 156559.9558 | 0 | 395378.6024
7737 | 1015.72 | 2206.8524 | 1055.1348 | 2148.2837 | 1015.72 | 1665.45 | 1778227.6605 | 365659.2 | 165867.076 | 0 | 339809.126
7738 | 1081.252 | 3275.8116 | 1123.2097 | 3188.8733 | 1081.252 | 1441.8 | 1640841.5798 | 389250.72 | 176568.4516 | 0 | 603554.8664
7739 | 1456.647 | 3662.5222 | 1513.1718 | 3565.3209 | 1456.647 | 1050.25 | 1613358.1695 | 524392.92 | 237870.4551 | 0 | 1383450.4882
7740 | 1355.634 | 2371.6795 | 1408.239 | 2308.7365 | 1355.634 | 698.7 | 1000589.3718 | 488028.24 | 221375.0322 | 0 | 1764086.5242
7741 | 1091.508 | 2574.9196 | 1133.8637 | 2506.5826 | 1091.508 | 339.7 | 392173.5495 | 392942.88 | 178243.2564 | 0 | 1812230.7324
7742 | 1198.058 | 1894.9939 | 1244.5483 | 1844.7018 | 1198.058 | 1056.35 | 1337133.4226 | 431300.88 | 195642.8714 | 0 | 1130547.4317
7743 | 1592.282 | 509.9233 | 509.9233 | 496.3902 | 496.3902 | 1064.85 | 557278.6438 | 178700.4702 | 81060.5188 | 2008769.6787 | 454379.0983
7744 | 1106.455 | 149.8019 | 149.8019 | 145.8262 | 145.8262 | 1427.35 | 219195.9243 | 52497.4383 | 23813.4213 | 1760832.5586 | 81740.6337
7745 | 1246.387 | 20.2079 | 20.2079 | 19.6716 | 19.6716 | 1896.65 | 39239.3045 | 7081.7627 | 3212.3662 | 2248569.3961 | 1990.1076
7746 | 1322.503 | 0 | 0 | 0 | 0 | 1913.4 | 0 | 0 | 0 | 2424147.999 | 0
7747 | 1121.6 | 0 | 0 | 0 | 0 | 1913.15 | 0 | 0 | 0 | 3811196.8 | 0
7748 | 1195.2 | 0 | 0 | 0 | 0 | 1857.3 | 0 | 0 | 0 | 4061289.6 | 0
7749 | 1380 | 0 | 0 | 0 | 0 | 1827.1 | 0 | 0 | 0 | 4689240 | 0
7750 | 1388 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1837.85 | 597609.5474 | 111351.8261 | 50510.4255 | 3665386.4863 | 49597.4691
7751 | 1431.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1821.1 | 1146519.3983 | 215514.4963 | 97759.7701 | 2829000.2159 | 105908.8
7752 | 1104 | 0 | 0 | 0 | 0 | 1807.25 | 0 | 0 | 0 | 2023632 | 0
7753 | 1285.6 | 0 | 0 | 0 | 0 | 1793.85 | 0 | 0 | 0 | 1529864 | 0
7754 | 1016 | 0 | 0 | 0 | 0 | 1787.35 | 0 | 0 | 0 | 1209040 | 0
7755 | 1193.6 | 0 | 0 | 0 | 0 | 1777.1 | 0 | 0 | 0 | 1420384 | 0
7756 | 1489.6 | 0 | 0 | 0 | 0 | 1776.25 | 0 | 0 | 0 | 1772624 | 0
7757 | 1088.8 | 0 | 0 | 0 | 0 | 1777.65 | 0 | 0 | 0 | 1295672 | 0
7758 | 1126.4 | 0 | 0 | 0 | 0 | 1791.2 | 0 | 0 | 0 | 1340416 | 0
7759 | 799.087 | 238.4109 | 238.4109 | 232.0836 | 232.0836 | 1805.3 | 440509.2006 | 83550.092 | 37899.2501 | 1039317.2526 | 44230.7778
7760 | 933.699 | 969.931 | 969.931 | 944.1895 | 933.699 | 1826.75 | 1793729.4258 | 336131.64 | 152473.0467 | 0 | 161763.3518
7761 | 1028.874 | 2134.2005 | 1068.8002 | 2077.5599 | 1028.874 | 1857.2 | 2009802.7824 | 370394.64 | 168015.1242 | 0 | 146923.2072
7762 | 1429.183 | 2086.2877 | 1484.6421 | 2030.9187 | 1429.183 | 1654.1 | 2485520.1439 | 514505.88 | 233385.5839 | 0 | 494354.3997
7763 | 1309.361 | 2239.9217 | 1360.1704 | 2180.4754 | 1309.361 | 1050.25 | 1445309.4971 | 471369.96 | 213818.6513 | 0 | 1243565.6098
7764 | 1273.22 | 1522.2344 | 1322.627 | 1481.8351 | 1273.22 | 1040.45 | 1394648.8456 | 458359.2 | 207916.826 | 0 | 1221718.251
7765 | 1283.758 | 3154.3742 | 1333.5739 | 3070.6589 | 1283.758 | 1023.15 | 1387225.3723 | 462152.88 | 209637.6814 | 0 | 1254039.0023
7766 | 1017.049 | 2568.8291 | 1056.5153 | 2500.6538 | 1017.049 | 1217.3 | 1306704.9392 | 366137.64 | 166084.1017 | 0 | 796044.2523
7767 | 1569.862 | 1573.8868 | 1573.8868 | 1532.1167 | 1532.1167 | 1619.7 | 2616549.0375 | 551562.0273 | 250194.6641 | 69187.0568 | 570338.5721
7768 | 1212.909 | 114.844 | 114.844 | 111.7961 | 111.7961 | 1885.25 | 222184.655 | 40246.6041 | 18256.3068 | 2018339.9045 | 12557.2073
7769 | 1407.813 | 389.7917 | 389.7917 | 379.4469 | 379.4469 | 1900.75 | 759159.0296 | 136600.8783 | 61963.6762 | 1884995.0904 | 36863.435
7770 | 1339.188 | 0 | 0 | 0 | 0 | 1913.4 | 0 | 0 | 0 | 2454731.604 | 0
7771 | 1444 | 0 | 0 | 0 | 0 | 1913.15 | 0 | 0 | 0 | 4906712 | 0
7772 | 1498.4 | 0 | 0 | 0 | 0 | 1865.5 | 0 | 0 | 0 | 5091563.2 | 0
7773 | 1683.2 | 0 | 0 | 0 | 0 | 1849.6 | 0 | 0 | 0 | 5719513.6 | 0
7774 | 1572 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1837.85 | 598518.9343 | 111351.8261 | 50510.4255 | 4290618.4863 | 49597.4691
7775 | 1266.4 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1821.1 | 1148643.8291 | 215514.4963 | 97759.7701 | 2269009.8159 | 105908.8
7776 | 1252.8 | 0 | 0 | 0 | 0 | 1807.25 | 0 | 0 | 0 | 2296382.4 | 0
7777 | 1118.4 | 0 | 0 | 0 | 0 | 1655.6 | 0 | 0 | 0 | 1330896 | 0
7778 | 1283.2 | 0 | 0 | 0 | 0 | 1780.15 | 0 | 0 | 0 | 1527008 | 0
7779 | 1369.6 | 0 | 0 | 0 | 0 | 1777.1 | 0 | 0 | 0 | 1629824 | 0
7780 | 1394.4 | 0 | 0 | 0 | 0 | 1776.25 | 0 | 0 | 0 | 1659336 | 0
7781 | 1285.6 | 0 | 0 | 0 | 0 | 1777.65 | 0 | 0 | 0 | 1529864 | 0
7782 | 1056 | 0 | 0 | 0 | 0 | 1790.7 | 0 | 0 | 0 | 1256640 | 0
7783 | 1040.324 | 236.7675 | 236.7675 | 230.4838 | 230.4838 | 1801.7 | 436900.5965 | 82974.1732 | 37638.0069 | 1484437.0602 | 44738.0664
7784 | 869.633 | 1003.9736 | 903.3789 | 977.3287 | 869.633 | 1823.15 | 1669557.7642 | 313067.88 | 142011.0689 | 0 | 153794.596
7785 | 1098.227 | 2225.0907 | 1140.8434 | 2166.038 | 1098.227 | 1853.6 | 2144810.3467 | 395361.72 | 179340.4691 | 0 | 160780.4328
7786 | 1314.622 | 3383.654 | 1365.6356 | 3293.8537 | 1314.622 | 1763 | 2441825.0379 | 473263.92 | 214677.7726 | 0 | 311565.414
7787 | 1099.177 | 3447.3411 | 1141.8303 | 3355.8505 | 1099.177 | 1292.65 | 1496806.9577 | 395703.72 | 179495.6041 | 0 | 777502.851
7788 | 1346.221 | 2317.643 | 1398.4608 | 2256.134 | 1346.221 | 1216.9 | 1728969.3661 | 484639.56 | 219837.8893 | 0 | 1054225.6651
7789 | 1404.829 | 1627.8579 | 1459.343 | 1584.6555 | 1404.829 | 1398.55 | 2069253.2055 | 505738.44 | 229408.5757 | 0 | 844934.4021
7790 | 1166.196 | 2669.8518 | 1211.4499 | 2598.9954 | 1166.196 | 1578.45 | 1940200.9741 | 419830.56 | 190439.8068 | 0 | 491609.9238
7791 | 1431.156 | 2391.7399 | 1486.6916 | 2328.2644 | 1431.156 | 1755.1 | 2647227.3181 | 515216.16 | 233707.7748 | 0 | 350490.1044
7792 | 1408.691 | 519.3556 | 519.3556 | 505.5722 | 505.5722 | 1885.25 | 1003728.7057 | 182005.9966 | 82559.9423 | 1655416.7371 | 56787.2505
7793 | 1490.436 | 200.2836 | 200.2836 | 194.9682 | 194.9682 | 1900.75 | 389634.7783 | 70188.5573 | 31838.3095 | 2374592.4505 | 18941.267
7794 | 1393.933 | 0 | 0 | 0 | 0 | 1913.4 | 0 | 0 | 0 | 2555079.189 | 0
7795 | 1680.8 | 0 | 0 | 0 | 0 | 1913.15 | 0 | 0 | 0 | 5711358.4 | 0
7796 | 1324.8 | 0 | 0 | 0 | 0 | 1861.4 | 0 | 0 | 0 | 4501670.4 | 0
7797 | 1534.4 | 0 | 0 | 0 | 0 | 1722.1 | 0 | 0 | 0 | 5213891.2 | 0
7798 | 1571.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1627.85 | 530419.8373 | 111351.8261 | 50510.4255 | 4287900.0863 | 113831.0091
7799 | 1176.8 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1774.75 | 1119365.4533 | 215514.4963 | 97759.7701 | 1964549.0159 | 133348
7800 | 1416.8 | 0 | 0 | 0 | 0 | 1693.9 | 0 | 0 | 0 | 2596994.4 | 0
7801 | 1240 | 0 | 0 | 0 | 0 | 1531.3 | 0 | 0 | 0 | 1475600 | 0
7802 | 1348.8 | 0 | 0 | 0 | 0 | 1417.35 | 0 | 0 | 0 | 1605072 | 0
7803 | 1515.2 | 0 | 0 | 0 | 0 | 1468.2 | 0 | 0 | 0 | 1803088 | 0
7804 | 1366.4 | 0 | 0 | 0 | 0 | 1378.45 | 0 | 0 | 0 | 1626016 | 0
7805 | 1381.6 | 0 | 0 | 0 | 0 | 1319.35 | 0 | 0 | 0 | 1644104 | 0
7806 | 1362.4 | 0 | 0 | 0 | 0 | 1514.7 | 0 | 0 | 0 | 1621256 | 0
7807 | 679.439 | 266.9406 | 266.9406 | 259.8562 | 259.8562 | 1540.5 | 421073.8748 | 93548.2172 | 42434.5108 | 769095.3477 | 116877.9605
7808 | 1137.376 | 1181.5116 | 1181.5116 | 1150.1549 | 1137.376 | 1565.55 | 1874135.0896 | 409455.36 | 185733.5008 | 0 | 494133.0032
7809 | 882.651 | 2269.7468 | 916.902 | 2209.509 | 882.651 | 1623.9 | 1509182.5782 | 317754.36 | 144136.9083 | 0 | 331965.0411
7810 | 432.662 | 2773.8788 | 449.4513 | 2700.2615 | 432.662 | 1422 | 648091.9155 | 155758.32 | 70653.7046 | 0 | 250078.636
7811 | 389.328 | 3422.3786 | 404.4358 | 3331.5505 | 389.328 | 1058 | 433595.7182 | 140158.08 | 63577.2624 | 0 | 366746.976
7812 | 396.46 | 3997.7694 | 411.8445 | 3891.6708 | 396.46 | 706.5 | 295351.3954 | 142725.6 | 64741.918 | 0 | 512821.01
7813 | 851.215 | 2671.1877 | 884.2462 | 2600.2959 | 851.215 | 681.4 | 610531.4338 | 306437.4 | 139003.4095 | 0 | 1122412.099
7814 | 1358.284 | 3046.1536 | 1410.9919 | 2965.3104 | 1358.284 | 1169.8 | 1670459.6002 | 488982.24 | 221807.7772 | 0 | 1127647.3768
7815 | 1653.136 | 2480.5504 | 1717.2855 | 2414.718 | 1653.136 | 1598.35 | 2768902.9792 | 595128.96 | 269957.1088 | 0 | 663982.0744
7816 | 1480.775 | 1520.004 | 1520.004 | 1479.664 | 1479.664 | 1780.75 | 2768018.8913 | 532679.0258 | 241629.1248 | 2036.5354 | 317553.807
7817 | 1522.428 | 686.8577 | 686.8577 | 668.6289 | 668.6289 | 1900.25 | 1334979.4088 | 240706.3934 | 109187.0946 | 1565013.804 | 65284.8787
7818 | 1682.404 | 0 | 0 | 0 | 0 | 1913.4 | 0 | 0 | 0 | 3083846.532 | 0
7819 | 1758.4 | 0 | 0 | 0 | 0 | 1913.15 | 0 | 0 | 0 | 5975043.2 | 0
7820 | 1597.6 | 0 | 0 | 0 | 0 | 1865 | 0 | 0 | 0 | 5428644.8 | 0
7821 | 1777.6 | 0 | 0 | 0 | 0 | 1824.1 | 0 | 0 | 0 | 6040284.8 | 0
7822 | 1849.6 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1837.85 | 598131.0024 | 111351.8261 | 50510.4255 | 5233903.2863 | 49597.4691
7823 | 1356 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1820.6 | 1149154.1855 | 215514.4963 | 97759.7701 | 2573470.6159 | 106204.8
7824 | 1280.8 | 0 | 0 | 0 | 0 | 1793.8 | 0 | 0 | 0 | 2347706.4 | 0
7825 | 1248.8 | 0 | 0 | 0 | 0 | 1615.8 | 0 | 0 | 0 | 2289050.4 | 0
7826 | 1583.2 | 0 | 0 | 0 | 0 | 1553.35 | 0 | 0 | 0 | 2902005.6 | 0
7827 | 1660 | 0 | 0 | 0 | 0 | 1544.8 | 0 | 0 | 0 | 3042780 | 0
7828 | 981.6 | 0 | 0 | 0 | 0 | 1518.65 | 0 | 0 | 0 | 1799272.8 | 0
7829 | 1345.6 | 0 | 0 | 0 | 0 | 1522.95 | 0 | 0 | 0 | 2466484.8 | 0
7830 | 1347.2 | 0 | 0 | 0 | 0 | 1582.2 | 0 | 0 | 0 | 2469417.6 | 0
7831 | 1080.957 | 400.3128 | 400.3128 | 389.6887 | 389.6887 | 1596.3 | 652872.5714 | 140287.9236 | 63636.1609 | 1267094.8368 | 153989.3465
7832 | 1190.482 | 1236.6784 | 1236.6784 | 1203.8576 | 1190.482 | 1593.45 | 1995708.9485 | 428573.52 | 194405.7106 | 0 | 483990.4571
7833 | 1061.094 | 2029.1825 | 1102.2695 | 1975.3291 | 1061.094 | 1596 | 1781693.6183 | 381993.84 | 173276.6502 | 0 | 428681.976
7834 | 1659.705 | 3319.1017 | 1724.1094 | 3231.0145 | 1659.705 | 1422 | 2487944.3194 | 597493.8 | 271029.8265 | 0 | 959309.49
7835 | 1735.038 | 3802.7671 | 1802.3657 | 3701.8437 | 1735.038 | 1065.75 | 1950957.0431 | 624613.68 | 283331.7054 | 0 | 1620959.2515
7836 | 1837.293 | 3813.2943 | 1908.5887 | 3712.0916 | 1837.293 | 698.75 | 1352605.7766 | 661425.48 | 300029.9469 | 0 | 2390777.5162
7837 | 1536.804 | 2493.8741 | 1596.4393 | 2427.6881 | 1536.804 | 681.45 | 1100352.7623 | 553249.44 | 250960.0932 | 0 | 2026352.9142
7838 | 1437.913 | 1034.3763 | 1034.3763 | 1006.9245 | 1006.9245 | 1096.1 | 1162237.7263 | 362492.8344 | 164430.7774 | 790001.8473 | 890906.4375
7839 | 1704.969 | 1723.215 | 1723.215 | 1677.4818 | 1677.4818 | 1490.05 | 2635968.9691 | 603893.4612 | 273932.7839 | 50383.9705 | 837336.8801
7840 | 1445.753 | 774.001 | 774.001 | 753.4594 | 753.4594 | 1651.95 | 1310765.2319 | 271245.38 | 123039.9182 | 1268974.189 | 256694.1841
7841 | 1513.323 | 398.8699 | 398.8699 | 388.2841 | 388.2841 | 1808.9 | 738886.4053 | 139782.2654 | 63406.7887 | 2062196.3576 | 72631.377
7842 | 1805.698 | 0 | 0 | 0 | 0 | 1913.4 | 0 | 0 | 0 | 3309844.434 | 0
7843 | 1423.2 | 0 | 0 | 0 | 0 | 1912.65 | 0 | 0 | 0 | 2608725.6 | 0
7844 | 1600 | 0 | 0 | 0 | 0 | 1627.6 | 0 | 0 | 0 | 2932800 | 0
7845 | 1737.6 | 0 | 0 | 0 | 0 | 1577.95 | 0 | 0 | 0 | 3185020.8 | 0
7846 | 1408 | 0 | 0 | 0 | 0 | 1724 | 0 | 0 | 0 | 2580864 | 0
7847 | 1577.6 | 0 | 0 | 0 | 0 | 1577.35 | 0 | 0 | 0 | 2891740.8 | 0
7848 | 1420.8 | 382.9616 | 382.9616 | 372.798 | 372.798 | 1490.65 | 585490.7488 | 134207.284 | 60877.9152 | 1920987.6456 | 185764.5291
7849 | 1040 | 0 | 0 | 0 | 0 | 1626.4 | 0 | 0 | 0 | 1237600 | 0
7850 | 1061.6 | 0 | 0 | 0 | 0 | 1596.75 | 0 | 0 | 0 | 1263304 | 0
7851 | 848 | 0 | 0 | 0 | 0 | 1570.15 | 0 | 0 | 0 | 1009120 | 0
7852 | 1101.6 | 0 | 0 | 0 | 0 | 1550.85 | 0 | 0 | 0 | 1310904 | 0
7853 | 727.2 | 0 | 0 | 0 | 0 | 1551.6 | 0 | 0 | 0 | 865368 | 0
7854 | 904 | 0 | 0 | 0 | 0 | 1558.8 | 0 | 0 | 0 | 1075760 | 0
7855 | 917.901 | 953.5199 | 953.5199 | 928.214 | 917.901 | 1568.8 | 1509420.4891 | 330444.36 | 149893.2333 | 0 | 395798.9112
7856 | 910.899 | 946.2462 | 946.2462 | 921.1333 | 910.899 | 1561.15 | 1488764.8497 | 327923.64 | 148749.8067 | 0 | 399748.0261
7857 | 920.17 | 1614.3213 | 955.877 | 1571.4781 | 920.17 | 1590.65 | 1534439.6648 | 331261.2 | 150263.761 | 0 | 376671.5895
7858 | 1061.386 | 2847.6339 | 1102.5728 | 2772.0593 | 1061.386 | 1577.1 | 1756342.4417 | 382098.96 | 173324.3338 | 0 | 448860.1394
7859 | 1019.092 | 3465.3851 | 1058.6376 | 3373.4157 | 1019.092 | 1330.85 | 1426676.8486 | 366873.12 | 166417.7236 | 0 | 681925.4118
7860 | 991.068 | 2304.1718 | 1029.5261 | 2243.0203 | 991.068 | 1218.85 | 1269728.6017 | 356784.48 | 161841.4044 | 0 | 774172.7682
7861 | 1143.278 | 2484.8262 | 1187.6426 | 2418.8802 | 1143.278 | 1306.9 | 1567364.0418 | 411580.08 | 186697.2974 | 0 | 792405.9818
7862 | 1101.732 | 2656.3266 | 1144.4844 | 2585.8291 | 1101.732 | 1561.15 | 1811609.8283 | 396623.52 | 179912.8356 | 0 | 483495.0882
7863 | 1117.132 | 1548.7644 | 1160.482 | 1507.661 | 1117.132 | 1599.9 | 1887252.3105 | 402167.52 | 182427.6556 | 0 | 446964.5132
7864 | 520.632 | 1040.178 | 540.835 | 1012.5723 | 520.632 | 1644.9 | 903319.8765 | 187427.52 | 85019.2056 | 0 | 184876.4232
7865 | 192.296 | 490.5132 | 199.758 | 477.4953 | 192.296 | 1675.7 | 339288.6406 | 69226.56 | 31401.9368 | 0 | 62361.5928
7866 | 257.187 | 116.6308 | 116.6308 | 113.5354 | 113.5354 | 1589.6 | 190434.2785 | 40872.7611 | 18540.3386 | 263313.2959 | 46077.2496
7867 | 150.4 | 156.2362 | 156.2362 | 152.0898 | 150.4 | 1571.65 | 249626.5219 | 54144 | 24560.32 | 0 | 64423.84
7868 | 158.4 | 164.5467 | 164.5467 | 160.1797 | 158.4 | 1528.85 | 256209.1832 | 57024 | 25866.72 | 0 | 74630.16
7869 | 125.6 | 130.4739 | 130.4739 | 127.0112 | 125.6 | 1542.5 | 204602.9601 | 45216 | 20510.48 | 0 | 57462
7870 | 120 | 124.6566 | 124.6566 | 121.3483 | 120 | 1616.9 | 204130.0083 | 43200 | 19596 | 0 | 45972
7871 | 115.2 | 119.6703 | 119.6703 | 116.4943 | 115.2 | 1603.7 | 194700.9293 | 41472 | 18812.16 | 0 | 45653.76
7872 | 116 | 120.5014 | 120.5014 | 117.3033 | 116 | 1553.5 | 190207.3144 | 41760 | 18942.8 | 0 | 51794
7873 | 107.2 | 0 | 0 | 0 | 0 | 1350.35 | 0 | 0 | 0 | 127568 | 0
7874 | 117.6 | 0 | 0 | 0 | 0 | 1471.75 | 0 | 0 | 0 | 139944 | 0
7875 | 96.8 | 0 | 0 | 0 | 0 | 1344.25 | 0 | 0 | 0 | 115192 | 0
7876 | 103.2 | 0 | 0 | 0 | 0 | 1323.1 | 0 | 0 | 0 | 122808 | 0
7877 | 96.8 | 0 | 0 | 0 | 0 | 1201.65 | 0 | 0 | 0 | 115192 | 0
7878 | 101.6 | 0 | 0 | 0 | 0 | 1200.95 | 0 | 0 | 0 | 120904 | 0
7879 | 87.682 | 91.0845 | 91.0845 | 88.6671 | 87.682 | 1200.25 | 111014.8755 | 31565.52 | 14318.4706 | 0 | 70123.6795
7880 | 158.372 | 611.0592 | 164.5176 | 594.8421 | 158.372 | 1206.6 | 200535.637 | 57013.92 | 25862.1476 | 0 | 125652.3448
7881 | 720.376 | 1987.9949 | 748.33 | 1935.2346 | 720.376 | 1277.95 | 966909.675 | 259335.36 | 117637.4008 | 0 | 520147.4908
7882 | 958.609 | 3373.9838 | 995.8076 | 3284.4401 | 958.609 | 1149.9 | 1160765.954 | 345099.24 | 156540.8497 | 0 | 814913.5109
7883 | 1110.708 | 3624.1228 | 1153.8087 | 3527.9406 | 1110.708 | 1088.95 | 1275418.9622 | 399854.88 | 181378.6164 | 0 | 1011910.5234
7884 | 1168.124 | 3363.8596 | 1213.4528 | 3274.5846 | 1168.124 | 1139 | 1408487.1805 | 420524.64 | 190754.6492 | 0 | 1005754.764
7885 | 1171.326 | 3207.7418 | 1216.779 | 3122.6101 | 1171.326 | 1016.65 | 1257019.8243 | 421677.36 | 191277.5358 | 0 | 1151823.4221
7886 | 1171.349 | 2880.0643 | 1216.8029 | 2803.629 | 1171.349 | 1019.35 | 1257070.4703 | 421685.64 | 191281.2917 | 0 | 1148683.3968
7887 | 1266.465 | 2423.3092 | 1315.6099 | 2358.9959 | 1266.465 | 1027.1 | 1366695.6737 | 455927.4 | 206813.7345 | 0 | 1232143.7985
7888 | 1231.431 | 1781.6395 | 1279.2164 | 1734.3557 | 1231.431 | 1032.35 | 1330805.7485 | 443315.16 | 201092.6823 | 0 | 1191594.2071
7889 | 1227.897 | 590.0868 | 590.0868 | 574.4262 | 574.4262 | 1112.6 | 671246.9063 | 206793.44 | 93803.8021 | 1197811.9354 | 498962.835
7890 | 1118.58 | 0 | 0 | 0 | 0 | 1461.55 | 0 | 0 | 0 | 2050357.14 | 0
7891 | 1358.4 | 0 | 0 | 0 | 0 | 1650.9 | 0 | 0 | 0 | 4615843.2 | 0
7892 | 1066.4 | 0 | 0 | 0 | 0 | 1555.45 | 0 | 0 | 0 | 3623627.2 | 0
7893 | 1076 | 0 | 0 | 0 | 0 | 1500.25 | 0 | 0 | 0 | 3656248 | 0
7894 | 1006.4 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1530.05 | 498106.007 | 111351.8261 | 50510.4255 | 2368709.6863 | 143745.4863
7895 | 1079.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1484.4 | 936762.9062 | 215514.4963 | 97759.7701 | 1632904.2159 | 305235.2
7896 | 1528 | 0 | 0 | 0 | 0 | 1394.35 | 0 | 0 | 0 | 2800824 | 0
7897 | 1220.8 | 0 | 0 | 0 | 0 | 1538.85 | 0 | 0 | 0 | 1452752 | 0
7898 | 923.2 | 0 | 0 | 0 | 0 | 1367.35 | 0 | 0 | 0 | 1098608 | 0
7899 | 1218.4 | 0 | 0 | 0 | 0 | 1468.2 | 0 | 0 | 0 | 1449896 | 0
7900 | 1200.8 | 0 | 0 | 0 | 0 | 1340.45 | 0 | 0 | 0 | 1428952 | 0
7901 | 896 | 0 | 0 | 0 | 0 | 1087 | 0 | 0 | 0 | 1066240 | 0
7902 | 1284 | 0 | 0 | 0 | 0 | 1400.15 | 0 | 0 | 0 | 1527960 | 0
7903 | 1092.491 | 318.0664 | 318.0664 | 309.6251 | 309.6251 | 1527.55 | 497766.7404 | 111465.044 | 50561.7824 | 1434993.1541 | 143188.2562
7904 | 1306.162 | 1356.8473 | 1356.8473 | 1320.8373 | 1306.162 | 1593.45 | 2186889.8958 | 470218.32 | 213296.2546 | 0 | 531020.1611
7905 | 1409.71 | 1560.3564 | 1464.4134 | 1518.9454 | 1409.71 | 1836.35 | 2725969.848 | 507495.6 | 230205.643 | 0 | 230699.0415
7906 | 984.961 | 1668.2945 | 1023.1811 | 1624.0188 | 984.961 | 1763 | 1829132.0804 | 354585.96 | 160844.1313 | 0 | 233435.757
7907 | 1372.328 | 2740.8552 | 1425.5808 | 2668.1144 | 1372.328 | 1558.65 | 2263737.3773 | 494038.08 | 224101.1624 | 0 | 605676.9628
7908 | 1453.632 | 2956.1485 | 1510.0398 | 2877.6939 | 1453.632 | 1496.9 | 2301081.6907 | 523307.52 | 237378.1056 | 0 | 731322.2592
7909 | 1182.818 | 3016.4116 | 1228.717 | 2936.3577 | 1182.818 | 1381.65 | 1720155.5323 | 425814.48 | 193154.1794 | 0 | 731395.5103
7910 | 1278.412 | 2253.4584 | 1328.0205 | 2193.6528 | 1278.412 | 1474.3 | 1983897.9508 | 460228.32 | 208764.6796 | 0 | 672061.1884
7911 | 1247.998 | 1711.275 | 1296.4262 | 1665.8587 | 1247.998 | 1638.85 | 2153163.3309 | 449279.28 | 203798.0734 | 0 | 450714.4777
7912 | 1086.354 | 406.9123 | 406.9123 | 396.1131 | 396.1131 | 1764.35 | 735331.6047 | 142600.6999 | 64685.2619 | 1265211.6515 | 91369.5171
7913 | 1467.39 | 416.2688 | 416.2688 | 405.2213 | 405.2213 | 1896.65 | 808412.1326 | 145879.6511 | 66172.6306 | 1946955.3134 | 40993.6741
7914 | 1410.488 | 0 | 0 | 0 | 0 | 1912.9 | 0 | 0 | 0 | 2585424.504 | 0
7915 | 1142.4 | 0 | 0 | 0 | 0 | 1913.15 | 0 | 0 | 0 | 3881875.2 | 0
7916 | 984.8 | 0 | 0 | 0 | 0 | 1860.9 | 0 | 0 | 0 | 3346350.4 | 0
7917 | 1211.2 | 0 | 0 | 0 | 0 | 1828.6 | 0 | 0 | 0 | 4115657.6 | 0
7918 | 1125.6 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1837.85 | 596047.9465 | 111351.8261 | 50510.4255 | 2773751.2863 | 49597.4691
7919 | 1388.8 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1821.1 | 1146952.4933 | 215514.4963 | 97759.7701 | 2684925.0159 | 105908.8
7920 | 985.6 | 0 | 0 | 0 | 0 | 1803.15 | 0 | 0 | 0 | 1806604.8 | 0
7921 | 1293.6 | 0 | 0 | 0 | 0 | 1768.25 | 0 | 0 | 0 | 1539384 | 0
7922 | 1131.2 | 0 | 0 | 0 | 0 | 1658.35 | 0 | 0 | 0 | 1346128 | 0
7923 | 1264.8 | 0 | 0 | 0 | 0 | 1575.3 | 0 | 0 | 0 | 1505112 | 0
7924 | 774.4 | 0 | 0 | 0 | 0 | 1601.75 | 0 | 0 | 0 | 921536 | 0
7925 | 1108.8 | 0 | 0 | 0 | 0 | 1740.85 | 0 | 0 | 0 | 1319472 | 0
7926 | 734.4 | 0 | 0 | 0 | 0 | 1678.35 | 0 | 0 | 0 | 873936 | 0
7927 | 812.644 | 352.9059 | 352.9059 | 343.5399 | 343.5399 | 1762.45 | 634466.0922 | 123674.377 | 56100.0716 | 859867.7489 | 79881.6511
7928 | 1161.248 | 1206.3099 | 1206.3099 | 1174.2951 | 1161.248 | 1635 | 1988358.04 | 418049.28 | 189631.7984 | 0 | 423855.52
7929 | 1243.412 | 1644.3053 | 1291.6623 | 1600.6664 | 1243.412 | 1766.35 | 2302209.4981 | 447628.32 | 203049.1796 | 0 | 290523.2138
7930 | 1326.775 | 2628.0804 | 1378.2602 | 2558.3326 | 1326.775 | 1846.1 | 2581915.9969 | 477639 | 216662.3575 | 0 | 204190.6725
7931 | 1621.135 | 2946.4315 | 1684.0427 | 2868.2348 | 1621.135 | 1625.25 | 2779401.3191 | 583608.6 | 264731.3455 | 0 | 607520.3413
7932 | 1251.306 | 3231.4151 | 1299.8626 | 3145.6551 | 1251.306 | 1399.45 | 1846185.4136 | 450470.16 | 204338.2698 | 0 | 751471.8183
7933 | 1349.218 | 3214.5491 | 1401.5741 | 3129.2367 | 1349.218 | 1149.8 | 1633183.3676 | 485718.48 | 220327.2994 | 0 | 1147105.1436
7934 | 1331.273 | 2505.3301 | 1382.9327 | 2438.84 | 1331.273 | 1399.85 | 1954884.9868 | 479258.28 | 217396.8809 | 0 | 798963.491
7935 | 1282.735 | 2030.9152 | 1332.5112 | 1977.0158 | 1282.735 | 1607.1 | 2165160.7177 | 461784.6 | 209470.6255 | 0 | 503986.5815
7936 | 1437.172 | 715.3573 | 715.3573 | 696.3721 | 696.3721 | 1651.95 | 1206392.5814 | 250693.9614 | 113717.5664 | 1357886.1894 | 237245.4981
7937 | 1620.088 | 123.5253 | 123.5253 | 120.247 | 120.247 | 1795.25 | 226078.149 | 43288.9261 | 19636.3379 | 2749208.5218 | 24099.894
7938 | 1488.651 | 0 | 0 | 0 | 0 | 1912.9 | 0 | 0 | 0 | 2728697.283 | 0
7939 | 1304.8 | 0 | 0 | 0 | 0 | 1913.15 | 0 | 0 | 0 | 4433710.4 | 0
7940 | 1217.6 | 0 | 0 | 0 | 0 | 1851.55 | 0 | 0 | 0 | 4137404.8 | 0
7941 | 1169.6 | 0 | 0 | 0 | 0 | 1826.6 | 0 | 0 | 0 | 3974300.8 | 0
7942 | 1280 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1837.35 | 594899.106 | 111351.8261 | 50510.4255 | 3298402.4863 | 49750.4061
7943 | 1238.4 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1821.1 | 1144551.9694 | 215514.4963 | 97759.7701 | 2173865.8159 | 105908.8
7944 | 1456 | 0 | 0 | 0 | 0 | 1803.15 | 0 | 0 | 0 | 2668848 | 0
7945 | 1352 | 0 | 0 | 0 | 0 | 1717.35 | 0 | 0 | 0 | 1608880 | 0
7946 | 1226.4 | 0 | 0 | 0 | 0 | 1592 | 0 | 0 | 0 | 1459416 | 0
7947 | 1184 | 0 | 0 | 0 | 0 | 1507.8 | 0 | 0 | 0 | 1408960 | 0
7948 | 1292 | 0 | 0 | 0 | 0 | 1506.95 | 0 | 0 | 0 | 1537480 | 0
7949 | 1500 | 0 | 0 | 0 | 0 | 1508.35 | 0 | 0 | 0 | 1785000 | 0
7950 | 1428.8 | 0 | 0 | 0 | 0 | 1520.55 | 0 | 0 | 0 | 1700272 | 0
7951 | 1297.339 | 361.2568 | 361.2568 | 351.6693 | 351.6693 | 1540.5 | 566479.5399 | 126600.9328 | 57427.5898 | 1733412.6373 | 158173.685
7952 | 1310.033 | 1331.1826 | 1331.1826 | 1295.8537 | 1295.8537 | 1646.35 | 2229637.0529 | 466507.3384 | 211612.9121 | 25990.6245 | 448584.5133
7953 | 994.134 | 1594.6868 | 1032.7111 | 1552.3647 | 994.134 | 1835.2 | 1907331.2299 | 357888.24 | 162342.0822 | 0 | 163833.2832
7954 | 1147.17 | 2190.9608 | 1191.6856 | 2132.8139 | 1147.17 | 1816.6 | 2185674.1978 | 412981.2 | 187332.861 | 0 | 210390.978
7955 | 1266.559 | 2899.25 | 1315.7075 | 2822.3055 | 1266.559 | 1229.5 | 1637846.4773 | 455961.24 | 206829.0847 | 0 | 975883.7095
7956 | 1524.5 | 3367.3957 | 1583.6578 | 3278.0269 | 1524.5 | 356.45 | 570896.4741 | 548820 | 248950.85 | 0 | 2505591.975
7957 | 1553.979 | 3002.7036 | 1614.2808 | 2923.0134 | 1553.979 | 338.65 | 551878.9814 | 559432.44 | 253764.7707 | 0 | 2581703.0116
7958 | 1388.914 | 2300.351 | 1442.8105 | 2239.301 | 1388.914 | 753.85 | 1099134.9587 | 500009.04 | 226809.6562 | 0 | 1730795.1811
7959 | 1652.723 | 1215.6104 | 1215.6104 | 1183.3487 | 1183.3487 | 1585.3 | 1971345.6017 | 426005.5389 | 193240.8458 | 860363.0568 | 480354.0599
7960 | 1570.274 | 1285.8751 | 1285.8751 | 1251.7487 | 1251.7487 | 1763.5 | 2316775.559 | 450629.5263 | 204410.5601 | 583856.9041 | 289776.355
7961 | 1459.662 | 687.7448 | 687.7448 | 669.4925 | 669.4925 | 1875.3 | 1317078.62 | 241017.2877 | 109328.1197 | 1448380.7563 | 81719.7757
7962 | 1449.583 | 0 | 0 | 0 | 0 | 1912.4 | 0 | 0 | 0 | 2657085.639 | 0
7963 | 1372.8 | 0 | 0 | 0 | 0 | 1913.15 | 0 | 0 | 0 | 4664774.4 | 0
7964 | 1579.2 | 0 | 0 | 0 | 0 | 1843.65 | 0 | 0 | 0 | 5366121.6 | 0
7965 | 1569.6 | 0 | 0 | 0 | 0 | 1621.7 | 0 | 0 | 0 | 5333500.8 | 0
7966 | 1548.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1726 | 560671.6237 | 111351.8261 | 50510.4255 | 4211784.8863 | 83809.476
7967 | 1433.6 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1787.15 | 1126785.8192 | 215514.4963 | 97759.7701 | 2837155.4159 | 126007.2
7968 | 1310.4 | 0 | 0 | 0 | 0 | 1762.75 | 0 | 0 | 0 | 2401963.2 | 0
7969 | 1088 | 0 | 0 | 0 | 0 | 1613.8 | 0 | 0 | 0 | 1294720 | 0
7970 | 1392 | 0 | 0 | 0 | 0 | 1672 | 0 | 0 | 0 | 1656480 | 0
7971 | 1436.8 | 0 | 0 | 0 | 0 | 1557.4 | 0 | 0 | 0 | 1709792 | 0
7972 | 1538.4 | 0 | 0 | 0 | 0 | 1505.7 | 0 | 0 | 0 | 1830696 | 0
7973 | 1468 | 0 | 0 | 0 | 0 | 1505.85 | 0 | 0 | 0 | 1746920 | 0
7974 | 1324 | 0 | 0 | 0 | 0 | 1513.45 | 0 | 0 | 0 | 1575560 | 0
7975 | 916 | 23.7388 | 23.7388 | 23.1088 | 23.1088 | 1528.8 | 36940.0063 | 8319.1508 | 3773.6592 | 1636669.6572 | 10658.544
7976 | 1538.833 | 395.2091 | 395.2091 | 384.7205 | 384.7205 | 1577.6 | 634992.2526 | 138499.3717 | 62824.8539 | 2115488.2548 | 159068.2368
7977 | 1337.062 | 996.5566 | 996.5566 | 970.1085 | 970.1085 | 1608.05 | 1637403.1211 | 349239.0569 | 158418.7166 | 672625.7812 | 372190.6247
7978 | 1341.153 | 1393.1961 | 1393.1961 | 1356.2214 | 1341.153 | 1573.55 | 2222256.1851 | 482815.08 | 219010.2849 | 0 | 571934.6968
7979 | 1403.197 | 1457.6477 | 1457.6477 | 1418.9625 | 1403.197 | 1050.25 | 1555818.5349 | 505150.92 | 229142.0701 | 0 | 1332686.3507
7980 | 1495.022 | 2130.065 | 1553.036 | 2073.5342 | 1495.022 | 1040.45 | 1636969.0406 | 538207.92 | 244137.0926 | 0 | 1434548.3601
7981 | 1415.791 | 1825.0491 | 1470.7304 | 1776.6132 | 1415.791 | 1023.15 | 1518152.5518 | 509684.76 | 231198.6703 | 0 | 1383015.4383
7982 | 1603.039 | 1790.0195 | 1665.2445 | 1742.5134 | 1603.039 | 1412.3 | 2365914.002 | 577094.04 | 261776.2687 | 0 | 942106.0203
7983 | 1305.477 | 1731.6782 | 1356.1357 | 1685.7204 | 1305.477 | 1584.05 | 2163385.8518 | 469971.72 | 213184.3941 | 0 | 543013.1582
7984 | 1797.5 | 452.119 | 452.119 | 440.12 | 440.12 | 1618.2 | 745686.9477 | 158443.1997 | 71871.5958 | 2488077.5417 | 164483.258
7985 | 1690.399 | 12.3306 | 12.3306 | 12.0034 | 12.0034 | 1857.75 | 23371.0947 | 4321.2113 | 1960.1494 | 3076499.1996 | 1671.4375
7986 | 1741.499 | 0 | 0 | 0 | 0 | 1692.05 | 0 | 0 | 0 | 3192167.667 | 0
7987 | 1718.4 | 0 | 0 | 0 | 0 | 1886.55 | 0 | 0 | 0 | 5839123.2 | 0
7988 | 1222.4 | 0 | 0 | 0 | 0 | 1566.95 | 0 | 0 | 0 | 4153715.2 | 0
7989 | 1288 | 0 | 0 | 0 | 0 | 1401.65 | 0 | 0 | 0 | 4376624 | 0
7990 | 1320.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1691.5 | 547254.764 | 111351.8261 | 50510.4255 | 3437040.8863 | 94362.129
7991 | 1376 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1551.1 | 973337.0982 | 215514.4963 | 97759.7701 | 2641430.6159 | 265748.8
7992 | 1328.8 | 0 | 0 | 0 | 0 | 1503.7 | 0 | 0 | 0 | 2435690.4 | 0
7993 | 1398.4 | 0 | 0 | 0 | 0 | 1364.35 | 0 | 0 | 0 | 2563267.2 | 0
7994 | 1504 | 0 | 0 | 0 | 0 | 1416.1 | 0 | 0 | 0 | 2756832 | 0
7995 | 1284 | 0 | 0 | 0 | 0 | 1486.05 | 0 | 0 | 0 | 2353572 | 0
7996 | 1360.8 | 0 | 0 | 0 | 0 | 1317.45 | 0 | 0 | 0 | 2494346.4 | 0
7997 | 1429.6 | 0 | 0 | 0 | 0 | 1239.1 | 0 | 0 | 0 | 2620456.8 | 0
7998 | 1222.4 | 0 | 0 | 0 | 0 | 1174.35 | 0 | 0 | 0 | 2240659.2 | 0
7999 | 1190.56 | 147.0698 | 147.0698 | 143.1667 | 143.1667 | 1372.05 | 205667.0799 | 51540.0005 | 23379.1169 | 1919871.9772 | 87999.6571
8000 | 1232.152 | 1061.0487 | 1061.0487 | 1032.889 | 1032.889 | 1610 | 1739889.7631 | 371840.0476 | 168670.7771 | 365249.0405 | 394305.6
8001 | 1245.954 | 1294.3029 | 1294.3029 | 1259.9528 | 1245.954 | 1816.8 | 2375805.1084 | 448543.44 | 203464.2882 | 0 | 228258.7728
8002 | 1352.375 | 1964.5668 | 1404.8536 | 1912.4282 | 1352.375 | 1719.6 | 2441198.6776 | 486855 | 220842.8375 | 0 | 379205.95
8003 | 1036.347 | 3168.421 | 1076.5622 | 3084.3328 | 1036.347 | 1255.95 | 1368978.3437 | 373084.92 | 169235.4651 | 0 | 771093.9853
8004 | 1453.973 | 2915.4782 | 1510.3941 | 2838.103 | 1453.973 | 1143.25 | 1746100.6236 | 523430.28 | 237433.7909 | 0 | 1245691.3677
8005 | 1380.768 | 3010.9475 | 1434.3484 | 2931.0386 | 1380.768 | 1023.15 | 1474469.7437 | 497076.48 | 225479.4144 | 0 | 1348803.2208
8006 | 1648.157 | 2400.014 | 1712.1133 | 2336.3189 | 1648.157 | 1310.9 | 2260837.5936 | 593336.52 | 269144.0381 | 0 | 1135744.9887
8007 | 1281.294 | 1847.2732 | 1331.0143 | 1798.2476 | 1281.294 | 1619.7 | 2171628.008 | 461265.84 | 209235.3102 | 0 | 487276.1082
8008 | 1404.316 | 644.7092 | 644.7092 | 627.599 | 627.599 | 1784.35 | 1171658.6154 | 225935.6415 | 102486.9174 | 1423722.2535 | 132478.755
8009 | 1308.225 | 260.2455 | 260.2455 | 253.3387 | 253.3387 | 1900.25 | 503894.0058 | 91201.9487 | 41370.2173 | 1933606.5026 | 24736.005
8010 | 1254.291 | 0 | 0 | 0 | 0 | 1912.4 | 0 | 0 | 0 | 2299115.403 | 0
8011 | 1336 | 0 | 0 | 0 | 0 | 1913.15 | 0 | 0 | 0 | 2448888 | 0
8012 | 854.4 | 0 | 0 | 0 | 0 | 1635.4 | 0 | 0 | 0 | 1566115.2 | 0
8013 | 1313.6 | 0 | 0 | 0 | 0 | 1306.2 | 0 | 0 | 0 | 2407828.8 | 0
8014 | 1232 | 0 | 0 | 0 | 0 | 1370.85 | 0 | 0 | 0 | 2258256 | 0
8015 | 1172.8 | 0 | 0 | 0 | 0 | 1221.4 | 0 | 0 | 0 | 2149742.4 | 0
8016 | 1341.6 | 0 | 0 | 0 | 0 | 1208.05 | 0 | 0 | 0 | 2459152.8 | 0
8017 | 1092 | 0 | 0 | 0 | 0 | 1634.4 | 0 | 0 | 0 | 1299480 | 0
8018 | 1248 | 0 | 0 | 0 | 0 | 1543.1 | 0 | 0 | 0 | 1485120 | 0
8019 | 1142.4 | 0 | 0 | 0 | 0 | 1580.15 | 0 | 0 | 0 | 1359456 | 0
8020 | 1088.8 | 0 | 0 | 0 | 0 | 1578.75 | 0 | 0 | 0 | 1295672 | 0
8021 | 978.4 | 0 | 0 | 0 | 0 | 1579.5 | 0 | 0 | 0 | 1164296 | 0
8022 | 1040.8 | 0 | 0 | 0 | 0 | 1583.8 | 0 | 0 | 0 | 1238552 | 0
8023 | 858.4 | 112.3073 | 112.3073 | 109.3267 | 109.3267 | 1728.3 | 198506.9154 | 39357.6068 | 17853.0477 | 1373051.3854 | 29075.7038
8024 | 1146.178 | 1080.9231 | 1080.9231 | 1052.236 | 1052.236 | 1801.5 | 1991725.9152 | 378804.9519 | 171830.1351 | 172195.7274 | 203857.7135
8025 | 1191.895 | 1238.1462 | 1238.1462 | 1205.2865 | 1191.895 | 1848.25 | 2317970.022 | 429082.2 | 194636.4535 | 0 | 180870.0663
8026 | 1166.901 | 1212.1823 | 1212.1823 | 1180.0116 | 1166.901 | 1808.05 | 2222384.1547 | 420084.36 | 190554.9333 | 0 | 223986.6469
8027 | 1126.266 | 2091.1441 | 1169.9705 | 2035.6463 | 1126.266 | 1620.1 | 1920262.881 | 405455.76 | 183919.2378 | 0 | 427868.4534
8028 | 1448.14 | 2713.1835 | 1504.3347 | 2641.1771 | 1448.14 | 1546 | 2346905.6599 | 521330.4 | 236481.262 | 0 | 657455.56
8029 | 920.542 | 2622.8469 | 956.2634 | 2553.238 | 920.542 | 1377.9 | 1325485.1984 | 331395.12 | 150324.5086 | 0 | 572669.1782
8030 | 997.387 | 2295.1643 | 1036.0904 | 2234.2519 | 997.387 | 1601.65 | 1670786.9874 | 359059.32 | 162873.2971 | 0 | 397309.1115
8031 | 860.713 | 1858.67 | 894.1128 | 1809.3419 | 860.713 | 1694.7 | 1526281.3604 | 309856.68 | 140554.4329 | 0 | 262775.6789
8032 | 234.947 | 864.3375 | 244.0641 | 841.3984 | 234.947 | 1837.8 | 451723.8239 | 84580.92 | 38366.8451 | 0 | 38108.4034
8033 | 183.063 | 647.2751 | 190.1667 | 630.0968 | 183.063 | 1861.1 | 356513.0365 | 65902.68 | 29894.1879 | 0 | 25427.4507
8034 | 137.552 | 142.8897 | 142.8897 | 139.0975 | 137.552 | 1759.4 | 253229.0451 | 49518.72 | 22462.2416 | 0 | 33095.0112
8035 | 148 | 153.7431 | 153.7431 | 149.6628 | 148 | 1843.75 | 286012.4731 | 53280 | 24168.4 | 0 | 23125
8036 | 100.8 | 104.7115 | 104.7115 | 101.9325 | 100.8 | 1649.6 | 174412.6727 | 36288 | 16460.64 | 0 | 35320.32
8037 | 96 | 99.7253 | 99.7253 | 97.0786 | 96 | 1673.95 | 168117.9094 | 34560 | 15676.8 | 0 | 31300.8
8038 | 102.4 | 106.3736 | 106.3736 | 103.5505 | 102.4 | 1783.9 | 190974.4955 | 36864 | 16721.92 | 0 | 22128.64
8039 | 91.2 | 94.739 | 94.739 | 92.2247 | 91.2 | 1789.1 | 171060.0075 | 32832 | 14892.96 | 0 | 19234.08
8040 | 100 | 103.8805 | 103.8805 | 101.1235 | 100 | 1773.4 | 185930.4465 | 36000 | 16330 | 0 | 22660
8041 | 89.6 | 0 | 0 | 0 | 0 | 1566.4 | 0 | 0 | 0 | 106624 | 0
8042 | 96 | 0 | 0 | 0 | 0 | 1531.2 | 0 | 0 | 0 | 114240 | 0
8043 | 89.6 | 0 | 0 | 0 | 0 | 1527.5 | 0 | 0 | 0 | 106624 | 0
8044 | 89.6 | 0 | 0 | 0 | 0 | 1537.55 | 0 | 0 | 0 | 106624 | 0
8045 | 91.2 | 31.0831 | 31.0831 | 30.2582 | 30.2582 | 1566.6 | 49638.9471 | 10892.9472 | 4941.1619 | 72520.7578 | 12968.1948
8046 | 92 | 95.57 | 95.57 | 93.0337 | 92 | 1567.5 | 150771.4876 | 33120 | 15023.6 | 0 | 39790
8047 | 72.8 | 75.625 | 75.625 | 73.6179 | 72.8 | 1568.9 | 119316.3068 | 26208 | 11888.24 | 0 | 31384.08
8048 | 89.61 | 451.9247 | 93.0873 | 439.9309 | 89.61 | 1578.15 | 147835.0654 | 32259.6 | 14633.313 | 0 | 37801.9785
8049 | 636.197 | 1902.3964 | 660.8845 | 1851.9078 | 636.197 | 1547.05 | 1032072.0672 | 229030.92 | 103890.9701 | 0 | 288165.4312
8050 | 1258.648 | 3450.4814 | 1307.4895 | 3358.9075 | 1258.648 | 1417.4 | 1875785.2532 | 453113.28 | 205537.2184 | 0 | 733288.3248
8051 | 1251.361 | 3927.2626 | 1299.9197 | 3823.0352 | 1251.361 | 1213.3 | 1599796.3221 | 450489.96 | 204347.2513 | 0 | 984445.6987
8052 | 1077.291 | 4111.9746 | 1119.095 | 4002.845 | 1077.291 | 1145.6 | 1299142.4711 | 387824.76 | 175921.6203 | 0 | 920437.4304
8053 | 1356.354 | 3424.6972 | 1408.987 | 3333.8076 | 1356.354 | 1049.25 | 1498304.2373 | 488287.44 | 221492.6082 | 0 | 1289553.5655
8054 | 1104.063 | 3494.5059 | 1146.9059 | 3401.7636 | 1104.063 | 1020.35 | 1181595.07 | 397462.68 | 180293.4879 | 0 | 1081595.318
8055 | 1125.992 | 2462.7318 | 1169.6858 | 2397.3723 | 1125.992 | 1153.6 | 1355916.644 | 405357.12 | 183874.4936 | 0 | 953039.6288
8056 | 1050.113 | 601.4534 | 601.4534 | 585.4912 | 585.4912 | 1433.15 | 875164.4694 | 210776.8178 | 95610.7065 | 851651.8318 | 324865.1361
8057 | 951.408 | 364.8469 | 364.8469 | 355.1641 | 355.1641 | 1601.7 | 593212.129 | 127859.0715 | 57998.2955 | 1092915.0915 | 138469.3933
8058 | 1136.61 | 0 | 0 | 0 | 0 | 1654.95 | 0 | 0 | 0 | 2083406.13 | 0
8059 | 1047.2 | 0 | 0 | 0 | 0 | 1779.3 | 0 | 0 | 0 | 3558385.6 | 0
8060 | 1128.8 | 0 | 0 | 0 | 0 | 1719.05 | 0 | 0 | 0 | 3835662.4 | 0
8061 | 778.4 | 0 | 0 | 0 | 0 | 1698.45 | 0 | 0 | 0 | 2645003.2 | 0
8062 | 1089.6 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1703.25 | 551915.6032 | 111351.8261 | 50510.4255 | 2651423.2863 | 90768.1095
8063 | 952.8 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1675.6 | 1052944.7732 | 215514.4963 | 97759.7701 | 1203397.0159 | 192044.8
8064 | 999.2 | 0 | 0 | 0 | 0 | 1566.1 | 0 | 0 | 0 | 1831533.6 | 0
8065 | 960 | 0 | 0 | 0 | 0 | 1643.35 | 0 | 0 | 0 | 1142400 | 0
8066 | 1305.6 | 0 | 0 | 0 | 0 | 1566.8 | 0 | 0 | 0 | 1553664 | 0
8067 | 1168.8 | 0 | 0 | 0 | 0 | 1573.1 | 0 | 0 | 0 | 1390872 | 0
8068 | 1358.4 | 0 | 0 | 0 | 0 | 1572.15 | 0 | 0 | 0 | 1616496 | 0
8069 | 1282.4 | 0 | 0 | 0 | 0 | 1553.65 | 0 | 0 | 0 | 1526056 | 0
8070 | 1162.4 | 0 | 0 | 0 | 0 | 1580.7 | 0 | 0 | 0 | 1383256 | 0
8071 | 1039.2 | 387.7806 | 387.7806 | 377.4891 | 377.4891 | 1660.7 | 651939.8095 | 135896.0876 | 61643.9753 | 1212916.0205 | 125372.7072
8072 | 1081.05 | 1122.9999 | 1122.9999 | 1093.1961 | 1081.05 | 1735.6 | 1952001.2148 | 389178 | 176535.465 | 0 | 285829.62
8073 | 811.981 | 2230.4177 | 843.4897 | 2171.2236 | 811.981 | 1757.45 | 1487933.0058 | 292313.16 | 132596.4973 | 0 | 196945.9915
8074 | 1146.669 | 3461.3816 | 1191.1652 | 3369.5184 | 1146.669 | 1762.75 | 2108756.8378 | 412800.84 | 187251.0477 | 0 | 272047.2202
8075 | 1380.393 | 3921.9284 | 1433.9588 | 3817.8425 | 1380.393 | 1650.9 | 2381530.7323 | 496941.48 | 225418.1769 | 0 | 481895.1963
8076 | 1173.817 | 4104.9492 | 1219.3667 | 3996.006 | 1173.817 | 1616.55 | 1984495.4457 | 422574.12 | 191684.3161 | 0 | 450100.1287
8077 | 1141.587 | 4009.9224 | 1185.886 | 3903.5013 | 1141.587 | 1594.2 | 1902568.9803 | 410971.32 | 186421.1571 | 0 | 463256.0046
8078 | 1217.119 | 3641.9238 | 1264.349 | 3545.2691 | 1217.119 | 1639.2 | 2078594.5491 | 438162.84 | 198755.5327 | 0 | 439136.5352
8079 | 1621.666 | 3003.8151 | 1684.5943 | 2924.0955 | 1621.666 | 1775.15 | 3000208.7574 | 583799.76 | 264818.0578 | 0 | 364631.6001
8080 | 617.579 | 2088.3403 | 641.544 | 2032.9169 | 617.579 | 1888.2 | 1214920.1815 | 222328.44 | 100850.6507 | 0 | 69045.3322
8081 | 1446.565 | 861.6221 | 861.6221 | 838.7551 | 838.7551 | 1908.65 | 1667456.762 | 301951.8272 | 136968.7038 | 1114115.5914 | 74999.5375
8082 | 1314.233 | 0 | 0 | 0 | 0 | 1927.95 | 0 | 0 | 0 | 2408989.089 | 0
8083 | 1122.4 | 0 | 0 | 0 | 0 | 1933.9 | 0 | 0 | 0 | 3813915.2 | 0
8084 | 976.8 | 0 | 0 | 0 | 0 | 1876.3 | 0 | 0 | 0 | 3319166.4 | 0
8085 | 1206.4 | 0 | 0 | 0 | 0 | 1861.9 | 0 | 0 | 0 | 4099347.2 | 0
8086 | 1304 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1844.05 | 594441.0846 | 111351.8261 | 50510.4255 | 3379954.4863 | 47701.0503
8087 | 1134.4 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1823.1 | 1137980.5667 | 215514.4963 | 97759.7701 | 1820473.8159 | 104724.8
8088 | 949.6 | 0 | 0 | 0 | 0 | 1797.35 | 0 | 0 | 0 | 1740616.8 | 0
8089 | 1222.4 | 0 | 0 | 0 | 0 | 1742.65 | 0 | 0 | 0 | 1454656 | 0
8090 | 851.2 | 0 | 0 | 0 | 0 | 1696.05 | 0 | 0 | 0 | 1012928 | 0
8091 | 1256.8 | 0 | 0 | 0 | 0 | 1693.4 | 0 | 0 | 0 | 1495592 | 0
8092 | 1092.8 | 0 | 0 | 0 | 0 | 1692.45 | 0 | 0 | 0 | 1300432 | 0
8093 | 1028.8 | 0 | 0 | 0 | 0 | 1693.95 | 0 | 0 | 0 | 1224272 | 0
8094 | 1088.8 | 0 | 0 | 0 | 0 | 1701 | 0 | 0 | 0 | 1295672 | 0
8095 | 1353.6 | 371.1275 | 371.1275 | 361.278 | 361.278 | 1716.95 | 645863.5147 | 130060.0861 | 58996.7002 | 1818926.1948 | 100096.3867
8096 | 697.26 | 772.8302 | 724.317 | 752.3197 | 697.26 | 1785.4 | 1296830.0878 | 251013.6 | 113862.558 | 0 | 149631.996
8097 | 894.813 | 2313.736 | 929.536 | 2252.3308 | 894.813 | 1861.75 | 1737843.0563 | 322132.68 | 146122.9629 | 0 | 123707.8972
8098 | 1264.732 | 3485.2502 | 1313.8096 | 3392.7535 | 1264.732 | 1875.95 | 2475504.235 | 455303.52 | 206530.7356 | 0 | 156890.0046
8099 | 1241.914 | 3904.4401 | 1290.1062 | 3800.8184 | 1241.914 | 1880.9 | 2450869.8409 | 447089.04 | 202804.5562 | 0 | 147911.9574
8100 | 1308.586 | 4041.8459 | 1359.3654 | 3934.5775 | 1308.586 | 1865.85 | 2556884.3729 | 471090.96 | 213692.0938 | 0 | 175546.8119
8101 | 1086.618 | 3915.494 | 1128.7839 | 3811.5789 | 1086.618 | 1788.5 | 2034770.2998 | 391182.48 | 177444.7194 | 0 | 229819.707
8102 | 1312.456 | 3565.2309 | 1363.3855 | 3470.6116 | 1312.456 | 1857.8 | 2551675.0287 | 472484.16 | 214324.0648 | 0 | 186631.2432
8103 | 1471.833 | 2975.8359 | 1528.9471 | 2896.8589 | 1471.833 | 1888.35 | 2902649.0852 | 529859.88 | 240350.3289 | 0 | 164330.1544
8104 | 1659.084 | 2010.6004 | 1723.4643 | 1957.2401 | 1659.084 | 1899.6 | 3285689.6256 | 597270.24 | 270928.4172 | 0 | 166572.0336
8105 | 1382.135 | 721.4904 | 721.4904 | 702.3424 | 702.3424 | 1914.35 | 1400663.0279 | 252843.2816 | 114692.5219 | 1246059.7461 | 58883.0903
8106 | 1357.739 | 0 | 0 | 0 | 0 | 1922.25 | 0 | 0 | 0 | 2488735.587 | 0
8107 | 1292 | 0 | 0 | 0 | 0 | 1928.2 | 0 | 0 | 0 | 4390216 | 0
8108 | 1217.6 | 0 | 0 | 0 | 0 | 1830.75 | 0 | 0 | 0 | 4137404.8 | 0
8109 | 1288 | 0 | 0 | 0 | 0 | 1798.2 | 0 | 0 | 0 | 4376624 | 0
8110 | 1356 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1844.05 | 594521.1823 | 111351.8261 | 50510.4255 | 3556650.4863 | 47701.0503
8111 | 968.8 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1817.4 | 1133585.0366 | 215514.4963 | 97759.7701 | 1257765.0159 | 108099.2
8112 | 1264 | 0 | 0 | 0 | 0 | 1796.65 | 0 | 0 | 0 | 2316912 | 0
8113 | 1316.8 | 0 | 0 | 0 | 0 | 1742.65 | 0 | 0 | 0 | 1566992 | 0
8114 | 1169.6 | 0 | 0 | 0 | 0 | 1696.05 | 0 | 0 | 0 | 1391824 | 0
8115 | 1160.8 | 0 | 0 | 0 | 0 | 1667.1 | 0 | 0 | 0 | 1381352 | 0
8116 | 1196 | 0 | 0 | 0 | 0 | 1666.15 | 0 | 0 | 0 | 1423240 | 0
8117 | 840 | 0 | 0 | 0 | 0 | 1680.8 | 0 | 0 | 0 | 999600 | 0
8118 | 1152.8 | 0 | 0 | 0 | 0 | 1701 | 0 | 0 | 0 | 1371832 | 0
8119 | 706.4 | 349.7479 | 349.7479 | 340.4658 | 340.4658 | 1716.95 | 608380.1932 | 122567.681 | 55598.062 | 670757.4243 | 94330.3752
8120 | 959.437 | 996.6677 | 996.6677 | 970.2167 | 959.437 | 1785.4 | 1782729.1565 | 345397.32 | 156676.0621 | 0 | 205895.1802
8121 | 900.079 | 2252.1432 | 935.0063 | 2192.3726 | 900.079 | 1856.05 | 1742377.0304 | 324028.44 | 146982.9007 | 0 | 129566.3721
8122 | 1146.42 | 3390.7325 | 1190.9065 | 3300.7443 | 1146.42 | 1812.25 | 2175024.3008 | 412711.2 | 187210.386 | 0 | 215240.355
8123 | 1422.593 | 3819.202 | 1477.7964 | 3717.8425 | 1422.593 | 1660.9 | 2474250.2821 | 512133.48 | 232309.4369 | 0 | 482401.2863
8124 | 1547.461 | 4007.2911 | 1607.5098 | 3900.9398 | 1547.461 | 1750.75 | 2837147.6464 | 557085.96 | 252700.3813 | 0 | 385704.6543
8125 | 1494.729 | 3798.9993 | 1552.7316 | 3698.176 | 1494.729 | 1748.85 | 2733620.4463 | 538102.44 | 244089.2457 | 0 | 375401.1884
8126 | 1257.696 | 3579.5664 | 1306.5006 | 3484.5666 | 1257.696 | 1863.5 | 2453033.3813 | 452770.56 | 205381.7568 | 0 | 171675.504
8127 | 1228.071 | 2472.5132 | 1275.726 | 2406.894 | 1228.071 | 1888.35 | 2424941.2009 | 442105.56 | 200543.9943 | 0 | 137114.1272
8128 | 1769.154 | 1925.2792 | 1837.8056 | 1874.1833 | 1769.154 | 1899.6 | 3507166.1976 | 636895.44 | 288902.8482 | 0 | 177623.0616
8129 | 1953.371 | 756.4067 | 756.4067 | 736.3321 | 736.3321 | 1914.35 | 1470202.8041 | 265079.554 | 120243.031 | 2230832.314 | 61732.7514
8130 | 1544.713 | 0 | 0 | 0 | 0 | 1927.95 | 0 | 0 | 0 | 2831458.929 | 0
8131 | 1589.6 | 0 | 0 | 0 | 0 | 1933.9 | 0 | 0 | 0 | 5401460.8 | 0
8132 | 1320 | 0 | 0 | 0 | 0 | 1881.3 | 0 | 0 | 0 | 4485360 | 0
8133 | 1744 | 0 | 0 | 0 | 0 | 1856.2 | 0 | 0 | 0 | 5926112 | 0
8134 | 1516.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1844.05 | 595516.6418 | 111351.8261 | 50510.4255 | 4103048.8863 | 47701.0503
8135 | 1599.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1823.1 | 1139384.3513 | 215514.4963 | 97759.7701 | 3399864.2159 | 104724.8
8136 | 1542.4 | 0 | 0 | 0 | 0 | 1802.35 | 0 | 0 | 0 | 2827219.2 | 0
8137 | 1434.4 | 0 | 0 | 0 | 0 | 1766.15 | 0 | 0 | 0 | 1706936 | 0
8138 | 1324 | 0 | 0 | 0 | 0 | 1696.05 | 0 | 0 | 0 | 1575560 | 0
8139 | 1325.6 | 0 | 0 | 0 | 0 | 1680.25 | 0 | 0 | 0 | 1577464 | 0
8140 | 1516.8 | 0 | 0 | 0 | 0 | 1666.45 | 0 | 0 | 0 | 1804992 | 0
8141 | 1291.2 | 0 | 0 | 0 | 0 | 1667.65 | 0 | 0 | 0 | 1536528 | 0
8142 | 1542.4 | 0 | 0 | 0 | 0 | 1730 | 0 | 0 | 0 | 1835456 | 0
8143 | 1000.8 | 353.3442 | 353.3442 | 343.9667 | 343.9667 | 1795.25 | 642466.4944 | 123828.0039 | 56169.7585 | 1203975.48 | 68937.2775
8144 | 828.43 | 991.8435 | 860.577 | 965.5205 | 828.43 | 1824.55 | 1575749.3103 | 298234.8 | 135282.619 | 0 | 145348.0435
8145 | 1062.166 | 2271.2323 | 1103.3841 | 2210.955 | 1062.166 | 1856.05 | 2056285.3276 | 382379.76 | 173451.7078 | 0 | 152898.7957
8146 | 1354.15 | 3416.6537 | 1406.6974 | 3325.9776 | 1354.15 | 1870.25 | 2649087.0815 | 487494 | 221132.695 | 0 | 175700.9625
8147 | 1544.599 | 3829.4862 | 1604.5368 | 3727.8537 | 1544.599 | 1791.2 | 2891739.9939 | 556055.64 | 252233.0167 | 0 | 322512.2712
8148 | 1620.767 | 4001.2411 | 1683.6605 | 3895.0504 | 1620.767 | 1696.7 | 2878390.4694 | 583476.12 | 264671.2511 | 0 | 491578.6311
8149 | 936.447 | 3807.7346 | 972.7856 | 3706.6794 | 936.447 | 1418.7 | 1387777.821 | 337120.92 | 152921.7951 | 0 | 544356.6411
8150 | 1379.589 | 2431.8367 | 1433.1236 | 2367.2971 | 1379.589 | 1719.35 | 2475870.9504 | 496652.04 | 225286.8837 | 0 | 387181.6529
8151 | 1282.753 | 2332.6942 | 1332.5299 | 2270.7858 | 1282.753 | 1870.6 | 2509039.2484 | 461791.08 | 209473.5649 | 0 | 165988.2382
8152 | 1281.053 | 1583.9581 | 1330.7639 | 1541.9207 | 1281.053 | 1893.9 | 2539446.5487 | 461179.08 | 209195.9549 | 0 | 135919.7233
8153 | 1015.736 | 725.7246 | 725.7246 | 706.4642 | 706.4642 | 1914.35 | 1411926.6667 | 254327.128 | 115365.6111 | 566895.1277 | 59228.688
8154 | 1172.039 | 0 | 0 | 0 | 0 | 1927.95 | 0 | 0 | 0 | 2148347.487 | 0
8155 | 1207.2 | 0 | 0 | 0 | 0 | 1933.9 | 0 | 0 | 0 | 4102065.6 | 0
8156 | 1226.4 | 0 | 0 | 0 | 0 | 1881.3 | 0 | 0 | 0 | 4167307.2 | 0
8157 | 1287.2 | 0 | 0 | 0 | 0 | 1856.2 | 0 | 0 | 0 | 4373905.6 | 0
8158 | 1448.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1844.05 | 595878.1209 | 111351.8261 | 50510.4255 | 3871984.8863 | 47701.0503
8159 | 1248.8 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1823.1 | 1140198.2667 | 215514.4963 | 97759.7701 | 2209205.0159 | 104724.8
8160 | 1272.8 | 0 | 0 | 0 | 0 | 1796.65 | 0 | 0 | 0 | 2333042.4 | 0
8161 | 1412 | 0 | 0 | 0 | 0 | 1781.8 | 0 | 0 | 0 | 2588196 | 0
8162 | 1366.4 | 0 | 0 | 0 | 0 | 1761.65 | 0 | 0 | 0 | 2504611.2 | 0
8163 | 1345.6 | 0 | 0 | 0 | 0 | 1759 | 0 | 0 | 0 | 2466484.8 | 0
8164 | 1445.6 | 0 | 0 | 0 | 0 | 1758.05 | 0 | 0 | 0 | 2649784.8 | 0
8165 | 1436 | 0 | 0 | 0 | 0 | 1733.1 | 0 | 0 | 0 | 2632188 | 0
8166 | 1366.4 | 0 | 0 | 0 | 0 | 1779.3 | 0 | 0 | 0 | 2504611.2 | 0
8167 | 1041.6 | 131.5802 | 131.5802 | 128.0881 | 128.0881 | 1795.25 | 239715.899 | 46111.7292 | 20916.7927 | 1674467.2457 | 25671.3502
8168 | 1319.128 | 1014.1383 | 1014.1383 | 987.2237 | 987.2237 | 1824.55 | 1878780.2381 | 355400.5144 | 161213.6222 | 608380.6714 | 169544.5285
8169 | 889.005 | 1220.1593 | 923.5026 | 1187.7769 | 889.005 | 1867.45 | 1725241.6894 | 320041.8 | 145174.5165 | 0 | 117837.6127
8170 | 1469.341 | 1735.4407 | 1526.3584 | 1689.3831 | 1469.341 | 1870.25 | 2839414.7818 | 528962.76 | 239943.3853 | 0 | 190646.9948
8171 | 1714.76 | 2818.6128 | 1781.3008 | 2743.8084 | 1714.76 | 1791.2 | 3200892.3178 | 617313.6 | 280020.308 | 0 | 358041.888
8172 | 1647.544 | 2848.8742 | 1711.4765 | 2773.2667 | 1647.544 | 1734.2 | 2972002.8912 | 593115.84 | 269043.9352 | 0 | 437917.1952
8173 | 1465.729 | 1927.9645 | 1522.6062 | 1876.7974 | 1465.729 | 1733.2 | 2645580.6656 | 527662.44 | 239353.5457 | 0 | 391056.4972
8174 | 1506.159 | 1320.2533 | 1320.2533 | 1285.2145 | 1285.2145 | 1768.85 | 2374309.2853 | 462677.2235 | 209875.5294 | 404991.2508 | 290793.1722
8175 | 1621.22 | 1128.5388 | 1128.5388 | 1098.588 | 1098.588 | 1876.95 | 2155099.9769 | 395491.6714 | 179399.4165 | 957984.4998 | 132321.6945
8176 | 1662.845 | 1496.3785 | 1496.3785 | 1456.6654 | 1456.6654 | 1893.9 | 2882280.7542 | 524399.5559 | 237873.4652 | 377927.1464 | 151282.8972
8177 | 1580.403 | 355.2837 | 355.2837 | 345.8547 | 345.8547 | 1914.35 | 690835.3274 | 124507.6755 | 56478.065 | 2262927.1179 | 28995.8654
8178 | 1155.725 | 0 | 0 | 0 | 0 | 1922.25 | 0 | 0 | 0 | 2118443.925 | 0
8179 | 1545.6 | 0 | 0 | 0 | 0 | 1933.9 | 0 | 0 | 0 | 2833084.8 | 0
8180 | 1300 | 0 | 0 | 0 | 0 | 1875.6 | 0 | 0 | 0 | 2382900 | 0
8181 | 1517.6 | 0 | 0 | 0 | 0 | 1856.2 | 0 | 0 | 0 | 2781760.8 | 0
8182 | 1541.6 | 0 | 0 | 0 | 0 | 1844.05 | 0 | 0 | 0 | 2825752.8 | 0
8183 | 1264.8 | 0 | 0 | 0 | 0 | 1811.7 | 0 | 0 | 0 | 2318378.4 | 0
8184 | 1515.2 | 300.2894 | 300.2894 | 292.3199 | 292.3199 | 1796.65 | 549117.6149 | 105235.146 | 47735.8315 | 2241539.3147 | 56575.4269
8185 | 1142.4 | 0 | 0 | 0 | 0 | 1686.1 | 0 | 0 | 0 | 1359456 | 0
8186 | 1111.2 | 0 | 0 | 0 | 0 | 1778.35 | 0 | 0 | 0 | 1322328 | 0
8187 | 1584.8 | 0 | 0 | 0 | 0 | 1762.75 | 0 | 0 | 0 | 1885912 | 0
8188 | 1384 | 0 | 0 | 0 | 0 | 1695.35 | 0 | 0 | 0 | 1646960 | 0
8189 | 1290.4 | 0 | 0 | 0 | 0 | 1696.65 | 0 | 0 | 0 | 1535576 | 0
8190 | 1424 | 0 | 0 | 0 | 0 | 1735 | 0 | 0 | 0 | 1694560 | 0
8191 | 1168.8 | 900.8556 | 900.8556 | 876.9474 | 876.9474 | 1688.95 | 1549010.938 | 315701.0696 | 143205.513 | 534965.7873 | 268874.4194
8192 | 1085.638 | 1127.7659 | 1127.7659 | 1097.8356 | 1085.638 | 1769.9 | 2004052.3935 | 390829.68 | 177284.6854 | 0 | 249805.3038
8193 | 1060.777 | 1644.1693 | 1101.9402 | 1600.5339 | 1060.777 | 1845.4 | 2044054.4639 | 381879.72 | 173224.8841 | 0 | 163996.1242
8194 | 1138.269 | 2312.7959 | 1182.4403 | 2251.4156 | 1138.269 | 1853.05 | 2209902.9142 | 409776.84 | 185879.3277 | 0 | 167268.6296
8195 | 1033.825 | 3280.4426 | 1073.9423 | 3193.3814 | 1033.825 | 1716.4 | 1860230.0113 | 372177 | 168823.6225 | 0 | 293192.77
8196 | 1090.429 | 3476.705 | 1132.7428 | 3384.4351 | 1090.429 | 1670.7 | 1912010.4103 | 392554.44 | 178067.0557 | 0 | 359078.2697
8197 | 1135.24 | 3101.0649 | 1179.2927 | 3018.7643 | 1135.24 | 1616.85 | 1924631.9979 | 408686.4 | 185384.692 | 0 | 434967.206
8198 | 1171.847 | 2328.62 | 1217.3202 | 2266.8197 | 1171.847 | 1658.35 | 2029716.604 | 421864.92 | 191362.6151 | 0 | 400361.5276
8199 | 1104.482 | 1147.3411 | 1147.3411 | 1116.8913 | 1104.482 | 1768.55 | 2044281.6549 | 397613.52 | 180361.9106 | 0 | 255632.3589
8200 | 224.458 | 763.7428 | 233.168 | 743.4734 | 224.458 | 1870.15 | 439849.3856 | 80804.88 | 36653.9914 | 0 | 29145.8713
8201 | 183.44 | 359.9614 | 190.5583 | 350.4082 | 183.44 | 1880.05 | 360807.7248 | 66038.4 | 29955.752 | 0 | 22003.628
8202 | 160.064 | 112.4755 | 112.4755 | 109.4905 | 109.4905 | 1880.15 | 215456.3667 | 39416.582 | 17879.7996 | 92701.2151 | 12976.6389
8203 | 206.4 | 214.4093 | 214.4093 | 208.719 | 206.4 | 1889.15 | 409063.8501 | 74304 | 33705.12 | 0 | 22879.44
8204 | 149.6 | 155.4052 | 155.4052 | 151.2808 | 149.6 | 1690.35 | 265616.9832 | 53856 | 24429.68 | 0 | 46323.64
8205 | 116 | 120.5014 | 120.5014 | 117.3033 | 116 | 1621 | 196937.1953 | 41760 | 18942.8 | 0 | 43964
8206 | 109.6 | 113.853 | 113.853 | 110.8314 | 109.6 | 1644.45 | 188359.8136 | 39456 | 17897.68 | 0 | 38968.28
8207 | 99.2 | 103.0494 | 103.0494 | 100.3146 | 99.2 | 1603.45 | 166353.1482 | 35712 | 16199.36 | 0 | 39337.76
8208 | 108.8 | 113.022 | 113.022 | 110.0224 | 108.8 | 1590.2 | 180840.2508 | 39168 | 17767.04 | 0 | 44586.24
8209 | 100.8 | 0 | 0 | 0 | 0 | 1415.9 | 0 | 0 | 0 | 119952 | 0
8210 | 109.6 | 0 | 0 | 0 | 0 | 1566.2 | 0 | 0 | 0 | 130424 | 0
8211 | 100 | 0 | 0 | 0 | 0 | 1553.55 | 0 | 0 | 0 | 119000 | 0
8212 | 104 | 0 | 0 | 0 | 0 | 1561.5 | 0 | 0 | 0 | 123760 | 0
8213 | 93.6 | 0 | 0 | 0 | 0 | 1519.9 | 0 | 0 | 0 | 111384 | 0
8214 | 101.6 | 0 | 0 | 0 | 0 | 1380.3 | 0 | 0 | 0 | 120904 | 0
8215 | 93.6 | 97.2321 | 97.2321 | 94.6516 | 93.6 | 1327.9 | 129462.6971 | 33696 | 15284.88 | 0 | 62908.56
8216 | 100.012 | 103.8929 | 103.8929 | 101.1357 | 100.012 | 1484.75 | 155186.6256 | 36004.32 | 16331.9596 | 0 | 51531.183
8217 | 218.574 | 1064.1422 | 227.0557 | 1035.9005 | 218.574 | 1243.4 | 284360.868 | 78686.64 | 35693.1342 | 0 | 165373.0884
8218 | 955.563 | 2609.2033 | 992.6434 | 2539.9565 | 955.563 | 663.8 | 665108.0549 | 344002.68 | 156043.4379 | 0 | 1276823.2806
8219 | 1162.174 | 2195.4245 | 1207.2719 | 2137.1591 | 1162.174 | 303.5 | 369137.4452 | 418382.64 | 189783.0142 | 0 | 1971628.191
8220 | 1591.079 | 2184.1649 | 1652.8204 | 2126.1983 | 1591.079 | 297.8 | 497852.531 | 572788.44 | 259823.2007 | 0 | 2708334.6738
8221 | 1379.816 | 2656.3557 | 1433.3594 | 2585.8574 | 1379.816 | 281.3 | 407989.7015 | 496733.76 | 225323.9528 | 0 | 2371489.7592
8222 | 1610.809 | 2614.0057 | 1673.316 | 2544.6314 | 1610.809 | 652.4 | 1098459.2063 | 579891.24 | 263045.1097 | 0 | 2170726.2084
8223 | 1808.052 | 1302.6414 | 1302.6414 | 1268.07 | 1268.07 | 1255.05 | 1659402.782 | 456505.2087 | 207075.8349 | 989786.9619 | 924666.2077
8224 | 2055.558 | 1301.6244 | 1301.6244 | 1267.08 | 1267.08 | 1468.6 | 1942576.2449 | 456148.8088 | 206914.168 | 1445280.129 | 659083.1978
8225 | 1608.955 | 451.2381 | 451.2381 | 439.2625 | 439.2625 | 1691.2 | 775254.1277 | 158134.4897 | 71731.5616 | 2144046.4049 | 132775.0448
8226 | 1527.332 | 0 | 0 | 0 | 0 | 1775.25 | 0 | 0 | 0 | 2799599.556 | 0
8227 | 1779.2 | 0 | 0 | 0 | 0 | 1857.6 | 0 | 0 | 0 | 6045721.6 | 0
8228 | 1836.8 | 0 | 0 | 0 | 0 | 1781.2 | 0 | 0 | 0 | 6241446.4 | 0
8229 | 1579.2 | 0 | 0 | 0 | 0 | 1724.45 | 0 | 0 | 0 | 5366121.6 | 0
8230 | 1553.6 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1700.75 | 551020.775 | 111351.8261 | 50510.4255 | 4228095.2863 | 91532.7945
8231 | 1396 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1578.8 | 990074.2907 | 215514.4963 | 97759.7701 | 2709390.6159 | 249350.4
8232 | 1387.2 | 0 | 0 | 0 | 0 | 1277.05 | 0 | 0 | 0 | 2542737.6 | 0
8233 | 1321.6 | 0 | 0 | 0 | 0 | 1481.9 | 0 | 0 | 0 | 1572704 | 0
8234 | 1526.4 | 0 | 0 | 0 | 0 | 1435.25 | 0 | 0 | 0 | 1816416 | 0
8235 | 1572 | 0 | 0 | 0 | 0 | 1405.9 | 0 | 0 | 0 | 1870680 | 0
8236 | 1433.6 | 0 | 0 | 0 | 0 | 1478.75 | 0 | 0 | 0 | 1705984 | 0
8237 | 1316 | 0 | 0 | 0 | 0 | 1564.7 | 0 | 0 | 0 | 1566040 | 0
8238 | 1384.8 | 0 | 0 | 0 | 0 | 1593.2 | 0 | 0 | 0 | 1647912 | 0
8239 | 1184.8 | 102.8448 | 102.8448 | 100.1153 | 100.1153 | 1686.15 | 176098.0812 | 36041.5231 | 16348.8353 | 1988226.9782 | 30756.3584
8240 | 1308.643 | 702.4647 | 702.4647 | 683.8217 | 683.8217 | 1785.4 | 1276266.5131 | 246175.8019 | 111668.079 | 1145297.4944 | 143644.0122
8241 | 1418.787 | 1515.8125 | 1473.8427 | 1475.5836 | 1418.787 | 1856.05 | 2751324.8907 | 510763.32 | 231687.9171 | 0 | 204234.3887
8242 | 1582.275 | 2814.4264 | 1643.6748 | 2739.7331 | 1582.275 | 1773.4 | 2934347.3449 | 569619 | 258385.5075 | 0 | 358543.515
8243 | 1549.679 | 3749.4525 | 1609.8139 | 3649.9441 | 1549.679 | 1670.9 | 2713933.34 | 557884.44 | 253062.5807 | 0 | 509999.3589
8244 | 1523.622 | 2614.4202 | 1582.7458 | 2545.0349 | 1523.622 | 1513 | 2424243.9711 | 548503.92 | 248807.4726 | 0 | 742003.914
8245 | 1514.182 | 1589.8138 | 1572.9395 | 1547.621 | 1514.182 | 1468.7 | 2336439.2797 | 545105.52 | 247265.9206 | 0 | 804484.8966
8246 | 1331.149 | 964.5146 | 964.5146 | 938.9169 | 938.9169 | 1625 | 1594739.0549 | 338010.0964 | 153325.1354 | 718961.3763 | 344645.625
8247 | 1245.736 | 143.4319 | 143.4319 | 139.6253 | 139.6253 | 1818.6 | 265566.9618 | 50265.1158 | 22800.815 | 2027500.8734 | 24792.3008
8248 | 1236.827 | 199.1835 | 199.1835 | 193.8973 | 193.8973 | 1893.9 | 384286.4655 | 69803.0339 | 31663.4318 | 1911690.1102 | 20137.3556
8249 | 1300.328 | 270.7904 | 270.7904 | 263.6038 | 263.6038 | 1908.65 | 526430.1316 | 94897.3671 | 43046.5001 | 1900315.4633 | 23570.7664
8250 | 1367.211 | 0 | 0 | 0 | 0 | 1927.95 | 0 | 0 | 0 | 2506097.763 | 0
8251 | 1213.6 | 0 | 0 | 0 | 0 | 1933.9 | 0 | 0 | 0 | 4123812.8 | 0
8252 | 1144.8 | 0 | 0 | 0 | 0 | 1869.9 | 0 | 0 | 0 | 3890030.4 | 0
8253 | 1432 | 0 | 0 | 0 | 0 | 1856.2 | 0 | 0 | 0 | 4865936 | 0
8254 | 1488.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1844.05 | 596171.7183 | 111351.8261 | 50510.4255 | 4007904.8863 | 47701.0503
8255 | 1432.8 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1823.1 | 1141069.7084 | 215514.4963 | 97759.7701 | 2834437.0159 | 104724.8
8256 | 1107.2 | 0 | 0 | 0 | 0 | 1796.65 | 0 | 0 | 0 | 2029497.6 | 0
8257 | 1325.6 | 0 | 0 | 0 | 0 | 1690.65 | 0 | 0 | 0 | 1577464 | 0
8258 | 1274.4 | 0 | 0 | 0 | 0 | 1673.05 | 0 | 0 | 0 | 1516536 | 0
8259 | 1459.2 | 0 | 0 | 0 | 0 | 1667.7 | 0 | 0 | 0 | 1736448 | 0
8260 | 1384.8 | 0 | 0 | 0 | 0 | 1715.1 | 0 | 0 | 0 | 1647912 | 0
8261 | 1256 | 0 | 0 | 0 | 0 | 1726.75 | 0 | 0 | 0 | 1494640 | 0
8262 | 1425.6 | 0 | 0 | 0 | 0 | 1779.3 | 0 | 0 | 0 | 1696464 | 0
8263 | 991.2 | 194.0622 | 194.0622 | 188.9119 | 188.9119 | 1795.25 | 353041.8574 | 68008.2932 | 30849.3175 | 1470594.0403 | 37861.551
8264 | 982.402 | 1020.5239 | 1020.5239 | 993.4397 | 982.402 | 1824.55 | 1864977.0018 | 353664.72 | 160426.2466 | 0 | 170620.2124
8265 | 1106.567 | 1781.5574 | 1149.5071 | 1734.2759 | 1106.567 | 1867.45 | 2154692.308 | 398364.12 | 180702.3911 | 0 | 146675.4558
8266 | 1162.384 | 1681.9215 | 1207.49 | 1637.2842 | 1162.384 | 1875.95 | 2277661.3368 | 418458.24 | 189817.3072 | 0 | 144193.7352
8267 | 957.501 | 2185.8436 | 994.6566 | 2127.8325 | 957.501 | 1869.5 | 1870464.6219 | 344700.36 | 156359.9133 | 0 | 124953.8805
8268 | 1301.609 | 2662.3766 | 1352.1176 | 2591.7186 | 1301.609 | 1853.8 | 2523075.9168 | 468579.24 | 212552.7497 | 0 | 190295.2358
8269 | 1278.001 | 2315.313 | 1327.5935 | 2253.8658 | 1278.001 | 1837.8 | 2453742.0479 | 460080.36 | 208697.5633 | 0 | 207291.7622
8270 | 1638.085 | 1745.1328 | 1701.6505 | 1698.8179 | 1638.085 | 1863.5 | 3183490.8314 | 589710.6 | 267499.2805 | 0 | 223598.6025
8271 | 1340.07 | 122.2902 | 122.2902 | 119.0447 | 119.0447 | 1888.35 | 235238.0592 | 42856.0769 | 19439.9927 | 2238139.4518 | 13010.1279
8272 | 1262.195 | 409.3493 | 409.3493 | 398.4854 | 398.4854 | 1899.6 | 792642.8362 | 143454.7489 | 65072.6681 | 1583179.6717 | 39161.6224
8273 | 1317.571 | 12.207 | 12.207 | 11.883 | 11.883 | 1914.35 | 23806.8261 | 4277.8899 | 1940.4984 | 2393326.0534 | 996.1951
8274 | 1073.537 | 0 | 0 | 0 | 0 | 1927.45 | 0 | 0 | 0 | 1967793.321 | 0
8275 | 968 | 0 | 0 | 0 | 0 | 1933.9 | 0 | 0 | 0 | 3289264 | 0
8276 | 1704.8 | 0 | 0 | 0 | 0 | 1820.6 | 0 | 0 | 0 | 5792910.4 | 0
8277 | 1280 | 0 | 0 | 0 | 0 | 1798.2 | 0 | 0 | 0 | 4349440 | 0
8278 | 953.6 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1844.05 | 596044.6019 | 111351.8261 | 50510.4255 | 2189295.2863 | 47701.0503
8279 | 1074.4 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1823.1 | 1140751.2123 | 215514.4963 | 97759.7701 | 1616593.8159 | 104724.8
8280 | 1128 | 0 | 0 | 0 | 0 | 1796.65 | 0 | 0 | 0 | 2067624 | 0
8281 | 1326.4 | 0 | 0 | 0 | 0 | 1723.45 | 0 | 0 | 0 | 1578416 | 0
8282 | 1213.6 | 0 | 0 | 0 | 0 | 1774.35 | 0 | 0 | 0 | 1444184 | 0
8283 | 932 | 0 | 0 | 0 | 0 | 1765.35 | 0 | 0 | 0 | 1109080 | 0
8284 | 1318.4 | 0 | 0 | 0 | 0 | 1682.3 | 0 | 0 | 0 | 1568896 | 0
8285 | 1150.4 | 0 | 0 | 0 | 0 | 1765.9 | 0 | 0 | 0 | 1368976 | 0
8286 | 1121.6 | 0 | 0 | 0 | 0 | 1779.3 | 0 | 0 | 0 | 1334704 | 0
8287 | 1252.8 | 226.902 | 226.902 | 220.8801 | 220.8801 | 1795.25 | 413779.6924 | 79516.8401 | 36069.7222 | 1891509.1557 | 44268.588
8288 | 1217.408 | 1041.2657 | 1041.2657 | 1013.6311 | 1013.6311 | 1824.55 | 1927414.216 | 364907.1792 | 165525.951 | 373523.1432 | 174079.7355
8289 | 1302.102 | 1684.7865 | 1352.6297 | 1640.0732 | 1302.102 | 1866.95 | 2539481.2786 | 468756.72 | 212633.2566 | 0 | 173244.6711
8290 | 1274.013 | 1392.737 | 1323.4508 | 1355.7745 | 1274.013 | 1875.95 | 2500404.5704 | 458644.68 | 208046.3229 | 0 | 158041.3127
8291 | 1359.024 | 1669.1619 | 1411.7606 | 1624.8632 | 1359.024 | 1869.5 | 2658579.5182 | 489248.64 | 221928.6192 | 0 | 177352.632
8292 | 1360.939 | 3055.3138 | 1413.7499 | 2974.2275 | 1360.939 | 1810.85 | 2578320.077 | 489938.04 | 222241.3387 | 0 | 257421.6118
8293 | 1309.39 | 1946.9247 | 1360.2005 | 1895.2544 | 1309.39 | 1780.7 | 2439692.3212 | 471380.4 | 213823.387 | 0 | 287149.227
8294 | 1346.761 | 2120.1153 | 1399.0217 | 2063.8486 | 1346.761 | 1863.5 | 2625555.555 | 484833.96 | 219926.0713 | 0 | 183832.8765
8295 | 1666.961 | 1159.3217 | 1159.3217 | 1128.5539 | 1128.5539 | 1888.35 | 2230450.4604 | 406279.4097 | 184292.8544 | 986900.1853 | 123337.6337
8296 | 1629.508 | 406.5581 | 406.5581 | 395.7682 | 395.7682 | 1899.6 | 786552.3516 | 142476.5607 | 64628.951 | 2261445.0093 | 38894.5584
8297 | 1510.972 | 16.329 | 16.329 | 15.8956 | 15.8956 | 1914.35 | 31819.2605 | 5722.4195 | 2595.7531 | 2740475.0232 | 1332.6284
8298 | 1715.055 | 0 | 0 | 0 | 0 | 1927.95 | 0 | 0 | 0 | 3143695.815 | 0
8299 | 1569.6 | 0 | 0 | 0 | 0 | 1933.9 | 0 | 0 | 0 | 5333500.8 | 0
8300 | 1138.4 | 0 | 0 | 0 | 0 | 1820.1 | 0 | 0 | 0 | 3868283.2 | 0
8301 | 1421.6 | 0 | 0 | 0 | 0 | 1798.5 | 0 | 0 | 0 | 4830596.8 | 0
8302 | 1424.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1844.05 | 596810.4708 | 111351.8261 | 50510.4255 | 3790432.8863 | 47701.0503
8303 | 1243.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1823.1 | 1141868.2778 | 215514.4963 | 97759.7701 | 2190176.2159 | 104724.8
8304 | 1226.4 | 0 | 0 | 0 | 0 | 1796.65 | 0 | 0 | 0 | 2247991.2 | 0
8305 | 871.2 | 0 | 0 | 0 | 0 | 980.5 | 0 | 0 | 0 | 1036728 | 0
8306 | 1341.6 | 0 | 0 | 0 | 0 | 1604.85 | 0 | 0 | 0 | 1596504 | 0
8307 | 1340 | 0 | 0 | 0 | 0 | 1602.2 | 0 | 0 | 0 | 1594600 | 0
8308 | 1356 | 0 | 0 | 0 | 0 | 1601.25 | 0 | 0 | 0 | 1613640 | 0
8309 | 1612 | 0 | 0 | 0 | 0 | 1378.35 | 0 | 0 | 0 | 1918280 | 0
8310 | 1690.4 | 0 | 0 | 0 | 0 | 1385.45 | 0 | 0 | 0 | 2011576 | 0
8311 | 1544.8 | 243.1063 | 243.1063 | 236.6544 | 236.6544 | 1625.75 | 401892.6617 | 85195.5743 | 38645.6591 | 2397830.9342 | 86694.6383
8312 | 1215.149 | 1262.3026 | 1262.3026 | 1228.8017 | 1215.149 | 1655.05 | 2099741.4741 | 437453.64 | 198433.8317 | 0 | 419165.6476
8313 | 1492.134 | 1830.106 | 1550.0359 | 1781.5359 | 1492.134 | 1804.05 | 2817061.1844 | 537168.24 | 243665.4822 | 0 | 292383.6573
8314 | 1882.658 | 2459.4669 | 1955.713 | 2394.1939 | 1882.658 | 1864.55 | 3681914.699 | 677756.88 | 307438.0514 | 0 | 255006.0261
8315 | 1450.765 | 2500.3324 | 1507.0616 | 2433.9749 | 1450.765 | 1676.5 | 2548667.4009 | 522275.4 | 236909.9245 | 0 | 469322.4775
8316 | 1737.05 | 1884.4957 | 1804.4558 | 1834.4822 | 1737.05 | 1527.5 | 2786610.4442 | 625338 | 283660.265 | 0 | 820756.125
8317 | 1360.505 | 2412.7528 | 1413.2991 | 2348.7197 | 1360.505 | 1171.25 | 1669576.5235 | 489781.8 | 222170.4665 | 0 | 1127518.5188
8318 | 1346.552 | 2554.3035 | 1398.8046 | 2486.5137 | 1346.552 | 1525.15 | 2147607.9507 | 484758.72 | 219891.9416 | 0 | 639410.2172
8319 | 1602.583 | 873.3086 | 873.3086 | 850.1315 | 850.1315 | 1818.6 | 1620640.3589 | 306047.3307 | 138826.4697 | 1379243.6467 | 150951.6472
8320 | 1371.928 | 538.3574 | 538.3574 | 524.0697 | 524.0697 | 1888.2 | 1037989.5851 | 188665.1033 | 85580.5871 | 1554124.2065 | 57351.6112
8321 | 1617.23 | 237.3284 | 237.3284 | 231.0299 | 231.0299 | 1896.6 | 459013.1331 | 83170.7574 | 37727.1797 | 2540904.8171 | 23383.1862
8322 | 1416.264 | 0 | 0 | 0 | 0 | 1864.55 | 0 | 0 | 0 | 2596011.912 | 0
8323 | 1540.8 | 0 | 0 | 0 | 0 | 1844.2 | 0 | 0 | 0 | 5235638.4 | 0
8324 | 1249.6 | 0 | 0 | 0 | 0 | 1733.15 | 0 | 0 | 0 | 4246140.8 | 0
8325 | 1344 | 0 | 0 | 0 | 0 | 1647.4 | 0 | 0 | 0 | 4566912 | 0
8326 | 1529.6 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1695.9 | 549396.3664 | 111351.8261 | 50510.4255 | 4146543.2863 | 93016.2834
8327 | 1204 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1613.1 | 1011526.3622 | 215514.4963 | 97759.7701 | 2056974.6159 | 229044.8
8328 | 1254.4 | 0 | 0 | 0 | 0 | 1440.55 | 0 | 0 | 0 | 2299315.2 | 0
8329 | 1176.8 | 0 | 0 | 0 | 0 | 1076.15 | 0 | 0 | 0 | 2157074.4 | 0
8330 | 1458.4 | 0 | 0 | 0 | 0 | 1380.5 | 0 | 0 | 0 | 2673247.2 | 0
8331 | 1106.4 | 0 | 0 | 0 | 0 | 1555.2 | 0 | 0 | 0 | 2028031.2 | 0
8332 | 1453.6 | 0 | 0 | 0 | 0 | 1478.75 | 0 | 0 | 0 | 2664448.8 | 0
8333 | 1477.6 | 0 | 0 | 0 | 0 | 1480.25 | 0 | 0 | 0 | 2708440.8 | 0
8334 | 1080 | 0 | 0 | 0 | 0 | 1548.55 | 0 | 0 | 0 | 1979640 | 0
8335 | 1225.6 | 215.4585 | 215.4585 | 209.7403 | 209.7403 | 1658.5 | 362988.2699 | 75506.5231 | 34250.5978 | 1862070.7533 | 70111.316
8336 | 918.666 | 954.3146 | 954.3146 | 928.9876 | 918.666 | 1746.25 | 1678904.9413 | 330719.76 | 150018.1578 | 0 | 233111.4975
8337 | 1374.39 | 1870.3804 | 1427.7229 | 1820.7415 | 1374.39 | 1856.05 | 2661401.4288 | 494780.4 | 224437.887 | 0 | 197843.4405
8338 | 1560.354 | 2536.354 | 1620.9031 | 2469.0405 | 1560.354 | 1825.4 | 2974639.6112 | 561727.44 | 254805.8082 | 0 | 272437.8084
8339 | 1797.136 | 2869.1413 | 1866.8734 | 2792.9959 | 1797.136 | 1700 | 3195228.7358 | 646968.96 | 293472.3088 | 0 | 539140.8
8340 | 1185.147 | 2983.8846 | 1231.1363 | 2904.6939 | 1185.147 | 1718.3 | 2134346.4983 | 426652.92 | 193534.5051 | 0 | 333855.9099
8341 | 1448.412 | 2716.892 | 1504.6173 | 2644.7872 | 1448.412 | 1342.1 | 2033024.0355 | 521428.32 | 236525.6796 | 0 | 952910.2548
8342 | 1481.714 | 2547.2542 | 1539.2115 | 2479.6514 | 1481.714 | 1463.95 | 2271705.3221 | 533417.04 | 241963.8962 | 0 | 794272.7897
8343 | 915.477 | 2042.9207 | 951.0019 | 1988.7027 | 915.477 | 1683.95 | 1617455.8885 | 329571.72 | 149497.3941 | 0 | 289336.5059
8344 | 1225.411 | 1391.6524 | 1272.9628 | 1354.7187 | 1225.411 | 1754.15 | 2252649.7114 | 441147.96 | 200109.6163 | 0 | 301267.2943
8345 | 1517.155 | 420.9943 | 420.9943 | 409.8214 | 409.8214 | 1896.6 | 813704.6509 | 147535.6907 | 66923.8286 | 2029742.5568 | 41479.1168
8346 | 1563.602 | 0 | 0 | 0 | 0 | 1877.4 | 0 | 0 | 0 | 2866082.466 | 0
8347 | 1392 | 0 | 0 | 0 | 0 | 1818.2 | 0 | 0 | 0 | 2551536 | 0
8348 | 1641.6 | 0 | 0 | 0 | 0 | 1728.05 | 0 | 0 | 0 | 3009052.8 | 0
8349 | 1546.4 | 0 | 0 | 0 | 0 | 1666.45 | 0 | 0 | 0 | 2834551.2 | 0
8350 | 1494.4 | 0 | 0 | 0 | 0 | 1658.6 | 0 | 0 | 0 | 2739235.2 | 0
8351 | 1361.6 | 0 | 0 | 0 | 0 | 1519.7 | 0 | 0 | 0 | 2495812.8 | 0
8352 | 1280.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1230.1 | 398507.9615 | 111351.8261 | 50510.4255 | 1780740.019 | 235492.3926
8353 | 1408 | 0 | 0 | 0 | 0 | 1133.65 | 0 | 0 | 0 | 1675520 | 0
8354 | 1036.8 | 0 | 0 | 0 | 0 | 1282.6 | 0 | 0 | 0 | 1233792 | 0
8355 | 1119.2 | 0 | 0 | 0 | 0 | 1227.35 | 0 | 0 | 0 | 1331848 | 0
8356 | 1168 | 0 | 0 | 0 | 0 | 1160.9 | 0 | 0 | 0 | 1389920 | 0
8357 | 1204.8 | 0 | 0 | 0 | 0 | 1152.45 | 0 | 0 | 0 | 1433712 | 0
8358 | 1127.2 | 0 | 0 | 0 | 0 | 1158 | 0 | 0 | 0 | 1341368 | 0
8359 | 1190.4 | 874.2539 | 874.2539 | 851.0517 | 851.0517 | 1199.25 | 1065849.7722 | 306378.6115 | 138976.7424 | 622025.4366 | 671878.0957
8360 | 210.344 | 820.2371 | 218.5063 | 798.4685 | 210.344 | 1327.3 | 291271.3536 | 75723.84 | 34349.1752 | 0 | 141498.4088
8361 | 101.182 | 2100.7904 | 105.1083 | 2045.0366 | 101.182 | 1646.8 | 174249.606 | 36425.52 | 16523.0206 | 0 | 35737.4824
8362 | 0 | 2354.559 | 0 | 2292.0703 | 0 | 1654.45 | 0 | 0 | 0 | 0 | 0
8363 | 0 | 1460.5449 | 0 | 1421.7829 | 0 | 1374.85 | 0 | 0 | 0 | 0 | 0
8364 | 0 | 1978.3039 | 0 | 1925.8008 | 0 | 1283.75 | 0 | 0 | 0 | 0 | 0
8365 | 0 | 1992.7641 | 0 | 1939.8772 | 0 | 1115 | 0 | 0 | 0 | 0 | 0
8366 | 0 | 3020.4162 | 0 | 2940.256 | 0 | 1253.8 | 0 | 0 | 0 | 0 | 0
8367 | 0 | 2222.6349 | 0 | 2163.6474 | 0 | 1614.7 | 0 | 0 | 0 | 0 | 0
8368 | 0 | 1197.7564 | 0 | 1165.9686 | 0 | 1430.55 | 0 | 0 | 0 | 0 | 0
8369 | 0 | 409.6568 | 0 | 398.7847 | 0 | 1625.8 | 0 | 0 | 0 | 0 | 0
8370 | 0 | 0 | 0 | 0 | 0 | 1641.2 | 0 | 0 | 0 | 0 | 0
8371 | 0 | 0 | 0 | 0 | 0 | 1690.55 | 0 | 0 | 0 | 0 | 0
8372 | 0 | 0 | 0 | 0 | 0 | 1496.15 | 0 | 0 | 0 | 0 | 0
8373 | 137.6 | 142.9395 | 142.9395 | 139.146 | 137.6 | 1332.8 | 192530.7577 | 49536 | 22470.08 | 0 | 91806.72
8374 | 224 | 232.6923 | 232.6923 | 226.5167 | 224 | 1432.25 | 335712.7675 | 80640 | 36579.2 | 0 | 127176
8375 | 279.2 | 290.0343 | 290.0343 | 282.3369 | 279.2 | 1162.95 | 339917.3088 | 100512 | 45593.36 | 0 | 233704.36
8376 | 275.2 | 108.7525 | 108.7525 | 105.8662 | 105.8662 | 992.5 | 110081.129 | 38111.8456 | 17287.9566 | 310388.786 | 103776.53
8377 | 272 | 0 | 0 | 0 | 0 | 1033.85 | 0 | 0 | 0 | 323680 | 0
8378 | 291.2 | 0 | 0 | 0 | 0 | 1007.1 | 0 | 0 | 0 | 346528 | 0
8379 | 199.2 | 0 | 0 | 0 | 0 | 1003.4 | 0 | 0 | 0 | 237048 | 0
8380 | 207.2 | 0 | 0 | 0 | 0 | 1002.4 | 0 | 0 | 0 | 246568 | 0
8381 | 285.6 | 0 | 0 | 0 | 0 | 1002.5 | 0 | 0 | 0 | 339864 | 0
8382 | 264 | 0 | 0 | 0 | 0 | 1003.4 | 0 | 0 | 0 | 314160 | 0
8383 | 318.4 | 330.7554 | 330.7554 | 321.9774 | 318.4 | 1004.8 | 333506.3118 | 114624 | 51994.72 | 0 | 316871.68
8384 | 138.494 | 832.467 | 143.8682 | 810.3737 | 138.494 | 1111.65 | 160640.1339 | 49857.84 | 22616.0702 | 0 | 123031.1449
8385 | 740.535 | 2122.0392 | 769.2713 | 2065.7214 | 740.535 | 1155.05 | 893937.5692 | 266592.6 | 120929.3655 | 0 | 625715.0483
8386 | 1328.616 | 2854.0901 | 1380.1726 | 2778.3441 | 1328.616 | 1163.35 | 1617315.7585 | 478301.76 | 216962.9928 | 0 | 1111586.5764
8387 | 1321.969 | 3644.8573 | 1373.2677 | 3548.1248 | 1321.969 | 1103 | 1526864.6622 | 475908.84 | 215877.5377 | 0 | 1185806.193
8388 | 1360.73 | 3585.1198 | 1413.5328 | 3489.9727 | 1360.73 | 1165.8 | 1663582.6178 | 489862.8 | 222207.209 | 0 | 1135120.966
8389 | 1345.146 | 2862.0982 | 1397.3441 | 2786.1397 | 1345.146 | 1115.3 | 1574051.6365 | 484252.56 | 219662.3418 | 0 | 1190050.6662
8390 | 1049.667 | 2368.2494 | 1090.3991 | 2305.3974 | 1049.667 | 1083.45 | 1190710.932 | 377880.12 | 171410.6211 | 0 | 962072.2889
8391 | 978.516 | 2141.6425 | 1016.4871 | 2084.8044 | 978.516 | 1034.6 | 1061983.7861 | 352265.76 | 159791.6628 | 0 | 944659.3464
8392 | 1113.713 | 663.4503 | 663.4503 | 645.8427 | 645.8427 | 1046.5 | 707951.0176 | 232503.3729 | 105466.1133 | 857606.2551 | 602784.5835
8393 | 1271.929 | 119.9653 | 119.9653 | 116.7815 | 116.7815 | 1099.15 | 134459.0557 | 42041.3447 | 19070.4211 | 2117385.3434 | 102977.0644
8394 | 1081.973 | 0 | 0 | 0 | 0 | 1248.45 | 0 | 0 | 0 | 1983256.509 | 0
8395 | 1176.8 | 0 | 0 | 0 | 0 | 1367.95 | 0 | 0 | 0 | 3998766.4 | 0
8396 | 942.4 | 0 | 0 | 0 | 0 | 1281.25 | 0 | 0 | 0 | 3202275.2 | 0
8397 | 892.8 | 0 | 0 | 0 | 0 | 1211.45 | 0 | 0 | 0 | 3033734.4 | 0
8398 | 998.4 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1175.4 | 381675.0715 | 111351.8261 | 50510.4255 | 2341525.6863 | 252223.7004
8399 | 1292 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1078.3 | 677142.2603 | 215514.4963 | 97759.7701 | 2355998.6159 | 545646.4
8400 | 1080.8 | 0 | 0 | 0 | 0 | 1033.55 | 0 | 0 | 0 | 1981106.4 | 0
8401 | 1272.8 | 0 | 0 | 0 | 0 | 1162.85 | 0 | 0 | 0 | 1514632 | 0
8402 | 1246.4 | 0 | 0 | 0 | 0 | 962.75 | 0 | 0 | 0 | 1483216 | 0
8403 | 1290.4 | 0 | 0 | 0 | 0 | 618.75 | 0 | 0 | 0 | 1535576 | 0
8404 | 856 | 0 | 0 | 0 | 0 | 962.45 | 0 | 0 | 0 | 1018640 | 0
8405 | 1009.6 | 0 | 0 | 0 | 0 | 963.95 | 0 | 0 | 0 | 1201424 | 0
8406 | 1304.8 | 0 | 0 | 0 | 0 | 971 | 0 | 0 | 0 | 1552712 | 0
8407 | 1032.8 | 197.0072 | 197.0072 | 191.7788 | 191.7788 | 1265.65 | 252351.1963 | 69040.3601 | 31317.4745 | 1541591.8998 | 137853.6507
8408 | 1361.032 | 1238.865 | 1238.865 | 1205.9862 | 1205.9862 | 1615.95 | 2027722.3133 | 434155.0448 | 196937.5523 | 284198.8861 | 453361.4238
8409 | 1132.013 | 1306.297 | 1175.9405 | 1271.6286 | 1132.013 | 1672 | 1974209.7126 | 407524.68 | 184857.7229 | 0 | 371300.264
8410 | 1598.971 | 2223.0328 | 1661.0187 | 2164.0347 | 1598.971 | 1572.55 | 2630755.8023 | 575629.56 | 261111.9643 | 0 | 683480.154
8411 | 1537.183 | 3753.3906 | 1596.833 | 3653.7777 | 1537.183 | 1331.8 | 2141045.1745 | 553385.88 | 251021.9839 | 0 | 1027145.6806
8412 | 1425.846 | 4067.011 | 1481.1756 | 3959.0747 | 1425.846 | 1209.35 | 1804756.6752 | 513304.56 | 232840.6518 | 0 | 1127345.1399
8413 | 1392.659 | 3866.7325 | 1446.7008 | 3764.1116 | 1392.659 | 1198.7 | 1748695.503 | 501357.24 | 227421.2147 | 0 | 1115937.6567
8414 | 1295.781 | 2165.9962 | 1346.0635 | 2108.5118 | 1295.781 | 1320.15 | 1784452.0592 | 466481.16 | 211601.0373 | 0 | 880936.7129
8415 | 1618.778 | 2473.0929 | 1681.5943 | 2407.4583 | 1618.778 | 1631.65 | 2753547.6949 | 582760.08 | 264346.4474 | 0 | 596276.8763
8416 | 1607.397 | 1585.5256 | 1585.5256 | 1543.4466 | 1543.4466 | 1782.6 | 2859929.9981 | 555640.7848 | 252044.8338 | 117221.0384 | 328447.4852
8417 | 1627.259 | 177.6917 | 177.6917 | 172.9759 | 172.9759 | 1811.8 | 325452.8499 | 62271.3119 | 28246.959 | 2665700.9839 | 31865.4594
8418 | 1365.124 | 0 | 0 | 0 | 0 | 1910.2 | 0 | 0 | 0 | 2502272.292 | 0
8419 | 1428 | 0 | 0 | 0 | 0 | 1922.5 | 0 | 0 | 0 | 4852344 | 0
8420 | 1173.6 | 0 | 0 | 0 | 0 | 1817.9 | 0 | 0 | 0 | 3987892.8 | 0
8421 | 1508 | 0 | 0 | 0 | 0 | 1713.75 | 0 | 0 | 0 | 5124184 | 0
8422 | 1451.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1793.5 | 578054.3124 | 111351.8261 | 50510.4255 | 3880140.0863 | 63162.981
8423 | 1724 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1706.1 | 1061861.7342 | 215514.4963 | 97759.7701 | 3823934.6159 | 173988.8
8424 | 1598.4 | 0 | 0 | 0 | 0 | 1612.6 | 0 | 0 | 0 | 2929867.2 | 0
8425 | 1463.2 | 0 | 0 | 0 | 0 | 1304.15 | 0 | 0 | 0 | 1741208 | 0
8426 | 1581.6 | 0 | 0 | 0 | 0 | 1278.55 | 0 | 0 | 0 | 1882104 | 0
8427 | 1542.4 | 0 | 0 | 0 | 0 | 1275.95 | 0 | 0 | 0 | 1835456 | 0
8428 | 1321.6 | 0 | 0 | 0 | 0 | 1333.1 | 0 | 0 | 0 | 1572704 | 0
8429 | 1266.4 | 0 | 0 | 0 | 0 | 1386.45 | 0 | 0 | 0 | 1507016 | 0
8430 | 1100 | 0 | 0 | 0 | 0 | 1301.65 | 0 | 0 | 0 | 1309000 | 0
8431 | 1120 | 212.4782 | 212.4782 | 206.8391 | 206.8391 | 1564.5 | 335789.1894 | 74462.0787 | 33776.8262 | 1673823.9161 | 88173.072
8432 | 977.25 | 1015.1719 | 1015.1719 | 988.2298 | 977.25 | 1720.55 | 1746740.9593 | 351810 | 159584.925 | 0 | 273092.5125
8433 | 1164.458 | 1435.4588 | 1209.6445 | 1397.3625 | 1164.458 | 1777.75 | 2157130.7685 | 419204.88 | 190155.9914 | 0 | 258800.7905
8434 | 1811.107 | 2362.9422 | 1881.3866 | 2300.231 | 1811.107 | 1711.95 | 3241630.3688 | 651998.52 | 295753.7731 | 0 | 521689.3714
8435 | 1589.091 | 3189.462 | 1650.7553 | 3104.8154 | 1589.091 | 1218.7 | 2027556.7404 | 572072.76 | 259498.5603 | 0 | 1241556.7983
8436 | 1463.659 | 3123.7337 | 1520.4559 | 3040.8315 | 1463.659 | 1051.85 | 1617275.8889 | 526917.24 | 239015.5147 | 0 | 1387768.2808
8437 | 1438.004 | 2777.6756 | 1493.8054 | 2703.9576 | 1438.004 | 1209.9 | 1826292.7845 | 517681.44 | 234826.0532 | 0 | 1136166.9604
8438 | 1439.024 | 2236.8281 | 1494.865 | 2177.4639 | 1439.024 | 1229.9 | 1856596.3831 | 518048.64 | 234992.6192 | 0 | 1108192.3824
8439 | 1791.185 | 1044.9856 | 1044.9856 | 1017.2523 | 1017.2523 | 1364.75 | 1449935.859 | 366210.8235 | 166117.2985 | 1418618.6621 | 632540.0235
8440 | 1612.223 | 622.7385 | 622.7385 | 606.2114 | 606.2114 | 1679.6 | 1059614.7119 | 218236.0949 | 98994.3175 | 1844019.3094 | 190121.5152
8441 | 1277.059 | 80.5957 | 80.5957 | 78.4567 | 78.4567 | 1765.9 | 144113.4685 | 28244.4125 | 12811.9793 | 2197038.0134 | 17978.1777
8442 | 1399.92 | 0 | 0 | 0 | 0 | 1814.75 | 0 | 0 | 0 | 2566053.36 | 0
8443 | 1373.6 | 0 | 0 | 0 | 0 | 1898.2 | 0 | 0 | 0 | 4667492.8 | 0
8444 | 1170.4 | 0 | 0 | 0 | 0 | 1793.6 | 0 | 0 | 0 | 3977019.2 | 0
8445 | 1194.4 | 0 | 0 | 0 | 0 | 1712.45 | 0 | 0 | 0 | 4058571.2 | 0
8446 | 1397.6 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1728.35 | 558481.7641 | 111351.8261 | 50510.4255 | 3698007.2863 | 83090.6721
8447 | 1476 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1642.2 | 1027306.2936 | 215514.4963 | 97759.7701 | 2981230.6159 | 211817.6
8448 | 1419.2 | 0 | 0 | 0 | 0 | 1551.35 | 0 | 0 | 0 | 2601393.6 | 0
8449 | 1497.6 | 0 | 0 | 0 | 0 | 1476.85 | 0 | 0 | 0 | 1782144 | 0
8450 | 1310.4 | 0 | 0 | 0 | 0 | 1278.65 | 0 | 0 | 0 | 1559376 | 0
8451 | 1341.6 | 0 | 0 | 0 | 0 | 1276 | 0 | 0 | 0 | 1596504 | 0
8452 | 1416 | 0 | 0 | 0 | 0 | 1275.05 | 0 | 0 | 0 | 1685040 | 0
8453 | 957.6 | 0 | 0 | 0 | 0 | 1290.15 | 0 | 0 | 0 | 1139544 | 0
8454 | 1168 | 0 | 0 | 0 | 0 | 1575.7 | 0 | 0 | 0 | 1389920 | 0
8455 | 1116.8 | 227.1565 | 227.1565 | 221.1279 | 221.1279 | 1658.5 | 384015.3997 | 79606.0311 | 36110.1802 | 1641767.025 | 73918.0165
8456 | 1100.114 | 1142.8036 | 1142.8036 | 1112.4743 | 1100.114 | 1722.75 | 1989203.386 | 396041.04 | 179648.6162 | 0 | 305006.6065
8457 | 1505.134 | 1563.5403 | 1563.5403 | 1522.0448 | 1505.134 | 1719 | 2721724.6391 | 541848.24 | 245788.3822 | 0 | 422942.654
8458 | 1372.623 | 2203.8627 | 1425.8873 | 2145.3734 | 1372.623 | 1619.25 | 2346224.3926 | 494144.28 | 224149.3359 | 0 | 522626.2072
8459 | 1730.814 | 2964.5576 | 1797.9778 | 2885.8799 | 1730.814 | 1331.8 | 2422414.7885 | 623093.04 | 282641.9262 | 0 | 1156529.9148
8460 | 1451.75 | 2930.3217 | 1508.0848 | 2852.5526 | 1451.75 | 1268.85 | 1937294.1383 | 522630 | 237070.775 | 0 | 1061447.0125
8461 | 1419.609 | 2127.9759 | 1474.6966 | 2071.5006 | 1419.609 | 1342 | 2001988.4028 | 511059.24 | 231822.1497 | 0 | 934102.722
8462 | 1566.858 | 2602.9642 | 1627.6595 | 2533.883 | 1566.858 | 1333.7 | 2191997.3867 | 564068.88 | 255867.9114 | 0 | 1043997.4854
8463 | 1497.729 | 1959.7696 | 1555.848 | 1907.7583 | 1497.729 | 1381.2 | 2167614.7878 | 539182.44 | 244579.1457 | 0 | 926794.7052
8464 | 1156.838 | 1369.7648 | 1201.7288 | 1333.412 | 1156.838 | 1549.1 | 1869900.4032 | 416461.68 | 188911.6454 | 0 | 521618.2542
8465 | 1305.359 | 436.0217 | 436.0217 | 424.4499 | 424.4499 | 1765.9 | 781508.6194 | 152801.9621 | 69312.6678 | 1614706.3899 | 97261.7611
8466 | 1419.829 | 0 | 0 | 0 | 0 | 1842.45 | 0 | 0 | 0 | 2602546.557 | 0
8467 | 1196 | 0 | 0 | 0 | 0 | 1922.5 | 0 | 0 | 0 | 4064008 | 0
8468 | 1183.2 | 0 | 0 | 0 | 0 | 1820.1 | 0 | 0 | 0 | 4020513.6 | 0
8469 | 1408.8 | 0 | 0 | 0 | 0 | 1798.2 | 0 | 0 | 0 | 4787102.4 | 0
8470 | 1412 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1832.65 | 592805.5382 | 111351.8261 | 50510.4255 | 3746938.4863 | 51188.0139
8471 | 1347.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1722.75 | 1078429.1309 | 215514.4963 | 97759.7701 | 2543568.2159 | 164132
8472 | 1276 | 0 | 0 | 0 | 0 | 1705.5 | 0 | 0 | 0 | 2338908 | 0
8473 | 1184 | 0 | 0 | 0 | 0 | 1597.75 | 0 | 0 | 0 | 1408960 | 0
8474 | 1453.6 | 0 | 0 | 0 | 0 | 1529.05 | 0 | 0 | 0 | 1729784 | 0
8475 | 1312.8 | 0 | 0 | 0 | 0 | 1352.1 | 0 | 0 | 0 | 1562232 | 0
8476 | 1127.2 | 0 | 0 | 0 | 0 | 1308.1 | 0 | 0 | 0 | 1341368 | 0
8477 | 1457.6 | 0 | 0 | 0 | 0 | 1284.6 | 0 | 0 | 0 | 1734544 | 0
8478 | 1394.4 | 0 | 0 | 0 | 0 | 1529.25 | 0 | 0 | 0 | 1659336 | 0
8479 | 1288.8 | 68.5258 | 68.5258 | 66.7072 | 66.7072 | 1638.85 | 114047.2144 | 24014.5765 | 10893.2787 | 2240096.1816 | 23581.6504
8480 | 1161.104 | 582.0859 | 582.0859 | 566.6377 | 566.6377 | 1686.5 | 998187.0173 | 203989.5673 | 92531.9343 | 1089656.7517 | 173883.0885
8481 | 829.113 | 1099.4606 | 861.2865 | 1070.2815 | 829.113 | 1686.55 | 1462286.5517 | 298480.68 | 135394.1529 | 0 | 259885.4698
8482 | 1028.635 | 1693.4159 | 1068.5509 | 1648.4735 | 1028.635 | 1680.5 | 1808766.6191 | 370308.6 | 167976.0955 | 0 | 328648.8825
8483 | 1605.522 | 3118.2394 | 1667.8239 | 3035.4831 | 1605.522 | 1267.1 | 2127519.0986 | 577987.92 | 262181.7426 | 0 | 1176687.0738
8484 | 1388.834 | 3265.8286 | 1442.7274 | 3179.1553 | 1388.834 | 1051.85 | 1530440.9722 | 499980.24 | 226796.5922 | 0 | 1316822.9571
8485 | 1422.415 | 2718.3349 | 1477.6115 | 2646.1918 | 1422.415 | 1161.6 | 1725132.4304 | 512069.4 | 232280.3695 | 0 | 1192552.736
8486 | 1624.992 | 2754.4573 | 1688.0494 | 2681.3555 | 1624.992 | 1278.2 | 2170316.0868 | 584997.12 | 265361.1936 | 0 | 1172919.2256
8487 | 1558.054 | 1791.5216 | 1618.5139 | 1743.9756 | 1558.054 | 1364.75 | 2218724.8453 | 560899.44 | 254430.2182 | 0 | 989753.8035
8488 | 1796.174 | 280.3298 | 280.3298 | 272.89 | 272.89 | 1494.35 | 425793.899 | 98240.3901 | 44562.9325 | 2792179.6225 | 135067.7111
8489 | 1733.951 | 214.1049 | 214.1049 | 208.4227 | 208.4227 | 1751.65 | 381493.854 | 75032.1728 | 34035.4273 | 2796293.37 | 50666.6285
8490 | 1379.821 | 0 | 0 | 0 | 0 | 1812.55 | 0 | 0 | 0 | 2529211.893 | 0
8491 | 1425.6 | 0 | 0 | 0 | 0 | 1922.5 | 0 | 0 | 0 | 4844188.8 | 0
8492 | 1449.6 | 0 | 0 | 0 | 0 | 1778.75 | 0 | 0 | 0 | 4925740.8 | 0
8493 | 1551.2 | 0 | 0 | 0 | 0 | 1772.2 | 0 | 0 | 0 | 5270977.6 | 0
8494 | 1432.8 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1741.5 | 562457.7237 | 111351.8261 | 50510.4255 | 3817616.8863 | 79068.429
8495 | 1576.8 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1705.1 | 1065339.801 | 215514.4963 | 97759.7701 | 3323749.0159 | 174580.8
8496 | 1746.4 | 0 | 0 | 0 | 0 | 1690.05 | 0 | 0 | 0 | 3201151.2 | 0
8497 | 704 | 0 | 0 | 0 | 0 | 1630.5 | 0 | 0 | 0 | 1290432 | 0
8498 | 883.2 | 0 | 0 | 0 | 0 | 1575.75 | 0 | 0 | 0 | 1618905.6 | 0
8499 | 1075.2 | 0 | 0 | 0 | 0 | 1395.9 | 0 | 0 | 0 | 1970841.6 | 0
8500 | 876.8 | 0 | 0 | 0 | 0 | 1293.1 | 0 | 0 | 0 | 1607174.4 | 0
8501 | 927.2 | 0 | 0 | 0 | 0 | 1284.6 | 0 | 0 | 0 | 1699557.6 | 0
8502 | 720.8 | 0 | 0 | 0 | 0 | 1443.5 | 0 | 0 | 0 | 1321226.4 | 0
8503 | 638.4 | 157.5368 | 157.5368 | 153.3559 | 153.3559 | 1643.95 | 263076.2464 | 55208.1155 | 25043.0146 | 889085.8785 | 53447.3776
8504 | 622.722 | 646.8866 | 646.8866 | 629.7186 | 622.722 | 1687.8 | 1096380.6484 | 224179.92 | 101690.5026 | 0 | 194413.8084
8505 | 603.316 | 2052.4071 | 626.7275 | 1997.9373 | 603.316 | 1541.95 | 969038.4496 | 217193.76 | 98521.5028 | 0 | 276348.8938
8506 | 1098.458 | 3416.7015 | 1141.0834 | 3326.0241 | 1098.458 | 1326.85 | 1519081.1147 | 395444.88 | 179378.1914 | 0 | 739427.0027
8507 | 979.053 | 3443.2316 | 1017.0449 | 3351.8501 | 979.053 | 1127.25 | 1155785.5117 | 352459.08 | 159879.3549 | 0 | 854468.5058
8508 | 716.923 | 3554.527 | 744.743 | 3460.1918 | 716.923 | 1051.85 | 793756.0417 | 258092.28 | 117073.5259 | 0 | 679750.5425
8509 | 680.172 | 3430.7763 | 706.5659 | 3339.7254 | 680.172 | 1095.55 | 781569.1301 | 244861.92 | 111072.0876 | 0 | 615181.5654
8510 | 780.334 | 3037.8505 | 810.6147 | 2957.2276 | 780.334 | 1104.35 | 901687.352 | 280920.24 | 127428.5422 | 0 | 698906.1471
8511 | 882.579 | 2281.7045 | 916.8273 | 2221.1493 | 882.579 | 1294.9 | 1191246.6832 | 317728.44 | 144125.1507 | 0 | 622306.4529
8512 | 842.753 | 2104.071 | 875.4558 | 2048.2301 | 842.753 | 1392.4 | 1218303.2572 | 303391.08 | 137621.5649 | 0 | 512056.7228
8513 | 490.41 | 898.1475 | 509.4402 | 874.3111 | 490.41 | 1751.65 | 896433.5396 | 176547.6 | 80083.953 | 0 | 121793.3235
8514 | 678.563 | 0 | 0 | 0 | 0 | 1877.4 | 0 | 0 | 0 | 1243805.979 | 0
8515 | 853.6 | 0 | 0 | 0 | 0 | 1922.5 | 0 | 0 | 0 | 1564648.8 | 0
8516 | 705.6 | 0 | 0 | 0 | 0 | 1830.75 | 0 | 0 | 0 | 1293364.8 | 0
8517 | 828.8 | 0 | 0 | 0 | 0 | 1798.5 | 0 | 0 | 0 | 1519190.4 | 0
8518 | 820 | 0 | 0 | 0 | 0 | 1832.65 | 0 | 0 | 0 | 1503060 | 0
8519 | 755.2 | 0 | 0 | 0 | 0 | 1772.55 | 0 | 0 | 0 | 1384281.6 | 0
8520 | 697.6 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1705.5 | 547254.9092 | 111351.8261 | 50510.4255 | 711734.419 | 90079.893
8521 | 1381.6 | 0 | 0 | 0 | 0 | 1669.3 | 0 | 0 | 0 | 1644104 | 0
8522 | 1472 | 0 | 0 | 0 | 0 | 1608.85 | 0 | 0 | 0 | 1751680 | 0
8523 | 1526.4 | 0 | 0 | 0 | 0 | 1665.05 | 0 | 0 | 0 | 1816416 | 0
8524 | 1505.6 | 0 | 0 | 0 | 0 | 1667.05 | 0 | 0 | 0 | 1791664 | 0
8525 | 1336.8 | 0 | 0 | 0 | 0 | 1669.35 | 0 | 0 | 0 | 1590792 | 0
8526 | 1504 | 0 | 0 | 0 | 0 | 1676.2 | 0 | 0 | 0 | 1789760 | 0
8527 | 1156.8 | 653.9691 | 653.9691 | 636.6132 | 636.6132 | 1686.55 | 1122615.455 | 229180.7364 | 103958.9285 | 953502.4836 | 197209.8886
8528 | 151.282 | 157.1525 | 157.1525 | 152.9817 | 151.282 | 1763.4 | 278975.7912 | 54461.52 | 24704.3506 | 0 | 35793.3212
8529 | 203.767 | 686.1014 | 211.6741 | 667.8927 | 203.767 | 1845.4 | 393246.4361 | 73356.12 | 33275.1511 | 0 | 31502.3782
8530 | 271.406 | 1889.7967 | 281.9378 | 1839.6425 | 271.406 | 1753.75 | 499123.717 | 97706.16 | 44320.5998 | 0 | 66833.7275
8531 | 225.678 | 2923.7399 | 234.4354 | 2846.1454 | 225.678 | 1345.8 | 318594.9479 | 81244.08 | 36853.2174 | 0 | 147638.5476
8532 | 210.894 | 2932.764 | 219.0777 | 2854.93 | 210.894 | 1243.25 | 275586.7908 | 75921.84 | 34438.9902 | 0 | 159594.0345
8533 | 235.761 | 2347.5325 | 244.9096 | 2285.2303 | 235.761 | 1201.9 | 297667.593 | 84873.96 | 38499.7713 | 0 | 188160.8541
8534 | 236.032 | 1541.3774 | 245.1912 | 1500.4701 | 236.032 | 1312.8 | 323893.3694 | 84971.52 | 38544.0256 | 0 | 162201.1904
8535 | 258.885 | 1153.0826 | 268.931 | 1122.4804 | 258.885 | 1707.4 | 461888.8912 | 93198.6 | 42275.9205 | 0 | 75749.751
8536 | 263.906 | 563.9349 | 274.1468 | 548.9684 | 263.906 | 1826.7 | 500119.2511 | 95006.16 | 43095.8498 | 0 | 45734.9098
8537 | 505.286 | 247.6365 | 247.6365 | 241.0644 | 241.0644 | 1840.9 | 460723.4894 | 86783.1735 | 39365.8118 | 484318.2463 | 37542.0315
8538 | 457.786 | 0 | 0 | 0 | 0 | 1886.5 | 0 | 0 | 0 | 839121.738 | 0
8539 | 296 | 0 | 0 | 0 | 0 | 1889.15 | 0 | 0 | 0 | 1005808 | 0
8540 | 264.8 | 144.0552 | 144.0552 | 140.2321 | 140.2321 | 1785.65 | 261488.9454 | 50483.5427 | 22899.8959 | 423281.8501 | 29724.7719
8541 | 239.2 | 248.4821 | 248.4821 | 241.8875 | 239.2 | 1770.95 | 440446.1521 | 86112 | 39061.36 | 0 | 54788.76
8542 | 282.4 | 293.3585 | 293.3585 | 285.5729 | 282.4 | 1818.05 | 532754.2617 | 101664 | 46115.92 | 0 | 51382.68
8543 | 237.6 | 246.82 | 246.82 | 240.2695 | 237.6 | 1762.9 | 434704.7272 | 85536 | 38800.08 | 0 | 56334.96
8544 | 223.2 | 0 | 0 | 0 | 0 | 1683.5 | 0 | 0 | 0 | 409125.6 | 0
8545 | 259.2 | 0 | 0 | 0 | 0 | 1421.9 | 0 | 0 | 0 | 308448 | 0
8546 | 218.4 | 0 | 0 | 0 | 0 | 1585.75 | 0 | 0 | 0 | 259896 | 0
8547 | 200 | 0 | 0 | 0 | 0 | 1582.05 | 0 | 0 | 0 | 238000 | 0
8548 | 210.4 | 0 | 0 | 0 | 0 | 1566.5 | 0 | 0 | 0 | 250376 | 0
8549 | 123.2 | 0 | 0 | 0 | 0 | 1519.9 | 0 | 0 | 0 | 146608 | 0
8550 | 180 | 0 | 0 | 0 | 0 | 1582.05 | 0 | 0 | 0 | 214200 | 0
8551 | 153.6 | 78.7393 | 78.7393 | 76.6496 | 76.6496 | 1598 | 128385.2063 | 27593.8645 | 12516.8835 | 141050.0399 | 30161.256
8552 | 243.992 | 253.46 | 253.46 | 246.7334 | 243.992 | 1592.7 | 406806.26 | 87837.12 | 39843.8936 | 0 | 99377.9416
8553 | 437.884 | 1090.0365 | 454.8749 | 1061.1075 | 437.884 | 1409.85 | 646187.3285 | 157638.24 | 71506.4572 | 0 | 258417.2426
8554 | 969.506 | 2024.9359 | 1007.1274 | 1971.1952 | 969.506 | 1304.25 | 1321217.5448 | 349022.16 | 158320.3298 | 0 | 674533.7995
8555 | 1470.638 | 2402.5507 | 1527.7057 | 2338.7884 | 1470.638 | 1306.4 | 2005761.7476 | 529429.68 | 240155.1854 | 0 | 1020034.5168
8556 | 1520.337 | 2895.1873 | 1579.3333 | 2818.3506 | 1520.337 | 1300.7 | 2066124.9501 | 547321.32 | 248271.0321 | 0 | 1063171.6641
8557 | 1436.091 | 2911.9349 | 1491.8181 | 2834.6537 | 1436.091 | 1188.6 | 1785141.7975 | 516992.76 | 234513.6603 | 0 | 1165244.2374
8558 | 1653.246 | 2277.9191 | 1717.3998 | 2217.4644 | 1653.246 | 1187.15 | 2046739.6854 | 595168.56 | 269975.0718 | 0 | 1343841.0111
8559 | 1597.991 | 1938.2954 | 1660.0006 | 1886.8541 | 1597.991 | 1259.6 | 2097440.9242 | 575276.76 | 260951.9303 | 0 | 1183152.5364
8560 | 1630.98 | 307.8124 | 307.8124 | 299.6432 | 299.6432 | 1313.5 | 410268.2245 | 107871.5582 | 48931.7374 | 2440340.3229 | 201353.196
8561 | 1716.665 | 596.598 | 596.598 | 580.7646 | 580.7646 | 1560 | 941906.4079 | 209075.2726 | 94838.8667 | 2082105.3487 | 250131.2
8562 | 1572.735 | 0 | 0 | 0 | 0 | 1707.15 | 0 | 0 | 0 | 2882823.255 | 0
8563 | 1589.6 | 0 | 0 | 0 | 0 | 1818.45 | 0 | 0 | 0 | 5401460.8 | 0
8564 | 1557.6 | 0 | 0 | 0 | 0 | 1716.35 | 0 | 0 | 0 | 5292724.8 | 0
8565 | 1602.4 | 0 | 0 | 0 | 0 | 1711.6 | 0 | 0 | 0 | 5444955.2 | 0
8566 | 1444 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1655.15 | 535092.8959 | 111351.8261 | 50510.4255 | 3855674.4863 | 105480.6489
8567 | 1375.2 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1485.4 | 929501.3574 | 215514.4963 | 97759.7701 | 2638712.2159 | 304643.2
8568 | 1093.6 | 0 | 0 | 0 | 0 | 1275.55 | 0 | 0 | 0 | 2004568.8 | 0
8569 | 1228 | 0 | 0 | 0 | 0 | 1463.7 | 0 | 0 | 0 | 1461320 | 0
8570 | 1288 | 0 | 0 | 0 | 0 | 1254.75 | 0 | 0 | 0 | 1532720 | 0
8571 | 1141.6 | 0 | 0 | 0 | 0 | 1242.6 | 0 | 0 | 0 | 1358504 | 0
8572 | 1294.4 | 0 | 0 | 0 | 0 | 1241.15 | 0 | 0 | 0 | 1540336 | 0
8573 | 1065.6 | 0 | 0 | 0 | 0 | 1259.55 | 0 | 0 | 0 | 1268064 | 0
8574 | 829.6 | 0 | 0 | 0 | 0 | 1432.15 | 0 | 0 | 0 | 987224 | 0
8575 | 1029.6 | 214.8435 | 214.8435 | 209.1417 | 209.1417 | 1658.5 | 362379.9441 | 75291.0086 | 34152.8381 | 1503900.0813 | 69911.197
8576 | 822.307 | 854.2164 | 854.2164 | 831.546 | 822.307 | 1785.4 | 1533743.0542 | 296030.52 | 134282.7331 | 0 | 176467.0822
8577 | 592.193 | 2022.1425 | 615.1729 | 1968.476 | 592.193 | 1831.75 | 1134483.3576 | 213189.48 | 96705.1169 | 0 | 99636.4723
8578 | 240.544 | 3316.701 | 249.8782 | 3228.6776 | 240.544 | 1717.15 | 433273.5218 | 86595.84 | 39280.8352 | 0 | 68037.8704
8579 | 160.732 | 2862.0982 | 166.9692 | 2786.1397 | 160.732 | 1229.9 | 207533.3461 | 57863.52 | 26247.5356 | 0 | 123779.7132
8580 | 234.455 | 2722.2678 | 243.553 | 2650.0203 | 234.455 | 1197.75 | 295079.4421 | 84403.8 | 38286.5015 | 0 | 188091.5237
8581 | 799.112 | 3543.7868 | 830.1213 | 3449.7367 | 799.112 | 1196.25 | 1001690.525 | 287680.32 | 130494.9896 | 0 | 642286.27
8582 | 1280.093 | 2857.7217 | 1329.7667 | 2781.8794 | 1280.093 | 1345.15 | 1793425.2645 | 460833.48 | 209039.1869 | 0 | 838268.901
8583 | 1234.242 | 1961.9459 | 1282.1365 | 1909.8769 | 1234.242 | 1738.5 | 2234385.5877 | 444327.12 | 201551.7186 | 0 | 322754.283
8584 | 1396.75 | 935.2048 | 935.2048 | 910.3849 | 910.3849 | 1849.05 | 1754574.5492 | 327738.5735 | 148665.8585 | 891507.1797 | 134515.6207
8585 | 1167.432 | 461.463 | 461.463 | 449.2161 | 449.2161 | 1902.95 | 891223.8433 | 161717.7823 | 73356.9829 | 1316489.8147 | 42674.2437
8586 | 1508.661 | 5.033 | 5.033 | 4.8994 | 4.8994 | 1916.55 | 9808.9817 | 1763.7968 | 800.0778 | 2756394.9474 | 400.2262
8587 | 1127.2 | 0 | 0 | 0 | 0 | 1928.2 | 0 | 0 | 0 | 3830225.6 | 0
8588 | 1019.2 | 0 | 0 | 0 | 0 | 1869.9 | 0 | 0 | 0 | 3463241.6 | 0
8589 | 1018.4 | 0 | 0 | 0 | 0 | 1811.35 | 0 | 0 | 0 | 3460523.2 | 0
8590 | 1072 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1832.65 | 592550.6622 | 111351.8261 | 50510.4255 | 2591618.4863 | 51188.0139
8591 | 1246.4 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1772.55 | 1108814.3489 | 215514.4963 | 97759.7701 | 2201049.8159 | 134650.4
8592 | 1248 | 0 | 0 | 0 | 0 | 1705.5 | 0 | 0 | 0 | 2287584 | 0
8593 | 1350.4 | 0 | 0 | 0 | 0 | 1680 | 0 | 0 | 0 | 1606976 | 0
8594 | 1180.8 | 0 | 0 | 0 | 0 | 1669.05 | 0 | 0 | 0 | 1405152 | 0
8595 | 1263.2 | 0 | 0 | 0 | 0 | 1667.7 | 0 | 0 | 0 | 1503208 | 0
8596 | 924 | 0 | 0 | 0 | 0 | 1666.75 | 0 | 0 | 0 | 1099560 | 0
8597 | 1158.4 | 0 | 0 | 0 | 0 | 1666.95 | 0 | 0 | 0 | 1378496 | 0
8598 | 944.8 | 0 | 0 | 0 | 0 | 1675 | 0 | 0 | 0 | 1124312 | 0
8599 | 1162.4 | 190.8918 | 190.8918 | 185.8256 | 185.8256 | 1716.95 | 331155.6348 | 66897.2286 | 30345.3262 | 1790060.8109 | 51485.3797
8600 | 1102.325 | 1145.1004 | 1145.1004 | 1114.7101 | 1102.325 | 1775.95 | 2030005.356 | 396837 | 180009.6725 | 0 | 246975.9162
8601 | 1299.188 | 1349.6027 | 1349.6027 | 1313.7849 | 1299.188 | 1856.05 | 2505612.5883 | 467707.68 | 212157.4004 | 0 | 187018.1126
8602 | 1255.151 | 2326.6816 | 1303.8568 | 2264.9328 | 1255.151 | 1825.4 | 2384254.1776 | 451854.36 | 204966.1583 | 0 | 219149.3646
8603 | 1741.645 | 2773.8788 | 1809.2291 | 2700.2615 | 1741.645 | 1645.9 | 2998172.6757 | 626992.2 | 284410.6285 | 0 | 616716.4945
8604 | 1714.976 | 3201.2368 | 1781.5252 | 3116.2777 | 1714.976 | 1348 | 2418674.071 | 617391.36 | 280055.5808 | 0 | 1118164.352
8605 | 1914.011 | 4068.2939 | 1988.2837 | 3960.3236 | 1914.011 | 1298.7 | 2589375.0556 | 689043.96 | 312557.9963 | 0 | 1342295.9143
8606 | 1870.71 | 2820.8421 | 1943.3024 | 2745.9785 | 1870.71 | 1493.7 | 2905622.328 | 673455.6 | 305486.943 | 0 | 947140.473
8607 | 1783.81 | 1955.6715 | 1853.0303 | 1903.769 | 1783.81 | 1827.15 | 3392938.7686 | 642171.6 | 291296.173 | 0 | 308331.5585
8608 | 2019.637 | 1511.9086 | 1511.9086 | 1471.7834 | 1471.7834 | 1849.05 | 2818633.9423 | 529842.025 | 240342.2297 | 1004215.6438 | 217466.1175
8609 | 1410.31 | 277.3609 | 277.3609 | 269.9999 | 269.9999 | 1902.95 | 535644.5733 | 97199.9502 | 44090.9774 | 2090188.4837 | 25649.1504
8610 | 1651.085 | 0 | 0 | 0 | 0 | 1922.25 | 0 | 0 | 0 | 3026438.805 | 0
8611 | 1632 | 0 | 0 | 0 | 0 | 1933.9 | 0 | 0 | 0 | 5545536 | 0
8612 | 1364.8 | 0 | 0 | 0 | 0 | 1875.6 | 0 | 0 | 0 | 4637590.4 | 0
8613 | 1691.2 | 0 | 0 | 0 | 0 | 1811.35 | 0 | 0 | 0 | 5746697.6 | 0
8614 | 1349.6 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1832.65 | 588670.6281 | 111351.8261 | 50510.4255 | 3534903.2863 | 51188.0139
8615 | 1433.6 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1811.7 | 1130336.2278 | 215514.4963 | 97759.7701 | 2837155.4159 | 111473.6
8616 | 1556 | 0 | 0 | 0 | 0 | 1757.5 | 0 | 0 | 0 | 2852148 | 0
8617 | 1457.6 | 0 | 0 | 0 | 0 | 1677.8 | 0 | 0 | 0 | 1734544 | 0
8618 | 1494.4 | 0 | 0 | 0 | 0 | 1669.05 | 0 | 0 | 0 | 1778336 | 0
8619 | 1759.2 | 0 | 0 | 0 | 0 | 1633.65 | 0 | 0 | 0 | 2093448 | 0
8620 | 1729.6 | 0 | 0 | 0 | 0 | 1632.7 | 0 | 0 | 0 | 2058224 | 0
8621 | 1414.4 | 0 | 0 | 0 | 0 | 1668.25 | 0 | 0 | 0 | 1683136 | 0
8622 | 1408.8 | 0 | 0 | 0 | 0 | 1688.15 | 0 | 0 | 0 | 1676472 | 0
8623 | 1471.2 | 161.1093 | 161.1093 | 156.8335 | 156.8335 | 1756.1 | 287208.0431 | 56460.0654 | 25610.913 | 2409233.7668 | 37442.5524
8624 | 1645.752 | 1105.3682 | 1105.3682 | 1076.0324 | 1076.0324 | 1824.55 | 2045043.6526 | 387371.6531 | 175716.086 | 1044296.0824 | 184796.2215
8625 | 1196.191 | 1504.0844 | 1242.6089 | 1464.1668 | 1196.191 | 1856.05 | 2313766.71 | 430628.76 | 195337.9903 | 0 | 172191.6944
8626 | 1139.333 | 2180.8895 | 1183.5445 | 2123.0099 | 1139.333 | 1864.55 | 2219341.7093 | 410159.88 | 186053.0789 | 0 | 154322.6548
8627 | 1201.095 | 3069.0053 | 1247.7032 | 2987.5555 | 1201.095 | 1569.95 | 1974935.1131 | 432394.2 | 196138.8135 | 0 | 516530.9047
8628 | 1464.687 | 3343.5032 | 1521.5238 | 3254.7684 | 1464.687 | 1322.45 | 2033026.9997 | 527287.32 | 239183.3871 | 0 | 992398.6769
8629 | 1491.287 | 2290.7463 | 1549.156 | 2229.9511 | 1491.287 | 1029.5 | 1606595.5865 | 536863.32 | 243527.1671 | 0 | 1447294.0335
8630 | 1221.935 | 2762.1631 | 1269.3519 | 2688.8568 | 1221.935 | 1471.55 | 1871862.9671 | 439896.6 | 199541.9855 | 0 | 645731.5508
8631 | 1440.758 | 1496.6663 | 1496.6663 | 1456.9455 | 1440.758 | 1837.8 | 2760628.985 | 518672.88 | 235275.7814 | 0 | 233690.9476
8632 | 1143.128 | 1723.7085 | 1187.4858 | 1677.9622 | 1143.128 | 1888.2 | 2247744.5114 | 411526.08 | 186672.8024 | 0 | 127801.7104
8633 | 1279.819 | 687.7926 | 687.7926 | 669.539 | 669.539 | 1908.65 | 1331273.8008 | 241034.0337 | 109335.7159 | 1118643.2719 | 59868.5976
8634 | 1197.79 | 6.1861 | 6.1861 | 6.0219 | 6.0219 | 1922.25 | 12079.4889 | 2167.8865 | 983.3774 | 2184510.9144 | 458.2585
8635 | 973.6 | 0 | 0 | 0 | 0 | 1922.5 | 0 | 0 | 0 | 3308292.8 | 0
8636 | 1392 | 0 | 0 | 0 | 0 | 1869.9 | 0 | 0 | 0 | 4730016 | 0
8637 | 827.2 | 0 | 0 | 0 | 0 | 1850.5 | 0 | 0 | 0 | 2810825.6 | 0
8638 | 1307.2 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1844.05 | 595777.7931 | 111351.8261 | 50510.4255 | 3390828.0863 | 47701.0503
8639 | 978.4 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1823.1 | 1141239.1653 | 215514.4963 | 97759.7701 | 1290385.8159 | 104724.8
8640 | 1164.8 | 0 | 0 | 0 | 0 | 1796.65 | 0 | 0 | 0 | 2135078.4 | 0
8641 | 1192 | 0 | 0 | 0 | 0 | 1677.8 | 0 | 0 | 0 | 1418480 | 0
8642 | 1257.6 | 0 | 0 | 0 | 0 | 1670.35 | 0 | 0 | 0 | 1496544 | 0
8643 | 1376.8 | 0 | 0 | 0 | 0 | 1667.4 | 0 | 0 | 0 | 1638392 | 0
8644 | 1199.2 | 0 | 0 | 0 | 0 | 1665.45 | 0 | 0 | 0 | 1427048 | 0
8645 | 1092.8 | 0 | 0 | 0 | 0 | 1668.25 | 0 | 0 | 0 | 1300432 | 0
8646 | 1172.8 | 0 | 0 | 0 | 0 | 1701 | 0 | 0 | 0 | 1395632 | 0
8647 | 1270.4 | 159.0566 | 159.0566 | 154.8353 | 154.8353 | 1795.25 | 289220.2757 | 55740.713 | 25284.6068 | 2044830.0697 | 31031.91
8648 | 1082.229 | 1124.2246 | 1124.2246 | 1094.3883 | 1082.229 | 1824.55 | 2055208.1884 | 389602.44 | 176727.9957 | 0 | 189877.078
8649 | 1267.43 | 1756.3581 | 1316.6123 | 1709.7453 | 1267.43 | 1856.05 | 2449196.0806 | 456274.8 | 206971.319 | 0 | 182446.5485
8650 | 1460.39 | 2843.8932 | 1517.0601 | 2768.4178 | 1460.39 | 1864.55 | 2850572.836 | 525740.4 | 238481.687 | 0 | 197809.8255
8651 | 1254.555 | 3174.1739 | 1303.2377 | 3089.933 | 1254.555 | 1760.4 | 2317283.8237 | 451639.8 | 204868.8315 | 0 | 300591.378
8652 | 1447.708 | 3771.0503 | 1503.8859 | 3670.9687 | 1447.708 | 1504.05 | 2288282.15 | 521174.88 | 236410.7164 | 0 | 717990.7826
8653 | 1292.068 | 3006.1576 | 1342.2064 | 2926.3758 | 1292.068 | 1203.3 | 1636949.1732 | 465144.48 | 210994.7044 | 0 | 1029390.5756
8654 | 1332.407 | 2765.3211 | 1384.1107 | 2691.931 | 1332.407 | 1543.7 | 2157907.7777 | 479666.52 | 217582.0631 | 0 | 607977.3141
8655 | 1699.676 | 2188.665 | 1765.6315 | 2130.579 | 1699.676 | 1876.95 | 3317870.4775 | 611883.36 | 277557.0908 | 0 | 209145.1318
8656 | 1738.895 | 1727.0472 | 1727.0472 | 1681.2123 | 1681.2123 | 1893.9 | 3332891.4203 | 605236.4223 | 274541.966 | 105732.4182 | 174603.3589
8657 | 1656.8 | 681.7364 | 681.7364 | 663.6435 | 663.6435 | 1902.95 | 1322522.0164 | 238911.6528 | 108372.9803 | 1820455.9012 | 63044.1652
8658 | 1844.457 | 10.7277 | 10.7277 | 10.443 | 10.443 | 1916.55 | 21004.9728 | 3759.4902 | 1705.3465 | 3361747.61 | 853.0259
8659 | 1589.6 | 0 | 0 | 0 | 0 | 1922.5 | 0 | 0 | 0 | 5401460.8 | 0
8660 | 1539.2 | 0 | 0 | 0 | 0 | 1869.9 | 0 | 0 | 0 | 5230201.6 | 0
8661 | 1721.6 | 0 | 0 | 0 | 0 | 1811.35 | 0 | 0 | 0 | 5849996.8 | 0
8662 | 1580 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1832.65 | 594437.5415 | 111351.8261 | 50510.4255 | 4317802.4863 | 51188.0139
8663 | 1633.6 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1811.7 | 1139623.7367 | 215514.4963 | 97759.7701 | 3516755.4159 | 111473.6
8664 | 1402.4 | 0 | 0 | 0 | 0 | 1796.65 | 0 | 0 | 0 | 2570599.2 | 0
8665 | 1166.4 | 0 | 0 | 0 | 0 | 1527.55 | 0 | 0 | 0 | 2138011.2 | 0
8666 | 950.4 | 0 | 0 | 0 | 0 | 1451.3 | 0 | 0 | 0 | 1742083.2 | 0
8667 | 1228.8 | 0 | 0 | 0 | 0 | 1239.5 | 0 | 0 | 0 | 2252390.4 | 0
8668 | 1433.6 | 0 | 0 | 0 | 0 | 1238.55 | 0 | 0 | 0 | 2627788.8 | 0
8669 | 1112.8 | 0 | 0 | 0 | 0 | 1276.55 | 0 | 0 | 0 | 2039762.4 | 0
8670 | 1390.4 | 0 | 0 | 0 | 0 | 1385.45 | 0 | 0 | 0 | 2548603.2 | 0
8671 | 1300 | 132.539 | 132.539 | 129.0215 | 129.0215 | 1602.25 | 217337.9304 | 46447.7425 | 21069.2121 | 2146403.5779 | 50232.643
8672 | 1239.89 | 1022.2057 | 1022.2057 | 995.0769 | 995.0769 | 1715.45 | 1792739.8294 | 358227.686 | 162496.0587 | 448742.4021 | 277159.3828
8673 | 1372.872 | 1427.7706 | 1426.146 | 1389.8784 | 1372.872 | 1816.9 | 2626381.2641 | 494233.92 | 224189.9976 | 0 | 251372.8632
8674 | 1438.053 | 2746.5582 | 1493.8573 | 2673.666 | 1438.053 | 1825.4 | 2763246.4014 | 517699.08 | 234834.0549 | 0 | 251084.0538
8675 | 1474.877 | 3292.5955 | 1532.1092 | 3205.2118 | 1474.877 | 1475.65 | 2292005.0482 | 530955.72 | 240847.4141 | 0 | 773351.7549
8676 | 1655.249 | 3419.7058 | 1719.4805 | 3328.9486 | 1655.249 | 1466.3 | 2551443.2257 | 595889.64 | 270302.1617 | 0 | 883406.3913
8677 | 1465.832 | 3870.7184 | 1522.7132 | 3767.9917 | 1465.832 | 1308.7 | 2016461.1404 | 527699.52 | 239370.3656 | 0 | 1013329.6616
8678 | 1372.877 | 3612.3064 | 1426.1511 | 3516.4377 | 1372.877 | 1591 | 2303860.6015 | 494235.72 | 224190.8141 | 0 | 561506.693
8679 | 1501.38 | 2626.4069 | 1559.6407 | 2556.7035 | 1501.38 | 1876.95 | 2972445.7375 | 540496.8 | 245175.354 | 0 | 184744.809
8680 | 1727.807 | 1470.2681 | 1470.2681 | 1431.248 | 1431.248 | 1899.6 | 2865953.0501 | 515249.2909 | 233722.8033 | 543592.5915 | 140657.5888
8681 | 1880.42 | 844.1109 | 844.1109 | 821.7087 | 821.7087 | 1908.65 | 1652991.6808 | 295815.1247 | 134185.0274 | 1940617.8498 | 73475.2714
8682 | 1581.08 | 13.5959 | 13.5959 | 13.235 | 13.235 | 1922.25 | 26870.9126 | 4764.6178 | 2161.2836 | 2873859.7945 | 1007.2513
8683 | 1718.4 | 0 | 0 | 0 | 0 | 1933.9 | 0 | 0 | 0 | 3149827.2 | 0
8684 | 1398.4 | 0 | 0 | 0 | 0 | 1830.75 | 0 | 0 | 0 | 2563267.2 | 0
8685 | 1615.2 | 0 | 0 | 0 | 0 | 1745.2 | 0 | 0 | 0 | 2960661.6 | 0
8686 | 1388 | 0 | 0 | 0 | 0 | 1832.65 | 0 | 0 | 0 | 2544204 | 0
8687 | 1260 | 0 | 0 | 0 | 0 | 1811.7 | 0 | 0 | 0 | 2309580 | 0
8688 | 1138.4 | 293.105 | 293.105 | 285.3261 | 285.3261 | 1739.55 | 524540.3131 | 102717.4125 | 46593.7596 | 1563684.3746 | 71167.9625
8689 | 1516 | 0 | 0 | 0 | 0 | 1361.3 | 0 | 0 | 0 | 1804040 | 0
8690 | 1427.2 | 0 | 0 | 0 | 0 | 1439.25 | 0 | 0 | 0 | 1698368 | 0
8691 | 1350.4 | 0 | 0 | 0 | 0 | 1279.7 | 0 | 0 | 0 | 1606976 | 0
8692 | 1424.8 | 0 | 0 | 0 | 0 | 1267.45 | 0 | 0 | 0 | 1695512 | 0
8693 | 1365.6 | 0 | 0 | 0 | 0 | 1206.35 | 0 | 0 | 0 | 1625064 | 0
8694 | 1286.4 | 0 | 0 | 0 | 0 | 1274.3 | 0 | 0 | 0 | 1530816 | 0
8695 | 1076.8 | 706.8225 | 706.8225 | 688.0638 | 688.0638 | 1294.8 | 941552.2495 | 247702.9696 | 112360.8193 | 712553.4463 | 479198.2092
8696 | 900.697 | 935.6483 | 935.6483 | 910.8167 | 900.697 | 1319.65 | 1254795.3042 | 324250.92 | 147083.8201 | 0 | 612789.2039
8697 | 1097.2 | 1354.6201 | 1139.7766 | 1318.6692 | 1097.2 | 1397.75 | 1621924.5569 | 394992 | 179172.76 | 0 | 660788.7
8698 | 1366.655 | 2784.8039 | 1419.6877 | 2710.8967 | 1366.655 | 1320.9 | 1910150.5795 | 491995.8 | 223174.7615 | 0 | 928095.4105
8699 | 1227.291 | 3401.3958 | 1274.9157 | 3311.1246 | 1227.291 | 705.55 | 916822.5502 | 441824.76 | 200416.6203 | 0 | 1588666.835
8700 | 1383.572 | 3985.2082 | 1437.2612 | 3879.443 | 1383.572 | 697.35 | 1017707.0708 | 498085.92 | 225937.3076 | 0 | 1802310.0658
8701 | 1468.257 | 3315.6954 | 1525.2323 | 3227.6987 | 1468.257 | 325.8 | 502573.0565 | 528572.52 | 239766.3681 | 0 | 2458155.8694
8702 | 1027.48 | 2741.896 | 1067.3511 | 2669.1276 | 1027.48 | 694.95 | 753253.2845 | 369892.8 | 167787.484 | 0 | 1340912.774
8703 | 1438.064 | 1493.8677 | 1493.8677 | 1454.2213 | 1438.064 | 1237.5 | 1879173.0734 | 517703.04 | 234835.8512 | 0 | 1096523.8
8704 | 621.669 | 843.0119 | 645.7917 | 820.6388 | 621.669 | 1287.55 | 844508.8231 | 223800.84 | 101518.5477 | 0 | 442908.0791
8705 | 592.386 | 475.7165 | 475.7165 | 463.0912 | 463.0912 | 1496.15 | 729595.2287 | 166712.8404 | 75622.7968 | 236997.3258 | 228392.6857
8706 | 255.342 | 0 | 0 | 0 | 0 | 1646.4 | 0 | 0 | 0 | 468041.886 | 0
8707 | 254.4 | 98.3478 | 98.3478 | 95.7377 | 95.7377 | 1700.95 | 171714.2327 | 34465.5733 | 15633.967 | 539134.4827 | 28312.2597
8708 | 272 | 282.5549 | 282.5549 | 275.056 | 272 | 1282.15 | 368275.3394 | 97920 | 44417.6 | 0 | 195255.2
8709 | 180 | 186.9849 | 186.9849 | 182.0224 | 180 | 1244.45 | 235758.8705 | 64800 | 29394 | 0 | 135999
8710 | 245.6 | 255.1304 | 255.1304 | 248.3594 | 245.6 | 1413.25 | 364415.9094 | 88416 | 40106.48 | 0 | 144105.8
8711 | 105.6 | 109.6978 | 109.6978 | 106.7865 | 105.6 | 1179.55 | 131432.8946 | 38016 | 17244.48 | 0 | 86639.52
8712 | 99.2 | 0 | 0 | 0 | 0 | 1166.3 | 0 | 0 | 0 | 181833.6 | 0
8713 | 91.2 | 0 | 0 | 0 | 0 | 1232.8 | 0 | 0 | 0 | 108528 | 0
8714 | 98.4 | 0 | 0 | 0 | 0 | 1181 | 0 | 0 | 0 | 117096 | 0
8715 | 89.6 | 0 | 0 | 0 | 0 | 1163.1 | 0 | 0 | 0 | 106624 | 0
8716 | 95.2 | 0 | 0 | 0 | 0 | 1116.5 | 0 | 0 | 0 | 113288 | 0
8717 | 91.2 | 0 | 0 | 0 | 0 | 1003.6 | 0 | 0 | 0 | 108528 | 0
8718 | 96.8 | 0 | 0 | 0 | 0 | 1004.5 | 0 | 0 | 0 | 115192 | 0
8719 | 77.6 | 37.6546 | 37.6546 | 36.6553 | 36.6553 | 1005.9 | 38711.884 | 13195.8944 | 5985.8043 | 75051.7046 | 35668.308
8720 | 94.05 | 158.3834 | 97.6996 | 154.18 | 94.05 | 1222.55 | 120284.7752 | 33858 | 15358.365 | 0 | 73119.1725
8721 | 825.915 | 1434.1884 | 857.9655 | 1396.1258 | 825.915 | 1259.55 | 1095321.3368 | 297329.4 | 134871.9195 | 0 | 611548.7618
8722 | 1285.579 | 2052.4424 | 1335.4656 | 1997.9717 | 1285.579 | 1225.35 | 1662569.1279 | 462808.44 | 209935.0507 | 0 | 995873.7724
8723 | 1403.535 | 1457.9988 | 1457.9988 | 1419.3043 | 1403.535 | 1213.3 | 1795241.3882 | 505272.6 | 229197.2655 | 0 | 1104160.9845
8724 | 1280.109 | 1329.7833 | 1329.7833 | 1294.4916 | 1280.109 | 1222.3 | 1655360.0032 | 460839.24 | 209041.7997 | 0 | 995540.7693
8725 | 1122.521 | 1898.7086 | 1166.0801 | 1848.3179 | 1122.521 | 1191.1 | 1413141.7327 | 404107.56 | 183307.6793 | 0 | 908007.2369
8726 | 1380.964 | 1355.9446 | 1355.9446 | 1319.9585 | 1319.9585 | 1187.15 | 1649243.547 | 475185.0732 | 215549.2291 | 111823.0141 | 1050232.2755
8727 | 1395.618 | 1319.4254 | 1319.4254 | 1284.4086 | 1284.4086 | 1194.3 | 1617073.2888 | 462387.0798 | 209743.917 | 203846.9127 | 1012957.4623
8728 | 1382.822 | 544.6671 | 544.6671 | 530.212 | 530.212 | 1160.6 | 647801.0338 | 190876.3111 | 86583.6156 | 1562834.1752 | 435646.0818
8729 | 1035.196 | 248.6836 | 248.6836 | 242.0837 | 242.0837 | 1294.6 | 328616.5334 | 87150.1306 | 39532.2676 | 1453774.853 | 167153.7002
8730 | 1041.064 | 0 | 0 | 0 | 0 | 1651.2 | 0 | 0 | 0 | 1908270.312 | 0
8731 | 1022.4 | 0 | 0 | 0 | 0 | 1747.2 | 0 | 0 | 0 | 3474115.2 | 0
8732 | 1182.4 | 0 | 0 | 0 | 0 | 1632.15 | 0 | 0 | 0 | 4017795.2 | 0
8733 | 1686.4 | 0 | 0 | 0 | 0 | 1609.35 | 0 | 0 | 0 | 5730387.2 | 0
8734 | 897.6 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1598.8 | 519704.6315 | 111351.8261 | 50510.4255 | 1999007.2863 | 122716.6488
8735 | 1217.6 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1578.8 | 992010.5529 | 215514.4963 | 97759.7701 | 2103187.4159 | 249350.4
8736 | 1290.4 | 0 | 0 | 0 | 0 | 1370.85 | 0 | 0 | 0 | 2365303.2 | 0
8737 | 1120 | 0 | 0 | 0 | 0 | 1422.9 | 0 | 0 | 0 | 1332800 | 0
8738 | 1036.8 | 0 | 0 | 0 | 0 | 1205.75 | 0 | 0 | 0 | 1233792 | 0
8739 | 1090.4 | 0 | 0 | 0 | 0 | 1203.1 | 0 | 0 | 0 | 1297576 | 0
8740 | 1088 | 0 | 0 | 0 | 0 | 1221.65 | 0 | 0 | 0 | 1294720 | 0
8741 | 1287.2 | 0 | 0 | 0 | 0 | 1264.6 | 0 | 0 | 0 | 1531768 | 0
8742 | 1304.8 | 0 | 0 | 0 | 0 | 1534 | 0 | 0 | 0 | 1552712 | 0
8743 | 1274.4 | 78.9284 | 78.9284 | 76.8337 | 76.8337 | 1607.05 | 129378.8654 | 27660.1207 | 12546.9381 | 2195139.0857 | 29552.9836
8744 | 1022.55 | 782.0673 | 782.0673 | 761.3116 | 761.3116 | 1636.35 | 1306734.7912 | 274072.1876 | 124322.1895 | 478849.9282 | 270994.5256
8745 | 1026.462 | 1371.9006 | 1066.2936 | 1335.4911 | 1026.462 | 1610.75 | 1738858.9294 | 369526.32 | 167621.2446 | 0 | 399550.3335
8746 | 1278.239 | 2367.5825 | 1327.8407 | 2304.7481 | 1278.239 | 1283 | 1724879.9388 | 460166.04 | 208736.4287 | 0 | 916497.363
8747 | 1288.464 | 2599.0022 | 1338.4625 | 2530.0261 | 1288.464 | 1066.55 | 1448444.26 | 463847.04 | 210406.1712 | 0 | 1202716.7208
8748 | 1351.624 | 2654.25 | 1404.0734 | 2583.8077 | 1351.624 | 1221.55 | 1738904.9495 | 486584.64 | 220720.1992 | 0 | 1052171.7028
8749 | 1146.697 | 1855.4705 | 1191.1943 | 1806.2273 | 1146.697 | 1219.05 | 1466176.5223 | 412810.92 | 187255.6201 | 0 | 895513.0222
8750 | 1487.273 | 1775.3173 | 1544.9863 | 1728.2014 | 1487.273 | 1256.25 | 1965451.4865 | 535418.28 | 242871.6809 | 0 | 1106159.2937
8751 | 1161.038 | 2076.5177 | 1206.0918 | 2021.4081 | 1161.038 | 1483.05 | 1809353.0049 | 417973.68 | 189597.5054 | 0 | 600198.5941
8752 | 1604.111 | 1687.8022 | 1666.3581 | 1643.0088 | 1604.111 | 1694.8 | 2851777.0171 | 577479.96 | 261951.3263 | 0 | 489574.6772
8753 | 1704.867 | 267.6917 | 267.6917 | 260.5873 | 260.5873 | 1849.65 | 504213.5183 | 93811.4216 | 42553.9032 | 2647364.7229 | 38350.5263
8754 | 1368.022 | 0 | 0 | 0 | 0 | 1916.55 | 0 | 0 | 0 | 2507584.326 | 0
8755 | 1372.8 | 0 | 0 | 0 | 0 | 1922.5 | 0 | 0 | 0 | 4664774.4 | 0
8756 | 1204.8 | 0 | 0 | 0 | 0 | 1830.75 | 0 | 0 | 0 | 4093910.4 | 0
8757 | 1449.6 | 0 | 0 | 0 | 0 | 1754.25 | 0 | 0 | 0 | 4925740.8 | 0
8758 | 1340 | 317.7434 | 317.7434 | 309.3106 | 309.3106 | 1793.5 | 580766.624 | 111351.8261 | 50510.4255 | 3502282.4863 | 63162.981
8759 | 1208 | 614.9724 | 614.9724 | 598.6514 | 598.6514 | 1733.4 | 1089999.2157 | 215514.4963 | 97759.7701 | 2070566.6159 | 157827.2
8760 | 1216 | 0 | 0 | 0 | 0 | 1658.6 | 0 | 0 | 0 | 2228928 | 0