## Slide 1
CEBA CLEAN ENERGY PROCUREMENT WORKSHOP · 2026
Solar + BESS:
The Economic Case
A techno-economic analysis of four clean-energy procurement strategies for a single Vietnamese manufacturer — Factory A.
REopt MILP system optimization
25-year ESCO pro forma
70% project debt
9.3 GWh/yr load · 22–110 kV

## Slide 2
THE STUDY
One Factory, Four Procurement Strategies
FACTORY A — LOAD PROFILE
9.3 GWh
Annual electricity demand
2.43 MW
Peak demand · flat industrial load
22–110 kV
Grid connection voltage
S. Vietnam
HCMC region · strong solar resource
THE FOUR SCENARIOS — EACH INDEPENDENTLY SIZE-OPTIMIZED
CASE 4
Solar Only
New TOU (Decision 963). PV only — no storage. The conventional rooftop benchmark.
CASE 1
Solar + BESS
Today's tariff (current TOU). Integrated PV + battery, the baseline integrated system.
CASE 2
Solar + BESS
New evening-peak TOU (Decision 963, 17:30–22:30). Integrated PV + battery.
CASE 3
Solar + BESS
New TOU + two-component capacity tariff (~209,459 VND/kW/mo). PV + battery.
Method: PV and battery sizes are optimized in REopt for each tariff, then evaluated over a 25-year ESCO pro forma (70% debt). All monetary figures in USD. One anomalous 24-hour data spike was removed from the metered load.
Factory A · Solar + BESS Techno-Economic Case Study
02

## Slide 3
FINDING 1
Solar Alone Stalls at One-Third of Demand
Even fully optimized, a solar-only system meets only 36% of the factory's load.
Why it plateaus
Under Decision 963 the priced peak shifts to 17:30–22:30 — after sunset. Daytime panels offset only midday consumption.
The expensive evening peak stays on full-price grid power.
Adding more panels doesn't help: past ~36% of load, midday surplus is curtailed or exported at low value — so the optimizer stops at 3.45 MW.
It is a partial daytime hedge — not a path to 24/7 clean energy.
Chart: 
| Clean (solar) | Grid
mix | 35.8 | 64.2
Optimal system: 3.45 MW PV, no storage
36%
Clean self-supply
$245k
Annual bill savings
18.7%
Equity IRR
$0.80M
25-year NPV
Factory A · Solar + BESS Techno-Economic Case Study
03

## Slide 4
FINDING 2
Storage Nearly Doubles Clean Supply — and Savings
Same factory, same new tariff — add a battery (Case 4 → Case 2):
Chart: 
| Solar Only | Solar + BESS
s | 35.8 | 65.5
CLEAN SELF-SUPPLY (% of load)
Chart: 
| Solar Only | Solar + BESS
s | 245 | 569
ANNUAL BILL SAVINGS (USD)
+30 points clean energy · +$324k/yr savings · and the package still earns 16% equity IRR with $1.44M NPV.
The battery shifts midday solar into the evening peak — turning a daytime hedge into round-the-clock clean supply.
Factory A · Solar + BESS Techno-Economic Case Study
04

## Slide 5
FINDING 3
The 2026 Capacity Tariff Makes Peak-Shaving the Prize
When EVN starts billing capacity (~209,459 VND/kW/month), the dominant value flips from energy arbitrage to demand-charge avoidance.
The optimizer adds battery power to cut the grid peak nearly in half:
2,428 kW → 1,311 kW (−46%)
Returns tighten as the system grows — but every metric stays bankable, and this is the tariff Factory A will actually face in 2026.
Chart: 
| Grid peak (no battery) | Grid peak (with BESS)
s | 2428 | 1311
PEAK GRID DEMAND — CASE 3
$129k
Demand-charge savings / yr
-65%
Total bill ($758k → $263k)
12.4%
Equity IRR (still bankable)
1.01
Avg DSCR (debt-serviceable)
Factory A · Solar + BESS Techno-Economic Case Study
05

## Slide 6
SIDE BY SIDE
Full Techno-Economic Comparison
 | Solar Only | Solar + BESS | Solar + BESS | Solar + BESS
Tariff regime | New TOU 963 | Current TOU | New TOU 963 | TOU 963 + 2-comp.
PV size | 3.45 MW | 5.32 MW | 5.91 MW | 5.77 MW
Battery (power / energy) | — | 1.66 / 8.3 | 1.80 / 10.7 | 1.83 / 11.7
Clean self-supply | 35.8% | 59.5% | 65.5% | 65.8%
Total CapEx | $1.66M | $3.68M | $4.27M | $4.32M
Annual bill savings | $245k | $531k | $569k | $494k
Equity IRR | 18.7% | 18.2% | 16.1% | 12.4%
25-year NPV | $0.80M | $1.65M | $1.44M | $0.59M
Average DSCR | 1.33 | 1.31 | 1.21 | 1.01
Simple payback | 9.0 yr | 9.4 yr | 10.5 yr | 12.2 yr
READING THE TABLE
All four are NPV-positive and clear DSCR ≥ 1.0 — every option is financeable.
Adding BESS lifts clean supply from 36% to ~60–66%.
Tariff reform compresses returns (18% → 12%) but never breaks bankability.
Solar-only has the highest IRR but the lowest absolute value and clean share.
Factory A · Solar + BESS Techno-Economic Case Study
06

## Slide 7
CONCLUSIONS
What the Four Cases Tell CEBA Members
01
Solar alone is only a partial hedge
Optimized rooftop PV caps at ~36% of demand and leaves the priced evening peak on the grid.
02
BESS is what unlocks 24/7 clean energy
Storage lifts clean self-supply to 60–66% and roughly doubles bill savings — while equity IRR stays 16–18% and NPV stays positive.
03
Tariff reform compresses but never breaks the case
Across current TOU, Decision 963 and the two-component tariff, every Solar+BESS case clears DSCR ≥ 1.0 and remains financeable.
04
Size the battery for the 2026 tariff — not today's
Under the two-component capacity charge, demand-charge avoidance (peak −46%) becomes the single largest value stream. Size for power, not just energy.
RECOMMENDATION
Pursue integrated Solar + BESS now — and size storage to the tariff you will face in 2026, not the one you have today.
The battery converts a daytime solar hedge into bankable, round-the-clock clean supply.
Source: REopt system optimization + Vietnam ESCO pro forma (25 yr, 70% debt). Figures USD. One anomalous 24-hour load spike removed prior to modeling.
Factory A · Solar + BESS Techno-Economic Case Study
07